## BoQ1
Government eProcurement System Created By: VIDYUT KESH SINGH Created Date/Time: 22-Jun-2020 01:32 PM Tender Title: Modernization of Chennai Airport, Phase-II, Chennai SH Interior Electrical Lighting Works Tender ID: 2020_AAI_39372_1
Tender Inviting Authority: AGM (Engg.-Elect), Airports Authority of India Chennai Airport Desk, O/o Executive Director (Engg.)-SR, Corporate Head Quarters, A-Block, 3rd Floor, Rajiv Gandhi Bhawan, Safdarjang Airport, New Delhi-110 003
Name of Work:Modernization of Chennai Airport, Phase-II, Chennai SH: Interior Electrical Lighting Works
Contract No: Tender ID:(Bid No: 2020_AAI_39372_1)
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Godrej and Boyce Mfg Co Ltd |  | MIDAS ELECTRICALS PVT LTD
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, fabrication, supply, assembly, installation, testing & commissioning of PoE enabled smart suspended mounted strech fabric decorative luminaire along with necessary number of UL/CE certified PoE Drivers as per PoE network design. The shape and dimension of luminaire shall be as per tender intent drawing. The housing shall be made of aluminum 6062 White powder coated color RAL 9003 finish matt 50%. The luminaire shall have LM80 compliant high efficacy LEDs having CRI ≥ 80 & CCT 3000K & life of 50000 burning hours. The LED efficacy shall be minimum 160lm/w & shall have SDC<5. The luminaire shall ensure average illumination level of 300 lux to 400 lux and average uniformity ≥0.4 below luminaire at working plane level of 0.70M. The luminaires shall be suspended using MS threaded roads or of suitable structure or suitable size to bear the load of luminaire. The luminaire shall use the rating of LEDs which are compatible with PoE driver including wiring of 2x 1.5 sqmm FRLS from PoE Driver to Luminare and all accessories as required for installation of fixuteres as per site requirement complete in all respect and as per technical specification. Make: Wipro/Philips/Hubble/Divinity/CREE/ Trilux/ Equivalent meeting the technical specifictions. The luminaire shall use stretch fabric having following specifications complete in all respect: Fire retardant grade: European standard b-s1-d0 ( EN13501-1) Thickness: 0.15 to 0.20mm , Weight Approx.: 200gms/sq. mtr ,Breaking strength lengthwise: 185 kgs/cm2 Breaking strength widthwise: 220 kgs/cm2 ,Elongation lengthwise: 210% ,Elongation widthwise: 305% Hardness: 93.5 Shore A. Light reflection properties High glossy: >80% Light reflection properties for matt: <10% Light transmittance properties back lighting: minimun 70% Resistance to humidity: a) Impermeable to Water and steam, b) Anti-bacterial , Anti Fingal and Anti-Static, c) Flame retardant , non-flammable and self-extinguishing Thermal Properties: Dimensional Stability -5 deg C to +55 deg C Recycling properties: 100% recyclable. The luminaire shall be placed at following tentative heights from FFL:
2.00 | 3M to 4M Height from FFL: The luminaire shall occupy & illuminate below areas as per shapes & placement in tender intent drawings & ensure average Illumination level of 300lux to 400lux below luminaire at working plane level of 0.70M: a) Arrival area: 5032sq.ft. b) Departure Area: 2960 sq.ft. c) VIP lounge at Domestic arrival: 200sq.ft. d) VIP lounge at International Arrival: 220 sq.ft. e) VIP lounge at International Departure: 200 sq.ft. | 8612.00 | sqft |  | 3975.00 | 34232700.00 | 5075.00 | 43705900.00 | 34232700.00 | Godrej and Boyce Mfg Co Ltd
3.00 | 8M to 9M Height from FFL: The luminaire shall occupy & illuminate below areas as per shapes & placement in tender intent drawings & ensure average Illumination level of 300lux to 400lu lux below luminaire at working plane level of 0.70M: a) Mezzanine Area: 16388 sq.ft. | 16388.00 | sqft |  | 3975.00 | 65142300.00 | 5250.00 | 86037000.00 | 65142300.00 | Godrej and Boyce Mfg Co Ltd
4.00 | Design, fabrication, supply, assembly, installation, testing & commissioning of IP 20 Pendant mounted Ring LED Luminaire including suspension system , housing made of Aluminium, seamlessly welded or joint using suitable mechanism giving clean & good finish. Diffuser made of satin PMMA/Polystyerene. The luminaire shall deliver minimum 8000lm & with minimum system efficacy of 80lm/w. The lumianire shall have only down-wards lighting contribution. The luminaire shall have LM80 ,LM79compliant high efficacy LEDs having CRI ≥ 80 & CCT 3000K & life of 50000 burning hours. The LED efficacy shall be minimum 160lm/w & shall have SDC<5. Fixture should be hanged with Adjustable steel cable suspension. The luminaire shall have remote non integral BIS registered driver having THD≤ 10%, PF ≥0.95, surge protection ≥ 2KV & input volt age 140V to 270V. The LED Driver shall be easily avaiable in India for repair and service. Tentative Diameter of the ring shall be 2400mm to 2700mm & luminaire height between 90Mm to 150MM. The luminaire shall be complete in all respect including wiring with 1.5 sqmm FRLS from nearest tapping points and all accessories as required for installation of fixuteres as per site requirement complete in all respect and as per technical specification. The luminaire shall be with following certifications: LM79 from NABL accredited lab & LM80 issued by LED manufacture along with Photo Biological Safety Standard. Make: Wipro/Philips/Hubble/Divinity/CREE/ Trilux/ Equivalent meeting the technical specifictions. | 48.00 | Each |  | 68513.00 | 3288624.00 | 62500.00 | 3000000.00 | 3000000.00 | MIDAS ELECTRICALS PVT LTD
5.00 | Supply, Installtion, Testing & commissioning of exterior LED ground burial equipped with with Die-cast aluminium housing along with tempred step glass with IK 10 . Fixture should have IP rating of IP67. The luminaire shall deliver minimum 500lm & with minimum system efficacy of 65lm/w. The lumianire shall have only upward-wards lighting contribution & shall have 30 Degree beam angle. The luminaire shall have LM80 compliant high efficacy LEDs having CRI ≥ 70 & CCT 3000K & life of 35000 burning hours. The luminaire shall be with BIS Registered electronic driver with input voltage range of 150 to 270V, 35,000 Hrs LED Life with L70 Criteria. The luminaire shall be with following certifications: LM79 from NABL accrediated lab & LM80 issued by LED manufacturer. The luminaire shall be complete in all respect &including wiring with 1.5 sqmm FRLS from nearest tapping points and all accessories as required for installation of fixuteres as per site requirement complete in all respect and as per technical specification . Make: Wipro/Philips/Trilux/ Hubble/Divinity/Equivalent. | 140.00 | Each |  | 40891.00 | 5724740.00 | 35600.00 | 4984000.00 | 4984000.00 | MIDAS ELECTRICALS PVT LTD
6.00 | Supply, Installtion, Testing & commissioning of Integral circular LED flood light with circular base, made of die cast aluminium having IP66 Protection. The luminaire shall deliver minimum 1855lm & with minimum system efficacy of 65lm/w. The lumianire shall have beam angle of 30 Degrees. The luminaire shall have LM80 compliant high efficacy LEDs having CRI ≥ 70 & CCT 3000K & life of 35000 burning hours. The luminaire shall have remote non integral BIS registered driver having THD≤ 20%, PF ≥0.90, surge protection ≥ 2KV & input voltage 140V to 270V. The LED Driver shall be easily avaiable in India for repair and service. The luminaire shall be complete in all respect including wiring with 1.5 sqmm FRLS from nearest tapping points and all accessories as required for installation of fixuteres as per site requirementas and per technical specification The luminaire shall be with following certifications: LM79 from NABL accredited lab & LM80 issued by LED manufacture along with Photo Biological Safety Standard. Make: Wipro/Philips/Hubble/Divinity/CREE/ Trilux/ Equivalent meeting the technical specifictions. | 24.00 | Each |  | 25924.00 | 622176.00 | 24500.00 | 588000.00 | 588000.00 | MIDAS ELECTRICALS PVT LTD
7.00 | Supply, Installation, Testing & Commissioning of IP66 Integral Linear surface mounted wall washer made of Die-cast aluminium housing for better heat dissipation & having minimum lenth of 1000mm. The luminaire shall deliver minimum 2000lm & having minimum system efficacy of 50lm/w. The lumianire shall have beam angle of 30-50 Degrees. The luminaire shall have LM80 compliant high efficacy LEDs having CRI ≥ 70 & CCT 3000K & life of 35000 burning hours. The luminaire shall have remote non integral BIS registered driver having THD≤ 20%, PF ≥0.90, surge protection ≥ 2KV & input voltage 140V to 270V. The LED Driver shall be easily avaiable in India for repair and service. The luminaire shall be complete in all respect & including wiring with 1.5 sqmm FRLS from nearest tapping points and all accessories as required for installation of fixuteres as per site requirement complete in all respect and as per technical specification. The luminaire shall be with following certifications: LM79 from NABL accredited lab & LM80 issued by LED manufacture along with Photo Biological Safety Standard. Make: Wipro/Philips/Hubble/Divinity/CREE/ Trilux/ Equivalent meeting the technical specifictions. | 308.00 | Each |  | 55873.00 | 17208884.00 | 52500.00 | 16170000.00 | 16170000.00 | MIDAS ELECTRICALS PVT LTD
8.00 | Supply, Installtion, Testing & commissioning of Z-Plug Field-Terminated Plug complete in all respect as per site requirement. | 2595.00 | Each |  | 791.67 | 2054383.65 | 30.00 | 77850.00 | 77850.00 | MIDAS ELECTRICALS PVT LTD
9.00 | Supply, Installtion, Testing & commissioning of Cat6 UTP Horizontal cable, LSOH, 305M reel (PoE) in existing cable tay/surface as required complete in all respect | 815.00 | Reel |  | 4050.00 | 3300750.00 | 5750.00 | 4686250.00 | 3300750.00 | Godrej and Boyce Mfg Co Ltd
10.00 | Supply, Installtion, Testing & commissioning of Cat 6, double-ended, stranded modular cord, clear boot, CMG complete in all respect as per site requirement. | 5504.00 | Each |  | 255.00 | 1403520.00 | 500.00 | 2752000.00 | 1403520.00 | Godrej and Boyce Mfg Co Ltd
11.00 | Supply, Installtion, Testing & commissioning of Cat 6 Patch panel, 1U (At Rack side) complete in all respect as per site requirement. | 119.00 | Each |  | 9596.00 | 1141924.00 | 9600.00 | 1142400.00 | 1141924.00 | Godrej and Boyce Mfg Co Ltd
12.00 | Supply, Installtion, Testing & commissioning of Horizontal cable manager, 1U (for Patch panel) complete in all respect as per site requirement. | 119.00 | Each |  | 4736.00 | 563584.00 | 30400.00 | 3617600.00 | 563584.00 | Godrej and Boyce Mfg Co Ltd
13.00 | Supply, Installtion, Testing & commissioning of Horizontal cable manager, 1U (for Switch Chassis) complete in all respect as per site requirement. | 332.00 | Each |  | 2566.67 | 852134.44 | 1980.00 | 657360.00 | 657360.00 | MIDAS ELECTRICALS PVT LTD
14.00 | Supply, Installtion, Testing & commissioning of Fiber cable, Indoor/Outdoor, OM3 in existing cable tay/surface as required complete in all respect | 8500.00 | Mtrs. |  | 157.00 | 1334500.00 | 180.00 | 1530000.00 | 1334500.00 | Godrej and Boyce Mfg Co Ltd
15.00 | Supply, Installtion, Testing & commissioning of Fiber patch panel with 3 slots black complete in all respect as per site requirement. | 21.00 | Each |  | 25353.00 | 532413.00 | 26000.00 | 546000.00 | 532413.00 | Godrej and Boyce Mfg Co Ltd
16.00 | Supply, Installtion, Testing & commissioning of Fiber patch panel with high density fiber splicing complete in all respect as per site requirement. | 21.00 | Each |  | 30250.00 | 635250.00 | 29600.00 | 621600.00 | 621600.00 | MIDAS ELECTRICALS PVT LTD
17.00 | Supply, Installtion, Testing & commissioning of Fiber, Adapter ,12 Fiber, LC type complete in all respect as per site requirement. | 42.00 | Each |  | 7127.50 | 299355.00 | 50.00 | 2100.00 | 2100.00 | MIDAS ELECTRICALS PVT LTD
18.00 | Supply, Installtion, Testing & commissioning of Fiber, Adapter ,24 Fiber, LC type complete in all respect as per site requirement. | 42.00 | Each |  | 12700.00 | 533400.00 | 50.00 | 2100.00 | 2100.00 | MIDAS ELECTRICALS PVT LTD
19.00 | Supply, Installtion, Testing & commissioning of Fiber Blank plate complete in all respect as per site requirement. | 42.00 | Each |  | 325.00 | 13650.00 | 35.00 | 1470.00 | 1470.00 | MIDAS ELECTRICALS PVT LTD
20.00 | Supply, Installtion, Testing & commissioning of Fiber splice tray complete in all respect as per site requirement. | 21.00 | Each |  | 2462.50 | 51712.50 | 1900.00 | 39900.00 | 39900.00 | MIDAS ELECTRICALS PVT LTD
21.00 | Supply, Installtion, Testing & commissioning of Fiber, Pigtail, OM3 LC Type complete in all respect as per site requirement. | 504.00 | Each |  | 712.50 | 359100.00 | 550.00 | 277200.00 | 277200.00 | MIDAS ELECTRICALS PVT LTD
22.00 | Supply, Installtion, Testing & commissioning of HEAT SHRINK SLEEVE, 60MM complete in all respect as per site requirement. | 504.00 | Each |  | 45.00 | 22680.00 | 20.00 | 10080.00 | 10080.00 | MIDAS ELECTRICALS PVT LTD
23.00 | Supply, Installtion, Testing & commissioning of Fiber patch cord, LC-LC, OM3, 3M complete in all respect as per site requirement. | 84.00 | Each |  | 3343.00 | 280812.00 | 3050.00 | 256200.00 | 256200.00 | MIDAS ELECTRICALS PVT LTD
24.00 | Supply, Installtion, Testing & commissioning of Closed Cabinet, 42U/45U, with vertical patching provision design complete in all respect as per site requirement. | 21.00 | Each |  | 6123.00 | 128583.00 | 5500.00 | 115500.00 | 115500.00 | MIDAS ELECTRICALS PVT LTD
25.00 | Supply, Installtion, Testing & commissioning of Vertical Cable Tray, 42U/45U complete in all respect as per site requirement. | 42.00 | Each |  | 37321.67 | 1567510.14 | 1000.00 | 42000.00 | 42000.00 | MIDAS ELECTRICALS PVT LTD
26.00 | Supply, Installtion, Testing & commissioning of Blank panel complete in all respect as per site requirement. | 84.00 | Each |  | 3110.00 | 261240.00 | 50.00 | 4200.00 | 4200.00 | MIDAS ELECTRICALS PVT LTD
27.00 | Supply, Installtion, Testing & commissioning of CABLE BRUSH GUARD complete in all respect as per site requirement. | 21.00 | Each |  | 5572.50 | 117022.50 | 50.00 | 1050.00 | 1050.00 | MIDAS ELECTRICALS PVT LTD
28.00 | Supply, Installtion, Testing & commissioning of 20U Vertical frame to mount the patch panel vertically complete in all respect as per site requirement. | 119.00 | Each |  | 15032.50 | 1788867.50 | 50.00 | 5950.00 | 5950.00 | MIDAS ELECTRICALS PVT LTD
29.00 | Supply, Installtion, Testing & commissioning of Horizontal PDU,6 x 6/16A Sockets complete in all respect as per site requirement. | 120.00 | Each |  | 4924.17 | 590900.40 | 3800.00 | 456000.00 | 456000.00 | MIDAS ELECTRICALS PVT LTD
30.00 | Supply, Installtion, Testing & commissioning of Lighting management software for 3000+ devices as per detailed specificatios of tender complete in all respect as per site requirement. | 1.00 | Each |  | 2728931.00 | 2728931.00 | 3950000.00 | 3950000.00 | 2728931.00 | Godrej and Boyce Mfg Co Ltd
31.00 | Supply, Installtion, Testing & commissioning of UPoE Switch as per detailed specificatios of tender complete in all respect as per site requirement. | 314.00 | Each |  | 101697.00 | 31932858.00 | 98000.00 | 30772000.00 | 30772000.00 | MIDAS ELECTRICALS PVT LTD
32.00 | Supply, Installtion, Testing & commissioning of Layer - 2/3 switch with 24 ports as per detailed specificatios of tender complete in all respect as per site requirement. | 18.00 | Each |  | 571443.00 | 10285974.00 | 454123.00 | 8174214.00 | 8174214.00 | MIDAS ELECTRICALS PVT LTD
33.00 | Server as per detailed specification & all necessary accessories as per site requirement complete in all respect as per site requirement. | 1.00 | Each |  | 3894579.00 | 3894579.00 | 3720000.00 | 3720000.00 | 3720000.00 | MIDAS ELECTRICALS PVT LTD
34.00 | computer as per detailed specification & all necessary accessories as per site requirement complete in all respect as per site requirement. | 1.00 | Each |  | 198517.00 | 198517.00 | 323000.00 | 323000.00 | 198517.00 | Godrej and Boyce Mfg Co Ltd
35.00 | Supply and installing following size of galvanised iron perforated Hot dipped galvanized Iron cable tray (n galvanisation not less than 50 microns) type cable trays including with perforation not more than 17.5%, in convenient sections horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with GI suspenders etc as required. 650 mm width x 60mm depth x 2 mm thickness. | 60.00 | Mtr |  | 2348.00 | 140880.00 | 3125.00 | 187500.00 | 140880.00 | Godrej and Boyce Mfg Co Ltd
36.00 | Supply and installing following size of galvanised iron perforated Hot dipped galvanized Iron cable tray ( galvanisation not less than 50 microns) type cable trays including with perforation not more than 17.5%, in convenient sections horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with GI suspenders etc as required. 300 mm width x 60mm depth x 1.6 mm thickness | 1500.00 | Mtr |  | 1114.00 | 1671000.00 | 2450.00 | 3675000.00 | 1671000.00 | Godrej and Boyce Mfg Co Ltd
37.00 | Supply and installing following size of galvanised iron perforated Hot dipped galvanized Iron cable tray ( galvanisation not less than 50 microns) type cable trays including with perforation not more than 17.5%, in convenient sections horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with GI suspenders etc as required. 150 mm width x 60mm depth x 1.6 mm thickness. | 1000.00 | Mtr |  | 816.00 | 816000.00 | 2250.00 | 2250000.00 | 816000.00 | Godrej and Boyce Mfg Co Ltd
38.00 | Supply and installing following size of galvanised iron perforated Hot dipped galvanized Iron cable tray (galvanisation not less than 50 microns) type cable trays including with perforation not more than 17.5%, in convenient sections horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with GI suspenders etc as required. 32 MM | 500.00 | Mtr |  | 1082.00 | 541000.00 | 2250.00 | 1125000.00 | 541000.00 | Godrej and Boyce Mfg Co Ltd
39.00 | Supply and installing following size of galvanised iron perforated Hot dipped galvanized Iron cable tray ( galvanisation not less than 50 microns) type cable trays including with perforation not more than 17.5%, in convenient sections horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with GI suspenders etc as required. 25 MM | 500.00 | Mtr |  | 879.00 | 439500.00 | 2250.00 | 1125000.00 | 439500.00 | Godrej and Boyce Mfg Co Ltd
40.00 | Supply, Installation, Testing and commissioning of Wall Reccesed Bi-level Drinking Water Fountains, made of Stainless Steel 304 with cooling capacity of 8.0 GPH (gallons per hour) of 50 degree F drinking water, based on 80 degree F inlet water and 90 degree ambient per ASHRAE 18 testing, furnished with double flexible Bubbler in 100 Micron Straine with inbuilt UV and Sediment filter plant having 8 GPH permeate capacity.Unit shall be certified to UL 399 and CAN/CSA C22.2 No.120. Unit shall be lead-free design which is certified to NSF/ANSI 61 & 372 (lead free), GRIHA and TUV Certified and with ADA Compliant to be placed at different location of buidling. Agency has to execute all civil work for installing the Water Fountain for proper functioning and aesthetic view as directed by the engineer-in-charge and complete in all respect without any extra cost . Power:- 220-230v/60Hz Bubbler Style:- Double Bubbler Activation by:- Mechanical Front Bubbler Button Mounting Type:- Wall Mount (In-Wall Frame/Plate) Chilling Option:- 8.0 GPH Rated Watts:- 370 Installation Location:- Indoor No. of bottle filling station-1
41.00 | No. of Stations Served:- 2 Based on 80° F inlet water & 90° F ambient air temp for 50° F chilled drinking water. COOLING SYSTEM Compressor: Hermetically-sealed, reciprocating type, single phase. Sealed-in lifetime lubrication. Condenser: Fan cooled, copper tube with aluminum fins. Fan motor is permanently lubricated. Cooling Unit: Combination tube-tank type. Continuous copper tubing with fully insulated with EPS foam that meets UL requirements for self-extinguishing material. Refrigerant Control: Refrigerant R-134a Temperature Control: Easily accessible enclosed adjustable thermostat is factory preset. | 44.00 | each |  | 258073.00 | 11355212.00 | 397060.00 | 17470640.00 | 11355212.00 | Godrej and Boyce Mfg Co Ltd
42.00 | All inclusive Comprehensive Maintenance of decorative LED luminaires, Strech fabric, POE system, active & Passive network and drinking water fountain after DLP as provided under the main contract including trouble shooting, preventive maintenance and breakdown maintenance etc. as required as per good engineering practice, instructions of Engineer-in-Charge and as per terms and conditions specified tender
43.00 | 1st year after 2 Years of DLP.
44.00 | 2nd year after 2 Years of DLP.
45.00 | 3rd year after 2 Years of DLP.
46.00 | 4th year after 2 Years of DLP.
47.00 | 5th year after2 Years of DLP.
| Total in Figures |  |  |  |  | 208057167.13 |  | 244102064.00
Lowest Amount Quoted BY: Godrej and Boyce Mfg Co Ltd(208057167.13)

## BOQ Summary
BOQ Summary Details Tender Title: Modernization of Chennai Airport, Phase-II, Chennai SH Interior Electrical Lighting Works Tender ID: 2020_AAI_39372_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Godrej and Boyce Mfg Co Ltd | 208057167.13 | L1
| 2 | MIDAS ELECTRICALS PVT LTD | 244102064.00 | L2