## BoQ1
Government eProcurement System Created By: VIDYUT KESH SINGH Created Date/Time: 22-Jun-2020 03:23 PM Tender Title: Modernization of Chennai Airport, (Phase-II), SH Design, Manufacture, Supply, Installation, Testing and Commissioning of Signages Works Tender ID: 2020_AAI_39373_1
Tender Inviting Authority: Asstt. General Manager (Engg. -Elect.) Airports Authority of India O/o ED Engg. – SR CHQ, Rajiv Gandhi Bhawan, New Delhi-110 003
Name of Work: Modernization of Chennai Airport, (Phase-II), SH: Design, Manufacture, Supply, Installation, Testing & Commissioning of Signages works.
Contract No: 2020_AAI_39373_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Sri Balaji Associates |  | SATIN NEO DIMENSIONS PVT LTD |  | Vertex Lightco Industries |  | DESIGN DIALOGUES INDIA PRIVATE LIMITED |  | Sapphire Media Services |  | Diamond Display Solutions Pvt Ltd
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | ALL Signage Item SPECIFIC INCLUSIONS:
2.00 | All signage shall be as per Sign Design drawing & technical specification .
3.00 | Supply, installation, testing and commision to be done by signage vendor as per site requirements.
4.00 | Cost to include braille application in all mandatory signs which are accessible for public.
5.00 | Vendor has to include Cost of all internal connections, connectors , RCCB and Wiring etc. as per site requirement.
6.00 | All illuminated Sign shall be protected with RCCB.
7.00 | National Building code of India SP:7 2016
8.00 | IS 9457-2005 Code of practice for safety colours and safety signs
9.00 | IS 10322:2:22 Part 5: Sec 8:2013-Luminaires Part 5 Particular Requiremenst Section 8 Emergency Lighting
10.00 | IS 12349-1988 Fire protection-Safety Signs
11.00 | IS 1644-1988 Code of practice for safety of buildings (General):Exit requirements and personal hazard
12.00 | IS 1646 Code of practice for fire safety of buildings Electrical installations.
13.00 | IS 12407-1988Graphic Symbols for fire Protection plans.
14.00 | Shade shall equivalent to Pantone shade as specified in sign details
15.00 | SECTION : A
16.00 | Airport Sign BOQ
17.00 | Entry Announcer
18.00 | Providing and fixing of sign with basic dimension 6820x3400x200 mm, internal structural frame made from 50x50x2 mm MS box section hot dipped galvanised PU painted (RAL 9006). Base Plate 8 mm thick SS Plate 304 grade, as per Sign design drawing with holes to fix it on holding down bolts anchored in concrete slab. 200mm deep portal has to be fabricated from 3 mm thick Aluminium Composite Panel with 0.25 mm PVDF, exterior grade, with Yellow Pantone 116C Vinyl Stuck over it. Primary channel letters 50mm thick and Secondary proﬁle cut letters 10mm thick, 3D cut letters in black glossy opaque cell cast acrylic to be mount on rear Sign facia as per drawings. (ST-1.6b-1) | 12.00 | Job |  | 41646.00 | 499752.00 | 68700.00 | 824400.00 | 152000.00 | 1824000.00 | 214999.00 | 2579988.00 | 295802.00 | 3549624.00 | 212706.65 | 2552479.80 | 499752.00 | Sri Balaji Associates
19.00 | Exit Announcer
20.00 | Providing and fixing of sign with basic dimension 8800x3400x200 mm, internal structural frame made from 50x50x2 mm MS box section hot dipped galvanised PU painted (RAL 9006). Base Plate 8 mm thick SS Plate 304 grade, as per Sign design drawingwith holes to fix it on holding down bolts anchored in concrete slab. 200mm deep portal has to be fabricated from 3 mm thick Aluminium Composite Panel with 0.25 mm PVDF, exterior grade, with Yellow Pantone 116C Vinyl Stuck over it. Primary channel letters 50mm thick and Secondary proﬁle cut letters 10mm thick, 3D cut letters in black glossy opaque cell cast acrylic to be mount on rear Sign facia as per drawings. (ST-1.6b-2) | 12.00 | Job |  | 50523.00 | 606276.00 | 77200.00 | 926400.00 | 172000.00 | 2064000.00 | 260999.00 | 3131988.00 | 350000.00 | 4200000.00 | 260237.25 | 3122847.00 | 606276.00 | Sri Balaji Associates
21.00 | Entry Info Announcer
22.00 | Providing and fixing of sign with basic dimension 3550x3400x200 mm, internal structural frame made from 50x50x2 mm MS box section hot dipped galvanised PU painted (RAL 9006). Base Plate 8 mm thick SS Plate 304 grade, as per Sign design drawingwith holes to fix it on holding down bolts anchored in concrete slab. 200mm deep portal has to be fabricated from 3 mm thick Aluminium Composite Panel with 0.25 mm PVDF, exterior grade, with Yellow Pantone 116C Vinyl Stuck over it. Primary and Secondary channel letters proﬁle cut letters 10mm thick, 3D cut letters in black glossy opaque cell cast acrylic to be mount on rear Sign facia as per drawings. Sign shall have provision for fixing the Indoor Direct View LED Screen as as per Sign design drawing including Supply, Installation, testing and commissioning of Indoor Direct View LED of dimention 2400x700 mm compelet in all respect as per technical specification. LED Screen to be protected with anti-reflective 5mm clear cell cast acrylic with LT 92% (ST-1.6bA) | 16.00 | Job |  | 30720.00 | 491520.00 | 189200.00 | 3027200.00 | 510000.00 | 8160000.00 | 175999.00 | 2815984.00 | 200000.00 | 3200000.00 | 428097.80 | 6849564.80 | 491520.00 | Sri Balaji Associates
23.00 | Airport Route Map
24.00 | Providing and fixing of illuminated sign with basic dimension 1800x1420x50 mm. All structural members in Stainless steel 75x75x3 mm Hollow box section brush finish 304 grade. 50x50x3 mm cross brackets are tied with structural post to receive sign frame. Pole to be fixed on SS base Plate and Gussets in 300x300x8mm thick SS Plate as per Sign design drawing with holes to fix it on holding down bolts anchored in concrete slab. The post (pole) shall be closed with a 200x200x1.5 mm thick SS cover plate as specified and approved by the Engineer-In- charge. Sign frame is 50mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion with inbuilt frame to receive the sign face. Provision of openable cable access to be provided in both structural posts. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign rear surface of sign is 2mm thick powder coated Pantone Black 6C Aluminium sheet. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. The sign shall have minimum lumen output of 12474 lm using LED module suitable for 240 V/50 Hz operation, with electronic controllers etc. (ST-2.3a) | 8.00 | Job |  | 52500.00 | 420000.00 | 91100.00 | 728800.00 | 44865.00 | 358920.00 | 90999.00 | 727992.00 | 65000.00 | 520000.00 | 89799.45 | 718395.60 | 358920.00 | Vertex Lightco Industries
26.00 | Floor Mounted Directional Sign - Single/Double
27.00 | Providing and fixing of illuminated sign with basic dimension 2100x865x50 mm. Structural pole of height 4000mm in Stainless steel 100x100x3 mm Hollow box section brush finish 304 grade. 50x50x2 mm cross brackets are tied with structural post to receive sign frame. Pole to be fixed on SS base Plate 8mm thick SS Plate as per Sign design drawingwith holes to fix it on holding down bolts anchored in concrete slab. The post (pole) shall be closed with a 200x200x1.5 mm thick SS cover plate as specified and approved by the Engineer-In- charge. Sign frame is 50mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion with inbuilt frame to receive the sign face. Provision of openable cable access to be provided in both structural posts. Providing and fixing tension rod in brush finished SS with the turn buckle system. Tension rod shall be fixed to the sign structure and the sign frame with SS gusset plates. The single flange sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. For single flange: Sign shall have minimum lumen output of 12680 lm using LED module suitable for 240 V/50 Hz operation, with electronic controllers etc .
28.00 | Floor Mounted Directional Sign - single (ST-2.1b-3) | 32.00 | Job |  | 45600.00 | 1459200.00 | 69000.00 | 2208000.00 | 50000.00 | 1600000.00 | 78999.00 | 2527968.00 | 56000.00 | 1792000.00 | 89601.25 | 2867240.00 | 1459200.00 | Sri Balaji Associates
29.00 | Floor Mounted Directional Sign - Double -ST-2.1b-4 (ST-2.1b-4) | 20.00 | Job |  | 62800.00 | 1256000.00 | 106090.00 | 2121800.00 | 75153.00 | 1503060.00 | 112999.00 | 2259980.00 | 99256.00 | 1985120.00 | 151469.55 | 3029391.00 | 1256000.00 | Sri Balaji Associates
30.00 | Wall Mounted FIDS & DSS
31.00 | Providing and fixing of sign with screen sizes as specified below in accordance to sign design drawing . FIDS screen to be suspended from VESA mounts fixed to the substrate. Vendor to investigate the materiality of the substrate as per site conditions and specify the mechanical fasteners accordingly. FIDS/DSS Vendor to provide VESA Mount and provision to fix the screens on the wall. Signage Contractor has to coordinate with FIDS/DSS contractor for detailed mounting arrangement of Screens and other devices (Remote Reset Unit, RJ45, IPC & power socket) to confirm the final signage structure dimension.
32.00 | ST-FIDS(2W): Two 49"screens SIGN (ST-FIDS(2W)) | 17.00 | Job |  | 46500.00 | 790500.00 | 31680.00 | 538560.00 | 20000.00 | 340000.00 | 240999.00 | 4096983.00 | 24570.00 | 417690.00 | 12555.00 | 213435.00 | 213435.00 | Diamond Display Solutions Pvt Ltd
33.00 | ST-FIDS(3W): Three 49"screens SIGN (ST-FIDS(3W)) | 6.00 | Job |  | 54000.00 | 324000.00 | 47520.00 | 285120.00 | 30000.00 | 180000.00 | 310999.00 | 1865994.00 | 29000.00 | 174000.00 | 18832.50 | 112995.00 | 112995.00 | Diamond Display Solutions Pvt Ltd
34.00 | ST-FIDS(4W): Four 55"screens SIGN (ST-FIDS(4W)) | 7.00 | Job |  | 61500.00 | 430500.00 | 72576.00 | 508032.00 | 40000.00 | 280000.00 | 330999.00 | 2316993.00 | 62000.00 | 434000.00 | 18832.50 | 131827.50 | 131827.50 | Diamond Display Solutions Pvt Ltd
35.00 | Process Map
36.00 | Providing and fixing of illuminated sign with basic dimension 2350x250x50 mm, with sign frame 50mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign face to be aligned to the FIDS screen face as per site conditions with hidden spacers/details. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. The sign shall have minimum lumen output of 3696 lm using LED module suitable for 240 V/50 Hz operation, with electronic controllers etc. (ST-Info) | 7.00 | Job |  | 57040.00 | 399280.00 | 29543.00 | 206801.00 | 10553.00 | 73871.00 | 23999.00 | 167993.00 | 47500.00 | 332500.00 | 20656.87 | 144598.09 | 73871.00 | Vertex Lightco Industries
37.00 | Wall Mounted Check In Aisle Indicator
38.00 | Providing and fixing of sign (L Shape) with basic dimension 2x(1000x1000x50mm), with internal structure to be made from 50x50x2 mm MS hot dipped galvanised PU Painted in colour RAL 9006, with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign rear surface of sign is 2mm thick powder coated Pantone Black 6C Aluminium sheet. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. All text, information and icons in 50mm 3D cut black glossy opaque cell cast acrylic letters punch through rear surface with vinyl pasting. (ST-Check In) | 14.00 | Job |  | 50700.00 | 709800.00 | 64781.00 | 906934.00 | 22000.00 | 308000.00 | 64999.00 | 909986.00 | 47500.00 | 665000.00 | 53529.45 | 749412.30 | 308000.00 | Vertex Lightco Industries
39.00 | Ceiling Hung Facility Announcer with Screen
40.00 | Providing and fixing of sign with basic dimension 1500x665x150 mm, with sign frame 150mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion to receive the sign face. 25mm Aluminium extrusions hinged for easy open. 25 x 25 x 2 mm Aluminium square sections cross tied with sign frame as per drawing. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. Acrylic facia to be cut and to be removed in front LCD screen. Suspenders with specs 50x50x2mm Stainless Steel 304 grade hollow sections mounted on slabs / beams / walls. Vendor to integrate all ventilation, hardware, electrical and data requirements. Provision of openable cable access to be provided in both structural suspenders. FIDS/DSS screen to be suspended from VESA mounts fixed to the substrate. Vendor to investigate the materiality of the substrate as per site conditions and specify the mechanical fasteners accordingly. FIDS/DSS Vendor to provide VESA Mount and provision to fix the screens on the wall. Signage Contractor has to coordinate with FIDS/DSS contractor for detailed mounting arrangement of Screens and other devices (Remote Reset Unit, RJ45, IPC & power socket) to confirm the final signage structure dimension. (ST-2.2e - 2) | 251.00 | Job |  | 35560.00 | 8925560.00 | 24612.00 | 6177612.00 | 30000.00 | 7530000.00 | 85777.00 | 21530027.00 | 23100.00 | 5798100.00 | 41066.68 | 10307736.68 | 5798100.00 | Sapphire Media Services
41.00 | Ceiling Hung Directional Sign
42.00 | Providing and fixing of illuminated sign with basic dimension 2100x865x50 mm with sign frame 50mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion to receive the sign face. Provision of openable cable access to be provided in both structural suspenders. Suspenders with specs 25x25x2mm Stainless Steel 304 grade hollow sections mounted on slabs/beams/walls. Vendor to integrate all ventilation, hardware, electrical and data requirements. Provision of openable cable access to be provided in both structural suspenders. Sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. The sign shall have minimum lumen output of 12680 lm using LED module suitable for 240 V/50 Hz operation, with electronic controllers etc. (ST-2.1a) | 122.00 | Job |  | 46898.00 | 5721556.00 | 40686.00 | 4963692.00 | 40000.00 | 4880000.00 | 23999.00 | 2927878.00 | 28000.00 | 3416000.00 | 56374.50 | 6877689.00 | 2927878.00 | DESIGN DIALOGUES INDIA PRIVATE LIMITED
43.00 | Security Counter Sign
44.00 | Providing and fixing of sign with basic dimension 1220x665x150 mm, with sign frame 150mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion to receive the sign face. 25mm Aluminium extrusions hinged for easy open. 25 x 25 x 2 mm Aluminium square sections cross tied with sign frame as per drawing. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. Acrylic facia to be cut and to be removed in front LCD screen. Suspenders with specs 50x50x2mm Stainless Steel 304 grade hollow sections mounted on slabs / beams / walls. Vendor to integrate all ventilation, hardware, electrical and data requirements. Provision of openable cable access to be provided in both structural suspenders. FIDS/DSS screen to be suspended from VESA mounts fixed to the substrate. Vendor to investigate the materiality of the substrate as per site conditions and specify the mechanical fasteners accordingly. FIDS/DSS Vendor to provide VESA Mount and provision to fix the screens on the wall. Signage Contractor has to coordinate with FIDS/DSS contractor for detailed mounting arrangement of Screens and other devices (Remote Reset Unit, RJ45, IPC & power socket) to confirm the final signage structure dimension. (ST-DSS (1)) | 17.00 | Job |  | 20848.00 | 354416.00 | 36050.00 | 612850.00 | 30000.00 | 510000.00 | 95099.00 | 1616683.00 | 19500.00 | 331500.00 | 31792.15 | 540466.55 | 331500.00 | Sapphire Media Services
45.00 | Floor Mounted Directional Sign with FIDS
46.00 | Providing and fixing of illuuminated sign with basic dimension 2100x1300x50 mm. All structural members in Stainless steel 100x100x3 mm Hollow box section brush finish 304 grade. 50x50x3 mm cross brackets are tied with structural post to receive sign frame. Pole to be fixed on SS base Plate and Gussets in 300x300x8mm thick SS Plate as per Sign design drawingwith holes to fix it on holding down bolts anchored in concrete slab. The post (pole) shall be closed with a 200x200x1.5 mm thick SS cover plate as specified and approved by the Engineer-In- charge. Sign frame is 50mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion with inbuilt frame to receive the sign face. Provision of openable cable access to be provided in both structural posts. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign rear surface of sign is 2mm thick powder coated Pantone Black 6C Aluminium sheet. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. FIDS screen to be suspended from VESA mounts fixed to the substrate. Sign rear surface of sign is 2mm thick powder coated Pantone Black 6C Aluminium sheet to hide rear of the LCD Screens. Vendor to integrate all ventilation, hardware, electrical and data requirements. Vendor to investigate the materiality of the substrate as per site conditions and specify the mechanical fasteners accordingly. FIDS/DSS Vendor to provide VESA Mount and provision to fix the screens on the wall. Signage Contractor has to coordinate with FIDS/DSS contractor for detailed mounting arrangement of Screens and other devices (Remote Reset Unit, RJ45, IPC & power socket) to confirm the final signage structure dimension. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. Refer specification for details about the sign. The sign shall have minimum lumen output of 14784 lm using LED module suitable for 240 V/50 Hz operation, with electronic controllers etc. (ST-2.1b-1) | 2.00 | Job |  | 109496.00 | 218992.00 | 122480.00 | 244960.00 | 150000.00 | 300000.00 | 300099.00 | 600198.00 | 102000.00 | 204000.00 | 120705.10 | 241410.20 | 204000.00 | Sapphire Media Services
47.00 | Floor Mounted FIDS & DSS
48.00 | Providing and fixing of sign with basic dimension based on LCD Screen sizes as specified below. All structural members in Stainless steel 100x100x3 mm Hollow box section brush finish 304 grade. 50x50x3 mm cross brackets are tied with structural post to LCD Mounting. LCD will be mounted onto 2mm thick powdercoated Aluminium plate bolted on cross brackets. 50x25x2 mm thick SS brush finish 304 grade bolted on cross brackets for Electrical, IT provisions to mount on. Pole to be fixed on SS base Plate and Gussets in 300x300x6mm thick SS Plate as per Sign design drawingwith holes to fix it on holding down bolts anchored in concrete slab. The post (pole) shall be closed with a 200x200x1.5 mm thick SS cover plate as specified and approved by the Engineer-In- charge. Provision of openable cable access to be provided in both structural posts. FIDS screen to be suspended from VESA mounts fixed to the substrate. Sign rear surface of sign is 2mm thick powder coated Pantone Black 6C Aluminium sheet to hide rear of the LCD Screens. Vendor to integrate all ventilation, hardware, electrical and data requirements. Vendor to investigate the materiality of the substrate as per site conditions and specify the mechanical fasteners accordingly. FIDS/DSS Vendor to provide VESA Mount and provision to fix the screens on the wall. Signage Contractor has to coordinate with FIDS/DSS contractor for detailed mounting arrangement of Screens and other devices (Remote Reset Unit, RJ45, IPC & power socket) to confirm the final signage structure dimension. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. Refer specification for details about the sign.
49.00 | ST-FIDS(2F): Two 49"screens SIGN (ST-FIDS(2F)) | 2.00 | Job |  | 171742.00 | 343484.00 | 52346.00 | 104692.00 | 70000.00 | 140000.00 | 245955.00 | 491910.00 | 49000.00 | 98000.00 | 49025.00 | 98050.00 | 98000.00 | Sapphire Media Services
50.00 | ST-FIDS(3F): Three 49"screens SIGN (ST-FIDS(3F)) | 12.00 | Job |  | 245988.00 | 2951856.00 | 60322.00 | 723864.00 | 90000.00 | 1080000.00 | 305999.00 | 3671988.00 | 59000.00 | 708000.00 | 83714.25 | 1004571.00 | 708000.00 | Sapphire Media Services
51.00 | ST-FIDS(4F): Four 55"screens SIGN (ST-FIDS(4F)) | 4.00 | Job |  | 352790.00 | 1411160.00 | 72828.00 | 291312.00 | 110000.00 | 440000.00 | 334999.00 | 1339996.00 | 83000.00 | 332000.00 | 101742.00 | 406968.00 | 291312.00 | SATIN NEO DIMENSIONS PVT LTD
52.00 | Boarding Gates Sign
53.00 | Providing and fixing of sign with basic dimension 3000x3400x200 mm (Size include 2 signs as per drawing), internal structural frame made from 50x50x2 mm MS box section hot dipped galvanised PU painted (RAL 9006). Base Plate 8 mm thick SS Plate 304 grade, as per Sign design drawingwith holes to fix it on holding down bolts anchored in concrete slab. 200mm deep portal has to be fabricated from 5 mm thick cell cast acrylic, with Yellow Pantone 116C Vinyl Stuck over it. Primary channel letters 50mm thick and Secondary proﬁle cut letters 10mm thick, 3D cut letters in black glossy opaque cell cast acrylic to be mount on rear Sign facia as per drawings submitted. Acrylic facia to be cut and to be removed in front LCD screen. FIDS / DSS screen to be suspended from VESA mounts fixed to the substrate. Vendor to investigate the materiality of the substrate as per site conditions and specify the mechanical fasteners accordingly. FIDS/DSS Vendor to provide VESA Mount and provision to fix the screens on the wall. Signage Contractor has to coordinate with FIDS/DSS contractor for detailed mounting arrangement of Screens and other devices (Remote Reset Unit, RJ45, IPC & power socket) to confirm the final signage structure dimension. (ST-1.6b-3) | 44.00 | Job |  | 149800.00 | 6591200.00 | 79616.00 | 3503104.00 | 170945.00 | 7521580.00 | 94999.00 | 4179956.00 | 210000.00 | 9240000.00 | 238982.90 | 10515247.60 | 3503104.00 | SATIN NEO DIMENSIONS PVT LTD
54.00 | Baggage Belt Allocation FIDS
55.00 | Providing and fixing of sign with screen sizes as specified below and in accordance to sign drawing. Suspenders with specs 50x50x2mm Stainless Steel 304 grade hollow sections mounted on slabs/beams/walls. 2mm thick 450x450mm SS base plate bolted on 50x50x2 mm SS square brackets. The plate will have adjustable bolting holes for mounting VESA Mount. 50x25x2 mm thick SS brush finish 304 grade bolted on cross brackets for Electrical, IT provisions to mount on. Vendor to integrate all ventilation, hardware, electrical and data requirements. Provision of openable cable access to be provided in both structural suspenders. FIDS screen to be suspended from VESA mounts fixed to the substrate. Vendor to investigate the materiality of the substrate as per site conditions and specify the mechanical fasteners accordingly. FIDS/DSS Vendor to provide VESA Mount and provision to fix the screens on the wall. Signage Contractor has to coordinate with FIDS/DSS contractor for detailed mounting arrangement of Screens and other devices (Remote Reset Unit, RJ45, IPC & power socket) to confirm the final signage structure dimension. Sign rear surface of sign is 2mm thick powder coated Pantone Black 6C Aluminium sheet is bent in 'L" shape to hide rear and bottom of the LCD Screens.
56.00 | ST-FIDS(3C): Three 49"screens SIGN (1 screen per sign) (ST-FIDS(3C)) | 3.00 | Job |  | 97996.00 | 293988.00 | 78850.00 | 236550.00 | 24000.00 | 72000.00 | 135259.00 | 405777.00 | 18500.00 | 55500.00 | 92111.50 | 276334.50 | 55500.00 | Sapphire Media Services
57.00 | ST-FIDS(4C): Three 49"screens SIGN (2 screens per sign) (ST-FIDS(4C)) | 1.00 | Job |  | 166492.00 | 166492.00 | 88165.00 | 88165.00 | 30000.00 | 30000.00 | 160999.00 | 160999.00 | 13000.00 | 13000.00 | 75468.25 | 75468.25 | 13000.00 | Sapphire Media Services
58.00 | Baggage Carousel Information FIDS
59.00 | Providing and fixing of sign with basic dimension based on LCD Screen sizes as per sign drawing. All structural members in Stainless steel 100x100x3 mm Hollow box section brush finish 304 grade. 100x100x3 mm cross brackets are tied with structural post to LCD Mounting. Pole to be fixed on SS base Plate 8mm thick as per Sign design drawingwith holes to fix it on holding down bolts anchored in concrete slab. The post (pole) shall be closed with a 200x200x1.5 mm thick SS cover plate as specified and approved by the Engineer-In- charge. Provision of openable cable access to be provided in both structural posts. FIDS screen to be suspended from VESA mounts fixed to the substrate. Sreens are mounted on 2mm thick powder coated Pantone Black 6C Aluminium sheet. Vendor to integrate all ventilation, hardware, electrical and data requirements. Vendor to investigate the materiality of the substrate as per site conditions and specify the mechanical fasteners accordingly. FIDS/DSS Vendor to provide VESA Mount and provision to fix the screens on the wall. Signage Contractor has to coordinate with FIDS/DSS contractor for detailed mounting arrangement of Screens and other devices (Remote Reset Unit, RJ45, IPC & power socket) to confirm the final signage structure dimension. (ST-FIDS(1F)) | 20.00 | Job |  | 31500.00 | 630000.00 | 40560.00 | 811200.00 | 50000.00 | 1000000.00 | 53799.00 | 1075980.00 | 28000.00 | 560000.00 | 63990.00 | 1279800.00 | 560000.00 | Sapphire Media Services
60.00 | Belt No. Sign
61.00 | Providing and fixing of illuminated sign with basic dimension 600x600mm (4 such faces in each sign). All structural members in Stainless steel 75x75x3 mm Hollow box section brush finish 304 grade. Pole to be fixed on base Plate in 300x300x8mm thick SS Plate as per Sign design drawingwith holes to fix it on holding down bolts anchored in concrete slab. The post (pole) shall be closed with a 200x200x1.5 mm thick SS cover plate as specified and approved by the Engineer-In- charge. Provision of openable cable access to be provided in both structural posts. Bottom panel of 450x450x2 mm MS Panel, PU Painted in colour to match Vinyl Black of 95%(Pantone Black 6C). Entire Sign face, all 4 sides have vinyl pasted over 5mm thick double side UV coated White translucent 040 cell cast acrylic. The sign shall have minimum lumen output of 1540 lm using LED module suitable for 240 V/50 Hz operation, with electronic controllers etc. (ST-2.2h) | 20.00 | Job |  | 42700.00 | 854000.00 | 46300.00 | 926000.00 | 27000.00 | 540000.00 | 53799.00 | 1075980.00 | 23000.00 | 460000.00 | 50445.25 | 1008905.00 | 460000.00 | Sapphire Media Services
62.00 | Door Mounted Facility Announcer
63.00 | Providing and fixing of sign with basic dimension 600x300x25 mm, with sign frame 25mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion with inbuilt frame to receive the sign face. Sign base structure to be screwed onto door with SS self-tapping screws. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. (ST-2.2c) | 140.00 | Job |  | 7500.00 | 1050000.00 | 2403.00 | 336420.00 | 10000.00 | 1400000.00 | 6099.00 | 853860.00 | 10000.00 | 1400000.00 | 2936.70 | 411138.00 | 336420.00 | SATIN NEO DIMENSIONS PVT LTD
64.00 | Lift Directory Sign
65.00 | Providing and fixing of illuminated sign with basic dimension 460x800x50 mm, with sign frame 50mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign rear surface of sign is 2mm thick powder coated Pantone Black 6C Aluminium sheet. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. The sign shall have minimum lumen output of 1617 lm using LED module suitable for 240 V/50 Hz operation, with electronic controllers etc. (ST-2.3b) | 76.00 | Job |  | 19740.00 | 1500240.00 | 7420.00 | 563920.00 | 16000.00 | 1216000.00 | 21412.00 | 1627312.00 | 18000.00 | 1368000.00 | 11861.20 | 901451.20 | 563920.00 | SATIN NEO DIMENSIONS PVT LTD
66.00 | Lift No. Sign
67.00 | Providing and fixing of illuminated sign with basic dimension 400x400x50 mm, with sign frame 50mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. The sign shall have minimum lumen output of 3170 lm using LED module suitable for 240 V/50 Hz operation, with electronic controllers etc .
68.00 | Type 1- Wall projected : 400x400x50 mm (ST-2.4c) | 19.00 | Job |  | 11870.00 | 225530.00 | 5583.00 | 106077.00 | 9000.00 | 171000.00 | 19513.00 | 370747.00 | 8300.00 | 157700.00 | 6676.15 | 126846.85 | 106077.00 | SATIN NEO DIMENSIONS PVT LTD
69.00 | Washroom/ Drinking Water/ Baby Care
70.00 | Providing and fixing of illuminated sign with basic dimension 450x450x50 mm, with sign frame 50mm x 2.5mm (Wall thickness) wide powder coated, colour RAL 9006 Aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. For Type 2, sign rear surface of sign is 2mm thick powder coated Pantone Black 6C Aluminium sheet. Sign face is 5mm thick double side UV coated white 040 cell cast arylic with vinyl pasted over it as per grpahics. The sign shall have minimum lumen output of 3487 lm for Type 1 & 1155 lm for Type 2, using LED module suitable for 240 V/50 Hz operation, with electronic controllers etc .
71.00 | Type 1- Wall projected : 450x450x50 mm (ST-2.4a) | 63.00 | Job |  | 17640.00 | 1111320.00 | 6277.00 | 395451.00 | 10000.00 | 630000.00 | 11612.00 | 731556.00 | 9100.00 | 573300.00 | 7176.65 | 452128.95 | 395451.00 | SATIN NEO DIMENSIONS PVT LTD
72.00 | Type 2- Wall mounted : 450x450x50 mm (ST-2.4a) | 110.00 | Job |  | 17640.00 | 1940400.00 | 4622.00 | 508420.00 | 4400.00 | 484000.00 | 11612.00 | 1277320.00 | 8500.00 | 935000.00 | 6835.40 | 751894.00 | 484000.00 | Vertex Lightco Industries
73.00 | Service Area Sign
74.00 | Providing and fixing of sign with basic dimension 250x300x3 mm, with sign facia 3mm thk. Black cell cast acrylic digitally printed graphics, mounted on walls/claddings/ panelling using VHB Tape. (ST-2.4b) | 230.00 | Job |  | 1000.00 | 230000.00 | 389.00 | 89470.00 | 500.00 | 115000.00 | 200.00 | 46000.00 | 300.00 | 69000.00 | 982.80 | 226044.00 | 46000.00 | DESIGN DIALOGUES INDIA PRIVATE LIMITED
75.00 | Glass Graphic Sign
76.00 | Providing and fixing of all vinyl application onto glass. Cost to be quoted including printing ,cutting etc. as per graphic and site requirement. All vinyl cut surfaces to be protected with overlaminate. Vinyl shades shall be provided by vendor as specified in the intent drawings. (ST-Graphic) | 2200.00 | SQFT |  | 300.00 | 660000.00 | 125.00 | 275000.00 | 500.00 | 1100000.00 | 100.00 | 220000.00 | 145.00 | 319000.00 | 150.00 | 330000.00 | 220000.00 | DESIGN DIALOGUES INDIA PRIVATE LIMITED
77.00 | SECTION : B
78.00 | EMERGENCY LIGHTING & EXIT SYSTEM (CENTRAL BATTERY)
79.00 | Suply, Installation, Testing & Commissioing of Fully recessed Luminaire, Addressable and monitored 250 lm LED luminaire with Glow Wire Test of Plastic Materials 650 °C with Ingress protection IP20 and Fully compliant with requirements of the fire and safety code of practice & the respective EN 60598-2-22 and the system designed in compliance with EN1838 standards, with Backup for 90 Minutes operation via Central Battery System- suitable for staircase/ Corridor Areas emergency luminaires, Minimum size 327MM x 213 MM complaint to NBC 2016/ NFPA | 390.00 | Nos |  | 6720.00 | 2620800.00 | 4380.00 | 1708200.00 | 2400.00 | 936000.00 | 8999.00 | 3509610.00 | 2500.00 | 975000.00 | 21365.00 | 8332350.00 | 936000.00 | Vertex Lightco Industries
80.00 | Suply, Installation, Testing & Commissioing of Double SIDED WALL/SURFACE mounting Luminaire, Addressable and monitored, EXIT Luminaire, IP44 with 30 meter viewing distance with Glow Wire Test of Plastic Materials 650 °C, High power LED 230VAC/DC and fully compliant with requirements of the fire and safety code of practice & the respective EN 60598-2-22 and the system designed in compliance with EN1838 standards, with Backup for 90 Minutes operation via Central Battery System. Minimum size 327MM x 213 MM complaint to NBC 2016/ NFPA | 331.00 | Nos |  | 5880.00 | 1946280.00 | 4920.00 | 1628520.00 | 4800.00 | 1588800.00 | 12999.00 | 4302669.00 | 5570.00 | 1843670.00 | 21365.00 | 7071815.00 | 1588800.00 | Vertex Lightco Industries
81.00 | Suply, Installation, Testing & Commissioing of SINGLE SIDED WALL/SURFACE mounting Luminaire, Addressable and monitored, EXIT Luminaire, IP44 with 30 meter viewing distance with Glow Wire Test of Plastic Materials 650 °C, High power LED 230VAC/DC and fully compliant with requirements of the fire and safety code of practice & the respective EN 60598-2-22 and the system designed in compliance with EN1838 standards, with Backup for 90 Minutes operation via Central Battery System. Minimum size 327MM x 213 MM complaint to NBC 2016/ NFPA | 220.00 | Nos |  | 5880.00 | 1293600.00 | 4140.00 | 910800.00 | 3600.00 | 792000.00 | 9999.00 | 2199780.00 | 5570.00 | 1225400.00 | 18520.00 | 4074400.00 | 792000.00 | Vertex Lightco Industries
82.00 | Suply, Installation, Testing & Commissioing of CENTRAL BATTERY SYSTEM PANEL,Emergency System Panel with Liquid Crystal Display (LCD) for the simultaneous display of the system status and fault with Monitor and control all test cycles and functions and volt free contacts for internal fault, Shortened inspection effort due to CEWA GUARD technology, automatic function monitoring of up to 20 luminaires per circuit as per IEC code. With volt free contacts for internal fault, battery mode operation & external fault.The panel shall supervise the battery status such as Battery Over voltage / Battery Under voltage. The panel shall be fitted with a deep discharge protection circuit. Degree protection of IP54. The unit shall be fitted with a deep discharge protection circuit, which has two operation phases: When in battery mode the battery voltage decreases to 195V, a preliminary deep discharge alarm shall be given. When the battery voltage decreases to 175V, the load shall be disconnected. The circuit shall allow the battery to increase its voltage without switching the load ON again, thus avoiding detrimental full discharge. Main power supply required. The panel shall automatically return to normal operation, once the mains supply recovers. Fully compliant with requirements of designed and installed to meet the fire and safety code of practice & the respective EN 60598-2-22 and the system designed in compliance with EN50171, EN50272-2, EN50172, and EN1838 standards EN Standards
83.00 | 24 circuit panel with battery backup | 2.00 | Set |  | 200000.00 | 400000.00 | 420000.00 | 840000.00 | 200000.00 | 400000.00 | 350000.00 | 700000.00 | 14500.00 | 29000.00 | 5036260.00 | 10072520.00 | 29000.00 | Sapphire Media Services
84.00 | Suply, Installation, Testing & Commissioing of Intelligent Control Module, Intelligent controllers for 8 sub circuit monitoring contacts to one IC or 8 switching contacts per IC. IC shall be on a dedicated RS485 bus topology and it should be possible to connect a total of 32 IC’s per bus. The IC should comply to EN 61347-2-11:2001 in conjunction with EN 61347-1:2001. | 52.00 | Nos |  | 50000.00 | 2600000.00 | 912.00 | 47424.00 | 50000.00 | 2600000.00 | 25999.00 | 1351948.00 | 10000.00 | 520000.00 | 98635.00 | 5129020.00 | 47424.00 | SATIN NEO DIMENSIONS PVT LTD
85.00 | Suply, Installation, Testing & Commissioing of Distribution Panel, Hybrid operation of maintained light, non-maintained light and switched maintained light in a single circuit can be programmed with no additional data cable.Up to 20 luminaires can be monitored individually, AC/DC switching per module, Separate AV-feed for rental current, LED indicates fault and Run/ON for each circuit, Supplies electronic ballast and LED luminaires, DIN rail mounting, main power supply required. Comply to EN 61347-2-11:2001 in conjunction with EN 61347-1:2001. | 10.00 | Nos |  | 250000.00 | 2500000.00 | 4800.00 | 48000.00 | 50000.00 | 500000.00 | 35999.00 | 359990.00 | 10000.00 | 100000.00 | 120660.00 | 1206600.00 | 48000.00 | SATIN NEO DIMENSIONS PVT LTD
86.00 | Suply, Installation, Testing & Commissioing of Web Controller, PC with web conroller to monitored, design, contro & maintain luminaires. The web controller require PC. It takes over all the control and test functions, and it generates a comprehensive electronic log book for all connected system. | 1.00 | Nos |  | 300000.00 | 300000.00 | 330000.00 | 330000.00 | 200000.00 | 200000.00 | 259999.00 | 259999.00 | 65500.00 | 65500.00 | 1176890.00 | 1176890.00 | 65500.00 | Sapphire Media Services
87.00 | Suply, Installation, Testing & Commissioing of BATTERIES, Batteries shall be maintenance free VRLA sealed lead acid gas recombination type with a minimum design life of 10 years at prevailing ambient temperature. They shall have extremely low gas generation, low self-discharge and have permanently sealed pressure release vents. The batteries shall be sized to power complete system for 90 Minutes following mains failure at 100% light output for all emergency lamps.
88.00 | Sealed lead acid battery 18x 12V/33Ah with Enclosure | 1.00 | Set |  | 150000.00 | 150000.00 | 168480.00 | 168480.00 | 30000.00 | 30000.00 | 259999.00 | 259999.00 | 7220.00 | 7220.00 | 6152785.00 | 6152785.00 | 7220.00 | Sapphire Media Services
89.00 | Suply, Installation, Testing & Commissioing of BACNET/ IP Interface for integration with 3rd party BMS | 1.00 | Nos |  | 350000.00 | 350000.00 | 39000.00 | 39000.00 | 30000.00 | 30000.00 | 25999.00 | 25999.00 | 10000.00 | 10000.00 | 905450.00 | 905450.00 | 10000.00 | Sapphire Media Services
90.00 | Suply & Laying of 2C x 1.5 mm2, Fire Survival Armoured cable (600/1000V) with Class-2 annealed copper (7/0.53) Muiltistranded conductor having cross linkable Halogen Free insulation with Glass Mica (Fire barrier) tape along with ZHFR inner sheath Glass fibre tape over laidup cores & with Carbon Tape over the inner sheath and outer sheath with ZHFR as per BS: 7846:2009. Should retain circuit integrity upto minimum 2 Hours @ 950 Deg C as per BS 5839, BS EN 50200 + Annex-E & BS 6387 C.W.Z., feild cable for luminaires to control module | 14500.00 | Mtrs. |  | 110.00 | 1595000.00 | 160.00 | 2320000.00 | 155.00 | 2247500.00 | 200.00 | 2900000.00 | 220.00 | 3190000.00 | 180.00 | 2610000.00 | 1595000.00 | Sri Balaji Associates
91.00 | Suply & Laying of 4C x 1.5 mm2, Screen cable (600/1000V) with Class-2 annealed copper (7/0.53) Muiltistranded conductor having cross linkable Halogen Free insulation with Glass Mica (Fire barrier) tape along with ZHFR inner sheath Glass fibre tape over laidup cores & with Carbon Tape over the inner sheath and outer sheath with ZHFR as per BS: 7846:2009. Should retain circuit integrity upto minimum 2 Hours @ 950 Deg C as per BS 5839, BS EN 50200 + Annex-E & BS 6387 C.W.Z., feild cable from control module to distribution panel | 1700.00 | Mtrs. |  | 160.00 | 272000.00 | 78.00 | 132600.00 | 270.00 | 459000.00 | 200.00 | 340000.00 | 320.00 | 544000.00 | 198.00 | 336600.00 | 132600.00 | SATIN NEO DIMENSIONS PVT LTD
92.00 | Suply & Laying of 2C x 16 mm2 battery cable, for mains & battery supply | 1700.00 | Mtrs. |  | 250.00 | 425000.00 | 450.00 | 765000.00 | 325.00 | 552500.00 | 200.00 | 340000.00 | 280.00 | 476000.00 | 196.00 | 333200.00 | 333200.00 | Diamond Display Solutions Pvt Ltd
93.00 | SECTION : C
94.00 | Evacuation Plan
95.00 | Providing, fixing and commissioning of single sided photoluminescent signs. Vendor fix the signs in position at the specified locations. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing . Minimum Size: 594x420 mm complaint to NBC 2016/ NFPA | 80.00 | Nos. |  | 2500.00 | 200000.00 | 1025.00 | 82000.00 | 1500.00 | 120000.00 | 599.00 | 47920.00 | 7000.00 | 560000.00 | 2013.00 | 161040.00 | 47920.00 | DESIGN DIALOGUES INDIA PRIVATE LIMITED
96.00 | Floor indicator
97.00 | Providing, fixing and commissioning of single sided photoluminescent signs. Vendor fix the signs in position at the specified locations. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing . Minimum Size:400x400 complaint to NBC 2016/ NFPA | 75.00 | Nos. |  | 1500.00 | 112500.00 | 657.00 | 49275.00 | 1000.00 | 75000.00 | 599.00 | 44925.00 | 1900.00 | 142500.00 | 1292.00 | 96900.00 | 44925.00 | DESIGN DIALOGUES INDIA PRIVATE LIMITED
98.00 | Push/Pull Bar
99.00 | 1) Providing, fixing and commissioning of single sided non Illuminated signs as per design submitted.Sign made in photoluminescent sheet. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing. Minimum Size:400x150 mm complaint to NBC 2016/ NFPA | 80.00 | Nos. |  | 550.00 | 44000.00 | 279.00 | 22320.00 | 550.00 | 44000.00 | 599.00 | 47920.00 | 850.00 | 68000.00 | 485.00 | 38800.00 | 22320.00 | SATIN NEO DIMENSIONS PVT LTD
100.00 | Fire Extinguisher
101.00 | 1) Providing, fixing and commissioning of single sided non Illuminated signs as per design submitted. Sign made in photoluminescent sheet. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing. Minimum Size:150x200 mm complaint to NBC 2016/ NFPA | 600.00 | Nos. |  | 300.00 | 180000.00 | 161.00 | 96600.00 | 500.00 | 300000.00 | 599.00 | 359400.00 | 700.00 | 420000.00 | 252.00 | 151200.00 | 96600.00 | SATIN NEO DIMENSIONS PVT LTD
102.00 | Call Button
103.00 | 1) Providing, fixing and commissioning of single sided non Illuminated signs as per design submitted. Sign made in photoluminescent sheet. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing. Minimum Size:150x200 mm complaint to NBC 2016/ NFPA | 120.00 | Nos. |  | 300.00 | 36000.00 | 161.00 | 19320.00 | 300.00 | 36000.00 | 599.00 | 71880.00 | 750.00 | 90000.00 | 252.00 | 30240.00 | 19320.00 | SATIN NEO DIMENSIONS PVT LTD
104.00 | Fire Hose cabinet
105.00 | 1) Providing, fixing and commissioning of single sided non Illuminated signs as per design submitted. Sign made in photoluminescent sheet. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing. Minimum Size:400x200 complaint to NBC 2016/ NFPA | 200.00 | Nos. |  | 650.00 | 130000.00 | 430.00 | 86000.00 | 600.00 | 120000.00 | 599.00 | 119800.00 | 750.00 | 150000.00 | 645.00 | 129000.00 | 86000.00 | SATIN NEO DIMENSIONS PVT LTD
107.00 | Fire door Keep Closed
108.00 | 1) Providing, fixing and commissioning of single sided non Illuminated signs as per design submitted. Sign made in photoluminescent sheet. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing. Minimum Size:200x200 mm complaint to NBC 2016/ NFPA | 80.00 | Nos. |  | 375.00 | 30000.00 | 200.00 | 16000.00 | 400.00 | 32000.00 | 599.00 | 47920.00 | 590.00 | 47200.00 | 323.00 | 25840.00 | 16000.00 | SATIN NEO DIMENSIONS PVT LTD
109.00 | Fireman's Lift Sign
110.00 | 1) Providing, fixing and commissioning of single sided non Illuminated signs as per design submitted. Sign made in photoluminescent sheet. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing. Minimum Size:400x150 mm complaint to NBC 2016/ NFPA | 80.00 | Nos. |  | 600.00 | 48000.00 | 279.00 | 22320.00 | 460.00 | 36800.00 | 599.00 | 47920.00 | 2800.00 | 224000.00 | 485.00 | 38800.00 | 22320.00 | SATIN NEO DIMENSIONS PVT LTD
111.00 | Fire Lift Sign
112.00 | 1) Providing, fixing and commissioning of single sided non Illuminated signs as per design submitted. Sign made in photoluminescent sheet. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing. Minimum Size:200x200 mm complaint to NBC 2016/ NFPA | 80.00 | Nos. |  | 1800.00 | 144000.00 | 215.00 | 17200.00 | 400.00 | 32000.00 | 599.00 | 47920.00 | 1400.00 | 112000.00 | 323.00 | 25840.00 | 17200.00 | SATIN NEO DIMENSIONS PVT LTD
113.00 | Exit Signage
114.00 | 1) Providing, fixing and commissioning of single sided non Illuminated signs as per design submitted. Sign made in photoluminescent sheet. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing. Minimum Size:400x150 mm complaint to NBC 2016/ NFPA | 75.00 | Nos. |  | 600.00 | 45000.00 | 279.00 | 20925.00 | 460.00 | 34500.00 | 599.00 | 44925.00 | 2000.00 | 150000.00 | 485.00 | 36375.00 | 20925.00 | SATIN NEO DIMENSIONS PVT LTD
115.00 | Please Hold the Hand Rail + do not use mobile while on stairs
116.00 | Providing, fixing and commissioning of single sided photoluminescent signs. Primary and secondary route to be marked. Rigid Photo luminescent based Glow-in-the-dark rigid sheet with high intensity luminous properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported links, Thickness : 1 mm, Service Temp. : -10 to + 60°C, Application : Suitable for INDOOR use only, Surface Colour : Greenish Yellow, Visibility : Glow visible up to> 24 hours in total darkness, Properties : *Fungistatic *Non-radioactive *Contains no lead or Phosphorus * No health or environmental problem *Simple to install & easy to maintain, can be screwed or just peel off to stick *Self-Extinguishing. Minimum Size:600x150 mm complaint to NBC 2016/ NFPA | 75.00 | Nos. |  | 900.00 | 67500.00 | 430.00 | 32250.00 | 600.00 | 45000.00 | 599.00 | 44925.00 | 2000.00 | 150000.00 | 726.00 | 54450.00 | 32250.00 | SATIN NEO DIMENSIONS PVT LTD
117.00 | SECTOIN : D
118.00 | All inclusive Comprehensive Maintenance of Airport Sign, Emergency Lighting & Exit System (Central Battery) & Photoluminescent Signs after DLP as provided under the main contract including trouble shooting, preventive maintenance and breakdown maintenance etc. as required as per good engineering practice, instructions of Engineer-in-Charge and as per terms and conditions specified tender
119.00 | 1st year after 2 Years of DLP.
120.00 | 2nd year after 2 Years of DLP.
121.00 | 3rd year after 2 Years of DLP.
122.00 | 4th year after 2 Years of DLP.
123.00 | 5th year after2 Years of DLP.
| Total in Figures |  |  |  |  | 58056702.00 |  | 42643040.00 |  | 57062531.00 |  | 85081465.00 |  | 54407524.00 |  | 104514450.87
Lowest Amount Quoted BY: SATIN NEO DIMENSIONS PVT LTD(42643040.00)

## BOQ Summary
BOQ Summary Details Tender Title: Modernization of Chennai Airport, (Phase-II), SH Design, Manufacture, Supply, Installation, Testing and Commissioning of Signages Works Tender ID: 2020_AAI_39373_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SATIN NEO DIMENSIONS PVT LTD | 42643040.00 | L1
| 2 | Sapphire Media Services | 54407524.00 | L2
| 3 | Vertex Lightco Industries | 57062531.00 | L3
| 4 | Sri Balaji Associates | 58056702.00 | L4
| 5 | DESIGN DIALOGUES INDIA PRIVATE LIMITED | 85081465.00 | L5
| 6 | Diamond Display Solutions Pvt Ltd | 104514450.87 | L6