## BoQ1
Government eProcurement System Created By: Samir Naskar Created Date/Time: 04-Feb-2020 10:30 AM Tender Title: Construction of New ATC Tower and Technical Block at LBSI Airport Varanasi. SH Provisioning of 33KV power supply cabling from New Power House NPH distribution panels etc. Tender ID: 2020_AAI_39580_1
Tender Inviting Authority: Sr. Manager (Engg.-E), LBSI Airport Varanasi.
Name of Work: Name of work: Construction of New ATC Tower and Technical Block at LBSI Airport Varanasi. (SH: Provisioning of 33KV power supply cabling from New Power House (NPH), distribution panels etc.)
Contract No: 2020_AAI_39580_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED |  | SARASWAT ENGINEERING SERVICES |  | SAURABH ENTERPRISES |  | M/s J.K. Electric Engineering Works |  | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION |  | Choubay And Co.(Agencies) Pvt.Ltd. |  | Naagar Infrastructure Pvt Ltd |  | TECHNO CRAFTS AND SOLUTIONS
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 33 KV grade (33 KV Earthed System) XLPE insulated , PVC sheathed, Aluminium Conductor,Armoured Power cable of size 3X300 sq mm, Conforming to IS: 7098 (Part - II) amended upto date. | 2400.00 | Meter |  | 1600.00 | 3840000.00 | 1570.00 | 3768000.00 | 2000.00 | 4800000.00 | 1600.00 | 3840000.00 | 1750.00 | 4200000.00 | 1620.00 | 3888000.00 | 1630.00 | 3912000.00 | 1407.09 | 3377020.08 | 3377020.08 | TECHNO CRAFTS AND SOLUTIONS
2.00 | Supply of 4 core ,16 sq.mm of XPLE insulated PVC shealthed ,aluminium conductor armoured power cable of 1.1 KV grade conforming to IS 1554 (Part I),1988 ammended upto date | 50.00 | Meter |  | 100.00 | 5000.00 | 100.00 | 5000.00 | 140.00 | 7000.00 | 94.00 | 4700.00 | 220.00 | 11000.00 | 99.00 | 4950.00 | 100.00 | 5000.00 | 90.58 | 4528.93 | 4528.93 | TECHNO CRAFTS AND SOLUTIONS
3.00 | Supply of 4 core ,25 sq.mm of XPLE insulated PVC shealthed ,aluminium conductor armoured power cable of 1.1 KV grade conforming to IS 1554 (Part I),1988 ammended upto date | 270.00 | Meter |  | 140.00 | 37800.00 | 130.00 | 35100.00 | 140.00 | 37800.00 | 125.00 | 33750.00 | 230.00 | 62100.00 | 142.00 | 38340.00 | 130.00 | 35100.00 | 117.37 | 31689.90 | 31689.90 | TECHNO CRAFTS AND SOLUTIONS
4.00 | Supply of 3.5 core ,120 sq.mm of XPLE insulated PVC shealthed ,aluminium conductor armoured power cable of 1.1 KV grade conforming to IS 1554 (Part I),1988 ammended upto date | 550.00 | Meter |  | 400.00 | 220000.00 | 370.00 | 203500.00 | 430.00 | 236500.00 | 361.00 | 198550.00 | 650.00 | 357500.00 | 390.00 | 214500.00 | 380.00 | 209000.00 | 331.08 | 182094.22 | 182094.22 | TECHNO CRAFTS AND SOLUTIONS
5.00 | Supply of 3.5 core ,185 sq.mm of XPLE insulated PVC shealthed ,aluminium conductor armoured power cable of 1.1 KV grade conforming to IS 1554 (Part I),1988 ammended upto date | 250.00 | Meter |  | 588.00 | 147000.00 | 540.00 | 135000.00 | 650.00 | 162500.00 | 534.00 | 133500.00 | 950.00 | 237500.00 | 576.00 | 144000.00 | 560.00 | 140000.00 | 507.36 | 126839.63 | 126839.63 | TECHNO CRAFTS AND SOLUTIONS
6.00 | Supply of 3.5 core ,240 sq.mm of XPLE insulated PVC shealthed ,aluminium conductor armoured power cable of 1.1 KV grade conforming to IS 1554 (Part I),1988 ammended upto date | 800.00 | Meter |  | 740.00 | 592000.00 | 680.00 | 544000.00 | 650.00 | 520000.00 | 672.00 | 537600.00 | 1150.00 | 920000.00 | 711.00 | 568800.00 | 710.00 | 568000.00 | 615.38 | 492302.16 | 492302.16 | TECHNO CRAFTS AND SOLUTIONS
7.00 | Supply of 3.5 core ,300 sq.mm of XPLE insulated PVC shealthed ,aluminium conductor armoured power cable of 1.1 KV grade conforming to IS 1554 (Part I),1988 ammended upto date | 280.00 | Meter |  | 900.00 | 252000.00 | 840.00 | 235200.00 | 800.00 | 224000.00 | 823.00 | 230440.00 | 1500.00 | 420000.00 | 870.00 | 243600.00 | 880.00 | 246400.00 | 782.64 | 219140.46 | 219140.46 | TECHNO CRAFTS AND SOLUTIONS
8.00 | Supply of 3.5 core ,400 sq.mm of XPLE insulated PVC shealthed ,aluminium conductor armoured power cable of 1.1 KV grade conforming to IS 1554 (Part I),1988 ammended upto date | 850.00 | Meter |  | 1120.00 | 952000.00 | 1070.00 | 909500.00 | 1170.00 | 994500.00 | 1048.00 | 890800.00 | 1850.00 | 1572500.00 | 1110.00 | 943500.00 | 1100.00 | 935000.00 | 996.58 | 847091.30 | 847091.30 | TECHNO CRAFTS AND SOLUTIONS
9.00 | Supplying of PE80, 110 mm outer dia HDPE pipe ISI marked to lay in underground as per IS:4984/95 with latest ammendmants upto date duly ISI marked . Should withstand minimum pressure of 6 Kgf/cm2. | 1900.00 | Meter |  | 310.00 | 589000.00 | 280.00 | 532000.00 | 330.00 | 627000.00 | 290.00 | 551000.00 | 300.00 | 570000.00 | 320.00 | 608000.00 | 300.00 | 570000.00 | 145.50 | 276450.00 | 276450.00 | TECHNO CRAFTS AND SOLUTIONS
10.00 | Supply of 160 mm outer dia PE80 HDPE Pipe suitable to lay in underground as per IS:4984/95 with latest ammendmants upto date duly ISI marked . Should withstand minimum pressure of 6 Kgf/cm2. | 3200.00 | Meter |  | 600.00 | 1920000.00 | 580.00 | 1856000.00 | 600.00 | 1920000.00 | 315.00 | 1008000.00 | 400.00 | 1280000.00 | 640.00 | 2048000.00 | 600.00 | 1920000.00 | 291.00 | 931200.00 | 931200.00 | TECHNO CRAFTS AND SOLUTIONS
11.00 | Laying of HDPE Pipe (upto 160 mm OD) direct in under ground at depth of 120 cm below ground level including soil excavation and refilling the trench etc. as required. | 2650.00 | Meter |  | 100.00 | 265000.00 | 207.00 | 548550.00 | 100.00 | 265000.00 | 130.00 | 344500.00 | 250.00 | 662500.00 | 100.00 | 265000.00 | 150.00 | 397500.00 | 242.50 | 642625.00 | 265000.00 | SAURABH ENTERPRISES, Choubay And Co.(Agencies) Pvt.Ltd., JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
12.00 | Laying of HDPE Pipe (upto outer dia of 160 mm) in underground for laying of cable across taxi or runway/road at depth of upto 3 mtr through HDD Method (HDPE Pipe is to be provided by AAI). | 2450.00 | Meter |  | 600.00 | 1470000.00 | 932.00 | 2283400.00 | 750.00 | 1837500.00 | 600.00 | 1470000.00 | 280.00 | 686000.00 | 540.00 | 1323000.00 | 450.00 | 1102500.00 | 582.00 | 1425900.00 | 686000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
13.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Upto 35 sq. mm in the existing RCC/ HUME/ METAL pipe as required. | 250.00 | Meter |  | 20.00 | 5000.00 | 35.00 | 8750.00 | 10.00 | 2500.00 | 20.00 | 5000.00 | 90.00 | 22500.00 | 15.00 | 3750.00 | 50.00 | 12500.00 | 97.00 | 24250.00 | 2500.00 | SAURABH ENTERPRISES
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 95 sq. mm and upto 185 sq. mm in the existing RCC/ HUME/ METAL pipe as required. | 700.00 | Meter |  | 30.00 | 21000.00 | 63.00 | 44100.00 | 25.00 | 17500.00 | 35.00 | 24500.00 | 50.00 | 35000.00 | 20.00 | 14000.00 | 100.00 | 70000.00 | 116.40 | 81480.00 | 14000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
15.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 185 sq. mm and upto 400 sq. mm in the existing RCC/ HUME/ METAL pipe as required. | 1750.00 | Meter |  | 60.00 | 105000.00 | 81.00 | 141750.00 | 40.00 | 70000.00 | 40.00 | 70000.00 | 80.00 | 140000.00 | 30.00 | 52500.00 | 110.00 | 192500.00 | 145.50 | 254625.00 | 52500.00 | Choubay And Co.(Agencies) Pvt.Ltd.
16.00 | Laying of one number armoured XLPE insulated and PVC sheathed power cable of 33 KV grade of size above 120 sq. mm and upto 400 sq. mm in the existing HDPE /RCC / HUME / METAL pipe as required. | 2350.00 | Meter |  | 80.00 | 188000.00 | 86.00 | 202100.00 | 40.00 | 94000.00 | 80.00 | 188000.00 | 85.00 | 199750.00 | 40.00 | 94000.00 | 120.00 | 282000.00 | 194.00 | 455900.00 | 94000.00 | SAURABH ENTERPRISES, Choubay And Co.(Agencies) Pvt.Ltd.
17.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Upto 35 sq. mm in the existing masonry open duct as required. | 50.00 | Meter |  | 10.00 | 500.00 | 35.00 | 1750.00 | 20.00 | 1000.00 | 20.00 | 1000.00 | 60.00 | 3000.00 | 10.00 | 500.00 | 50.00 | 2500.00 | 77.60 | 3880.00 | 500.00 | Choubay And Co.(Agencies) Pvt.Ltd., JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
18.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 95 sq. mm and upto 185 sq. mm in the existing masonry open duct as required. | 75.00 | Meter |  | 20.00 | 1500.00 | 63.00 | 4725.00 | 30.00 | 2250.00 | 30.00 | 2250.00 | 100.00 | 7500.00 | 15.00 | 1125.00 | 100.00 | 7500.00 | 97.00 | 7275.00 | 1125.00 | Choubay And Co.(Agencies) Pvt.Ltd.
19.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 185 sq. mm and upto 400 sq. mm in the existing masonry open duct as required. | 150.00 | Meter |  | 50.00 | 7500.00 | 81.00 | 12150.00 | 50.00 | 7500.00 | 40.00 | 6000.00 | 80.00 | 12000.00 | 20.00 | 3000.00 | 150.00 | 22500.00 | 116.40 | 17460.00 | 3000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
20.00 | Laying of one number armoured XLPE insulated and PVC sheathed power cable of 33 KV grade of size above 120 sq. mm and upto 400 sq. mm in the existing masonary open duct as required . | 50.00 | Meter |  | 50.00 | 2500.00 | 81.00 | 4050.00 | 60.00 | 3000.00 | 80.00 | 4000.00 | 70.00 | 3500.00 | 25.00 | 1250.00 | 150.00 | 7500.00 | 291.00 | 14550.00 | 1250.00 | Choubay And Co.(Agencies) Pvt.Ltd.
21.00 | Laying and fixing of one number armoured XLPE insulated and PVC sheathed power cable of 33 KV grade of size above 120 sq and upto 400 sq mm on the existing cable tray/surface including providing suitable size clamps (clamped with 40x3mm MS flat clamp) to secure the cable on cable tray /surface as required. | 50.00 | Meter |  | 100.00 | 5000.00 | 115.00 | 5750.00 | 130.00 | 6500.00 | 130.00 | 6500.00 | 50.00 | 2500.00 | 75.00 | 3750.00 | 150.00 | 7500.00 | 485.00 | 24250.00 | 2500.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
22.00 | Supply and making end termination with brass compression gland and aluminium lugs for 4 X 16 sq. mm (28mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 4.00 | Each |  | 300.00 | 1200.00 | 205.00 | 820.00 | 300.00 | 1200.00 | 150.00 | 600.00 | 300.00 | 1200.00 | 400.00 | 1600.00 | 1500.00 | 6000.00 | 271.60 | 1086.40 | 600.00 | M/s J.K. Electric Engineering Works
23.00 | Supply and making end termination with brass compression gland and aluminium lugs for 4 X 25 sq. mm (28mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 6.00 | Each |  | 400.00 | 2400.00 | 284.00 | 1704.00 | 400.00 | 2400.00 | 210.00 | 1260.00 | 500.00 | 3000.00 | 400.00 | 2400.00 | 1500.00 | 9000.00 | 300.70 | 1804.20 | 1260.00 | M/s J.K. Electric Engineering Works
24.00 | Supply and making end termination with brass compression gland and aluminium lugs for 3.5 X 120 sq. mm (45mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 6.00 | Each |  | 500.00 | 3000.00 | 638.00 | 3828.00 | 550.00 | 3300.00 | 430.00 | 2580.00 | 800.00 | 4800.00 | 800.00 | 4800.00 | 4500.00 | 27000.00 | 436.50 | 2619.00 | 2580.00 | M/s J.K. Electric Engineering Works
25.00 | Supply and making end termination with brass compression gland and aluminium lugs for 3.5 X 185 sq. mm (57 mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 4.00 | Each |  | 600.00 | 2400.00 | 1058.00 | 4232.00 | 600.00 | 2400.00 | 590.00 | 2360.00 | 500.00 | 2000.00 | 800.00 | 3200.00 | 4800.00 | 19200.00 | 533.50 | 2134.00 | 2000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
26.00 | Supply and making end termination with brass compression gland and aluminium lugs for 3.5 X 240 sq. mm (62mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 14.00 | Each |  | 700.00 | 9800.00 | 1305.00 | 18270.00 | 650.00 | 9100.00 | 760.00 | 10640.00 | 1000.00 | 14000.00 | 1000.00 | 14000.00 | 5000.00 | 70000.00 | 679.00 | 9506.00 | 9100.00 | SAURABH ENTERPRISES
27.00 | Supply and making end termination with brass compression gland and aluminium lugs for 3.5 X 300 sq. mm (70 mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 4.00 | Each |  | 800.00 | 3200.00 | 1453.00 | 5812.00 | 700.00 | 2800.00 | 860.00 | 3440.00 | 1000.00 | 4000.00 | 1200.00 | 4800.00 | 6000.00 | 24000.00 | 1067.00 | 4268.00 | 2800.00 | SAURABH ENTERPRISES
28.00 | Supply and making end termination with brass compression gland and aluminium lugs for 3.5 X 400 sq. mm (82 mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 4.00 | Each |  | 1000.00 | 4000.00 | 1918.00 | 7672.00 | 1100.00 | 4400.00 | 1110.00 | 4440.00 | 1000.00 | 4000.00 | 1200.00 | 4800.00 | 6500.00 | 26000.00 | 1455.00 | 5820.00 | 4000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION, JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
29.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 3 core,300 sqmm XLPE aluminium conductor cable of 33 KV grade as required | 2.00 | Each |  | 12000.00 | 24000.00 | 18800.00 | 37600.00 | 23000.00 | 46000.00 | 23000.00 | 46000.00 | 5200.00 | 10400.00 | 9000.00 | 18000.00 | 25000.00 | 50000.00 | 11640.00 | 23280.00 | 10400.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
30.00 | Earthing with G.l. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry 'enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. This Item does not include GI strip required from earth plate./earth electrode and up to body terminal. | 14.00 | Each |  | 5000.00 | 70000.00 | 11800.00 | 165200.00 | 5000.00 | 70000.00 | 5395.00 | 75530.00 | 7500.00 | 105000.00 | 7000.00 | 98000.00 | 8000.00 | 112000.00 | 8730.00 | 122220.00 | 70000.00 | SAURABH ENTERPRISES, JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
31.00 | Providing· and fixing 25 mm X 5 mm· G.l. strip in 40 mm dia G.l. pipe from earth electrode including connection with G.l. nut, bolt, spring, washer excavation and refilling etc. as required. | 140.00 | Meter |  | 350.00 | 49000.00 | 564.00 | 78960.00 | 350.00 | 49000.00 | 393.00 | 55020.00 | 350.00 | 49000.00 | 400.00 | 56000.00 | 300.00 | 42000.00 | 2948.80 | 412832.00 | 42000.00 | Naagar Infrastructure Pvt Ltd
32.00 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required | 140.00 | Meter |  | 120.00 | 16800.00 | 160.00 | 22400.00 | 130.00 | 18200.00 | 151.00 | 21140.00 | 250.00 | 35000.00 | 150.00 | 21000.00 | 250.00 | 35000.00 | 261.90 | 36666.00 | 16800.00 | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
33.00 | Constructing full brick masonry manhole in cement mortar 1 : 4 ( 1 cement : 4 coarse sand ) R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) 10 mm dia reinforcement, foundation concrete 1:4:8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size) inside plastering 12mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement complete as per standard design including providing 02 no suitable lifting hook in the top RCC slab : Inside size 90x90 cm and 1200 cm deep. With common burnt clay F.P.S. (non modular) bricks of class designation 7.5. | 20.00 | Each |  | 7000.00 | 140000.00 | 12655.00 | 253100.00 | 12000.00 | 240000.00 | 12000.00 | 240000.00 | 20000.00 | 400000.00 | 4000.00 | 80000.00 | 18000.00 | 360000.00 | 0.00 | 0.00 | 0.00 | TECHNO CRAFTS AND SOLUTIONS
34.00 | SITC of indoor type UPS Input LT panel (PTTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMER'S CHANGEOVER: 100 Amp ,FP, Automatic Transfer Switch -01 Nos. INCOMERS: 100 Amp 25KA,FP, MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -01 Nos. OUTGOINGS: 63 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -3 Nos. Digital Ammeter with Selector Switch for all Outgoings. 01 Sets 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-01 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Copper bus bar but not less than 160 Amps. | 1.00 | Each |  | 125000.00 | 125000.00 | 166575.00 | 166575.00 | 100000.00 | 100000.00 | 200000.00 | 200000.00 | 143000.00 | 143000.00 | 99000.00 | 99000.00 | 140000.00 | 140000.00 | 143560.00 | 143560.00 | 99000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
35.00 | SITC of indoor type UPS Output LT panel (PTTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMERS:63 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -2 Nos. OUTGOINGS: 40 A,4P, 10 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -5 Nos. 25 A,DP, 10 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -2 Nos. 16 A,DP, 10 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. Digital Ammeter with Selector Switch for all Outgoings. 01 Sets 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-02 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Copper bus bar but not less than 100 Amps. | 1.00 | Each |  | 75000.00 | 75000.00 | 104685.00 | 104685.00 | 72000.00 | 72000.00 | 180000.00 | 180000.00 | 89000.00 | 89000.00 | 70000.00 | 70000.00 | 90000.00 | 90000.00 | 97000.00 | 97000.00 | 70000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
36.00 | SITC of indoor type Main LT panel (TTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMERS:315 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -2 Nos. OUTGOINGS: 160 A,4P, 25 kA,MCCB with therm al magnetic release O/L , S/C (Ics=Icu=100 %) -6 Nos. 100 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -4 Nos. 63 A,4P, 25 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -5 Nos. 63 A,4P, 10 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -5 Nos. 40 A,4P, 10 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -2 Nos. 25 A,DP, 300 mA,RCCB -1 Nos. BUSCOUPLER:315A,4P MCCB with thermal magnetic releaseO/L ,S/C (Ics=Icu=100%)-1 No. Digital Ammeter with Selector Switch for all Outgoings. 01 Sets 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-02 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings-01set BUS BARS: Suitable size TPN Aluminium bus bar but not less than 400 Amps. | 1.00 | Each |  | 500000.00 | 500000.00 | 617710.00 | 617710.00 | 203000.00 | 203000.00 | 640000.00 | 640000.00 | 532000.00 | 532000.00 | 390000.00 | 390000.00 | 700000.00 | 700000.00 | 527680.00 | 527680.00 | 203000.00 | SAURABH ENTERPRISES
37.00 | SITC of indoor type Light & Power LT panel (PTTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMER'S CHANGEOVER: 160 Amp ,FP, Automatic Transfer Switch -01 Nos INCOMERS:160 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. OUTGOINGS: 63 A,4P, 10 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -6 Nos. 40 A,4P, 10 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -3 Nos. 25 A,DP, 300 mA,RCCB -1 Nos. Digital Ammeter with Selector Switch for all Outgoings. 01 Sets 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-01 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Aluminium bus bar but not less than 200 Amps. | 2.00 | Each |  | 175000.00 | 350000.00 | 185475.00 | 370950.00 | 102000.00 | 204000.00 | 280000.00 | 560000.00 | 163000.00 | 326000.00 | 125000.00 | 250000.00 | 200000.00 | 400000.00 | 162960.00 | 325920.00 | 204000.00 | SAURABH ENTERPRISES
38.00 | SITC of outdoor type Air Conditioning LT panel (TTA)-1, made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 54 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMER'S CHANGEOVER: 400 Amp ,FP, Automatic Transfer Switch -01 Nos INCOMERS:400 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. OUTGOINGS:125 A,4P, 10 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -2 Nos. 100 A,4P, 25 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -5 Nos. 63 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. Digital Ammeter with Selector Switch for all Outgoings. 01 Sets 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-01 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Aluminium bus bar but not less than 500 Amps. | 1.00 | Each |  | 325000.00 | 325000.00 | 326095.00 | 326095.00 | 104000.00 | 104000.00 | 380000.00 | 380000.00 | 289000.00 | 289000.00 | 295000.00 | 295000.00 | 380000.00 | 380000.00 | 489850.00 | 489850.00 | 104000.00 | SAURABH ENTERPRISES
39.00 | SITC of outdoor type Air Conditioning LT panel (TTA)-2, made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 54 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMER'S CHANGEOVER: 400 Amp ,FP, Automatic Transfer Switch -01 Nos INCOMERS:400 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. OUTGOINGS:125 A,4P, 25 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -3Nos. 100 A,4P, 25 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -3 Nos. 63 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -3 Nos. Digital Ammeter with Selector Switch for all Outgoings. 01 Sets 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-01 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Aluminium bus bar but not less than 500 Amps. | 1.00 | Each |  | 325000.00 | 325000.00 | 362965.00 | 362965.00 | 105000.00 | 105000.00 | 415000.00 | 415000.00 | 323000.00 | 323000.00 | 320000.00 | 320000.00 | 400000.00 | 400000.00 | 499550.00 | 499550.00 | 105000.00 | SAURABH ENTERPRISES
40.00 | SITC of indoor type Lift LT panel (PTTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMER'S CHANGEOVER: 100 Amp ,FP, Automatic Transfer Switch -01 Nos INCOMERS:100 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. OUTGOINGS: 32 A,4P, 10 kA,MCB +300 mA ELCB -2 Nos. 16 A,SP, 10 kA,Curve C -6 Nos. Digital Ammeter with Selector Switch for all Outgoings. 01 Sets 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-01 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Copper bus bar but not less than 125 Amps. | 1.00 | Each |  | 75000.00 | 75000.00 | 95665.00 | 95665.00 | 60000.00 | 60000.00 | 230000.00 | 230000.00 | 80000.00 | 80000.00 | 95000.00 | 95000.00 | 100000.00 | 100000.00 | 116400.00 | 116400.00 | 60000.00 | SAURABH ENTERPRISES
41.00 | SITC of indoor type Plumbing panel (TTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMER'S CHANGEOVER: 63 Amp ,FP, Automatic Transfer Switch -01 Nos INCOMERS:63 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. OUTGOINGS:3.7 KW DOL starter Comprises of 32 A,TP, 25 kA,MCCB with Sequence Controller as per SLD of technical specification-2 Nos. 1.5 KW DOL starter Comprises of 25 A,TP, 25 kA,MCCBwith Sequence Controller as per SLD of technical specification-2 Nos. Space Provision for 3.75 KW DOL starter with Fitted 32 A,TP, 25 kA,MCCB-1 No. Space Provision for 1.55 KW DOL starter with Fitted 25 A,TP, 25 kA,MCCB-1 No. Digital Ammeter with Selector Switch for all Outgoings. 01 Sets 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-01 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Copper bus bar but not less than 100 Amps. | 1.00 | Each |  | 200000.00 | 200000.00 | 212545.00 | 212545.00 | 110000.00 | 110000.00 | 315000.00 | 315000.00 | 186000.00 | 186000.00 | 180000.00 | 180000.00 | 250000.00 | 250000.00 | 257050.00 | 257050.00 | 110000.00 | SAURABH ENTERPRISES
42.00 | SITC of indoor type STP panel (PTTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications.Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMERS: 63 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. OUTGOINGS:3.7 KW DOL starter Comprises of 32 A,TP, 25 kA,MCCB with Sequence Controller as per SLD of technical specification-2 Nos. 1.5 KW DOL starter Comprises of 25 A,TP, 25 kA,MCCBwith Sequence Controller as per SLD of technical specification-1 Nos. Space Provision for 3.75 KW DOL starter with Fitted 32 A,TP, 25 kA,MCCB-1 No. Space Provision for 1.55 KW DOL starter with Fitted 25 A,TP, 25 kA,MCCB-1 No. Digital Ammeter with Selector Switch for all Outgoings. 01 Sets 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-01 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Copper bus bar but not less than 100 Amps. | 1.00 | Each |  | 125000.00 | 125000.00 | 152765.00 | 152765.00 | 102000.00 | 102000.00 | 185000.00 | 185000.00 | 133000.00 | 133000.00 | 175000.00 | 175000.00 | 175000.00 | 175000.00 | 160050.00 | 160050.00 | 102000.00 | SAURABH ENTERPRISES
43.00 | SITC of indoor type Fire Fighting panel (TTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMER'S CHANGEOVER: 315 Amp ,FP, Automatic Transfer Switch -01 Nos INCOMERS: 315A,4P, 35 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. OUTGOINGS: 70 KW Star Delta starter comprises of 160 A,TP, 25 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. 7.5 KW DOL starter comprises of 40 A,TP, 10 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. 40 A,TP, 25 kA,MCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -2 Nos. Digital Ammeter with Selector Switch for all Outgoings. 01 Sets 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-01 No Metering: RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Copper bus bar but not less than 400 Amps. | 1.00 | Each |  | 325000.00 | 325000.00 | 370235.00 | 370235.00 | 109000.00 | 109000.00 | 430000.00 | 430000.00 | 329000.00 | 329000.00 | 310000.00 | 310000.00 | 400000.00 | 400000.00 | 354050.00 | 354050.00 | 109000.00 | SAURABH ENTERPRISES
44.00 | SITC of indoor,wall mounted type VTPN DB (PTTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications.Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works i/c providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMERS: 63A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. OUTGOINGS: 40A,FP, 10 kA, MCB Curve C -3 Nos. 40A,DP, 10 kA, MCB Curve C -1 No. 25A,DP, RCCB ,300mA -2 No. BUS BARS: Suitable size TPN Copper bus bar but not less than 100 Amps. | 1.00 | Each |  | 30000.00 | 30000.00 | 35210.00 | 35210.00 | 32000.00 | 32000.00 | 39000.00 | 39000.00 | 30000.00 | 30000.00 | 40000.00 | 40000.00 | 50000.00 | 50000.00 | 24250.00 | 24250.00 | 24250.00 | TECHNO CRAFTS AND SOLUTIONS
45.00 | SITC of outdoor type MS enclosed switchgear box made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 54 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with following switchgears: 1. 100 Amp 4 Pole , 25KA , MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos 2.100 A ,4 P ,300 mA,RCCB/Elcb-1 No 3..1 Lot of control wiring , 1 Set of designation plates &RYB indicating Lamp (Works include necessary minor civil works e.g. providing C-C channel etc. as per site requirement ). | 7.00 | Each |  | 15000.00 | 105000.00 | 28950.00 | 202650.00 | 60000.00 | 420000.00 | 28000.00 | 196000.00 | 26000.00 | 182000.00 | 30000.00 | 210000.00 | 16000.00 | 112000.00 | 23280.00 | 162960.00 | 105000.00 | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
46.00 | SITC of outdoor type MS enclosed switchgear box made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 54 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with following switchgears: 1. 125 Amp 4 Pole , 25KA , MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos 2.125 A ,4 P ,300 mA,RCCB/Elcb-1 Nos 3.1 Lot of control wiring , 1 Set of designation plates &RYB indicating Lamp (Works include necessary minor civil works e.g. providing C-C channel etc. as per site requirement ). | 4.00 | Each |  | 15000.00 | 60000.00 | 31230.00 | 124920.00 | 50000.00 | 200000.00 | 45000.00 | 180000.00 | 28000.00 | 112000.00 | 35000.00 | 140000.00 | 20000.00 | 80000.00 | 45105.00 | 180420.00 | 60000.00 | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
47.00 | 33 KV H.T. BREAKER SWITCH BOARD PANEL Supply, installation, testing and commissioning of 33 KV, 1500 MVA (Min short circuit current rating 25 kA, 630A, HT Panel Vacuum circuit breaker Switchboard (Single panel board ), cubicle type, made out of 2mm thick sheet steel, totally enclosed, IP 4X, free standing floor mounting, dust and vermin proof, indoor, compartmentalised, power coated painting suitable for operation on 33 KV, 3ph, 50Hz system with Aluminium/copper bus bars, Vacuum circuit breaker mounted on horizontally withdrawable truck including supply and installation of the following components (Ref. Technical specifications, Technical particular) OUTGOING : Vacuum circuit breaker -630 A, 3 pole, 25 kA-1 No. BUSBAR: Vaccum circuit breaker will be connected on existing , 33KV, TP HT Panel (SF6/VCB) Copper bus bar with necesaary modification as per site requirement. All metering and protection devices, interconnections, necessary control wiring and all other accessories shall be provided as per Technical specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C | 1.00 | Each |  | 800000.00 | 800000.00 | 862500.00 | 862500.00 | 38594.00 | 38594.00 | 1075300.00 | 1075300.00 | 638000.00 | 638000.00 | 900000.00 | 900000.00 | 900000.00 | 900000.00 | 1455000.00 | 1455000.00 | 38594.00 | SAURABH ENTERPRISES
| Total in Figures |  |  |  |  | 14371600.00 |  | 16085443.00 |  | 14144444.00 |  | 15038400.00 |  | 15429250.00 |  | 14246165.00 |  | 15602200.00 |  | 14856527.28
Lowest Amount Quoted BY: SAURABH ENTERPRISES(14144444.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New ATC Tower and Technical Block at LBSI Airport Varanasi. SH Provisioning of 33KV power supply cabling from New Power House NPH distribution panels etc. Tender ID: 2020_AAI_39580_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SAURABH ENTERPRISES | 14144444.00 | L1
| 2 | Choubay And Co.(Agencies) Pvt.Ltd. | 14246165.00 | L2
| 3 | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED | 14371600.00 | L3
| 4 | TECHNO CRAFTS AND SOLUTIONS | 14856527.28 | L4
| 5 | M/s J.K. Electric Engineering Works | 15038400.00 | L5
| 6 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION | 15429250.00 | L6
| 7 | Naagar Infrastructure Pvt Ltd | 15602200.00 | L7
| 8 | SARASWAT ENGINEERING SERVICES | 16085443.00 | L8