## BoQ1
Government eProcurement System Created By: Ravindra Kumar Created Date/Time: 27-Feb-2020 04:16 PM Tender Title: Providing higher capacity DG Set for Operational requirement at CATC, Allahabad Tender ID: 2020_AAI_39593_1
Tender Inviting Authority:- Sr. Manager (Engg-E), Airports Authority of India, Engineering Section, CATC Allahabad
Name of Work:- Providing higher capacity DG Set for Operational requirement at CATC, Allahabad
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | KRISHNA REFRIGERATION |  | S.M.Brothers |  | VIJAYPOWER GENERATORS LIMITED |  | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION |  | Choubay And Co.(Agencies) Pvt.Ltd. |  | Mona Generator Services Pvt. Ltd. |  | National Engineering |  | JAKSON AND COMPANY |  | LUMOS INFRA PVT LTD |  | Gainwell Commosales Private Limited
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | S.I.T.C. of 1 No. minimum 600 kVA , 415V, 3 phase,1500 R.P.M, 0.8 PF water/ coolant cooled, floor mounted Diesel Generator set with electronic governor and brush less alternator self excited and self regulated and acoustic enclosure & all accessories including supply & installation of Engine control panel with meters , CTs & transducers for all metering and protection, Antivibration mountings, residential type silencer, turbo charged after cooled, electric starter, batteries & battery charger, radiator, control wiring, first fill of lubricating oil, & Diesel for testing & commissioning at site & all spares & accessories, including sufficiently rated cooling system so as to obtain the full capacity of genarator as required complete with necessary civil work such as grouting, chipping, finishing etc.as required complete but without foundation. The work should be as per Central Electrical Inspectorate/ Pollution control boards standards. | 3.00 | Job | 10.00 | 3676470.00 | 11029410.00 | 3945108.00 | 11835324.00 | 3714000.00 | 11142000.00 | 3500000.00 | 10500000.00 | 3650000.00 | 10950000.00 | 3282659.36 | 9847978.08 | 3450000.00 | 10350000.00 | 3780000.00 | 11340000.00 | 3890700.00 | 11672100.00 | 3950000.00 | 11850000.00 | 9847978.08 | Mona Generator Services Pvt. Ltd.
2.00 | Supply and Installation of M.S. ERW "C" Class 25 mm dia pipe with 25 mm dia ball valve including painting of pipe with desired shade of synthetic enamel paint | 60.00 | Mtr | 10.00 | 846.00 | 50760.00 | 600.00 | 36000.00 | 500.00 | 30000.00 | 500.00 | 30000.00 | 370.00 | 22200.00 | 291.66 | 17499.60 | 280.00 | 16800.00 | 400.00 | 24000.00 | 207.00 | 12420.00 | 312.00 | 18720.00 | 12420.00 | LUMOS INFRA PVT LTD
3.00 | Supply and installation of 990 Ltr day service Fuel Tank capacity with level indicator, level switches, | 3.00 | Job | 10.00 | 22941.00 | 68823.00 | 32000.00 | 96000.00 | 9998.00 | 29994.00 | 25000.00 | 75000.00 | 20000.00 | 60000.00 | 20000.00 | 60000.00 | 16000.00 | 48000.00 | 25000.00 | 75000.00 | 20700.00 | 62100.00 | 51750.00 | 155250.00 | 29994.00 | VIJAYPOWER GENERATORS LIMITED
4.00 | Design, supply, erection, testing and commissioning of exhaust piping of 250mm dia size MS B Class exhaust pipes, SS belwo, bends, silencer insulation with welding joint including bends, clamps, dash fastener, flanges, nuts, bolts, insulation of exhaust pipe using 50 mm thick loosely bound resin mattress/mineral wool/rock wool density not less than 120 kg/mtr cube, wire chicken mesh over insulation and cladding aluminium sheet of 0.6 mm thick etc. complete as required and as per specifications. | 60.00 | Mtr | 10.00 | 3658.00 | 219480.00 | 3320.00 | 199200.00 | 2278.00 | 136680.00 | 3000.00 | 180000.00 | 3500.00 | 210000.00 | 4244.26 | 254655.60 | 3800.00 | 228000.00 | 6000.00 | 360000.00 | 4230.00 | 253800.00 | 15192.00 | 911520.00 | 136680.00 | VIJAYPOWER GENERATORS LIMITED
5.00 | Design, supply & fixing of self supporting MS structure suitable for pipes for exhaust of DG sets complete etc as required | 6000.00 | Kg | 10.00 | 106.00 | 636000.00 | 100.00 | 600000.00 | 74.00 | 444000.00 | 200.00 | 1200000.00 | 70.00 | 420000.00 | 65.00 | 390000.00 | 90.00 | 540000.00 | 90.00 | 540000.00 | 81.00 | 486000.00 | 98.00 | 588000.00 | 390000.00 | Mona Generator Services Pvt. Ltd.
6.00 | Dismantling of existing 380 KVA diesel generator and accessories by disconnecting electrical, controls , fuel connections, exhaust system and earthing connections of DG set and transporting the upto AAI store (not more than 50 mtrs) by engaging skilled and un skilled manpower with required T & P and machinery (hydra, jcb) etc complete as required. | 3.00 | Job | 10.00 | 18000.00 | 54000.00 | 12000.00 | 36000.00 | 5000.00 | 15000.00 | 50000.00 | 150000.00 | 7500.00 | 22500.00 | 30000.00 | 90000.00 | 15000.00 | 45000.00 | 15000.00 | 45000.00 | 18900.00 | 56700.00 | 63250.00 | 189750.00 | 15000.00 | VIJAYPOWER GENERATORS LIMITED
7.00 | Supply of following sizes of XLPE insulated PVC sheathed, armoured power cable of 1.1 KV grade conforming to IS-7098, amended upto date.
8.00 | 3.5Cx 300 Sq. mm Aluminium conductor | 743.00 | Meter | 10.00 | 968.00 | 719224.00 | 660.00 | 490380.00 | 864.00 | 641952.00 | 1500.00 | 1114500.00 | 877.00 | 651611.00 | 825.00 | 612975.00 | 1000.00 | 743000.00 | 1300.00 | 965900.00 | 1215.00 | 902745.00 | 1046.00 | 777178.00 | 490380.00 | S.M.Brothers
9.00 | 8 core 1.5 sqmm Copper control cable | 196.00 | Meter | 10.00 | 134.00 | 26264.00 | 100.00 | 19600.00 | 61.00 | 11956.00 | 250.00 | 49000.00 | 125.00 | 24500.00 | 250.00 | 49000.00 | 225.00 | 44100.00 | 250.00 | 49000.00 | 189.00 | 37044.00 | 148.00 | 29008.00 | 11956.00 | VIJAYPOWER GENERATORS LIMITED
10.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of XLPE insulated PVC sheathed/XLPE aluminium conductor cable of 1.1 kV grade as required.
11.00 | 3.5Cx 300 Sq. mm | 18.00 | Set | 10.00 | 882.00 | 15876.00 | 1352.00 | 24336.00 | 750.00 | 13500.00 | 5600.00 | 100800.00 | 1000.00 | 18000.00 | 1400.00 | 25200.00 | 800.00 | 14400.00 | 1500.00 | 27000.00 | 990.00 | 17820.00 | 4945.00 | 89010.00 | 13500.00 | VIJAYPOWER GENERATORS LIMITED
12.00 | 8 core 1.5 sqmm Copper control cable | 6.00 | Set | 10.00 | 235.00 | 1410.00 | 360.00 | 2160.00 | 50.00 | 300.00 | 150.00 | 900.00 | 300.00 | 1800.00 | 100.00 | 600.00 | 250.00 | 1500.00 | 300.00 | 1800.00 | 90.00 | 540.00 | 690.00 | 4140.00 | 300.00 | VIJAYPOWER GENERATORS LIMITED
13.00 | Laying of one number PVC insulated PVC sheathed/XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc. as required.
14.00 | upto 35 Sq. mm | 21.00 | Meter | 10.00 | 70.00 | 1470.00 | 160.00 | 3360.00 | 250.00 | 5250.00 | 200.00 | 4200.00 | 170.00 | 3570.00 | 540.00 | 11340.00 | 150.00 | 3150.00 | 800.00 | 16800.00 | 63.00 | 1323.00 | 115.00 | 2415.00 | 1323.00 | LUMOS INFRA PVT LTD
15.00 | Above 185 Sq. mm upto 400 Sq. mm | 15.00 | Meter | 10.00 | 100.00 | 1500.00 | 360.00 | 5400.00 | 250.00 | 3750.00 | 250.00 | 3750.00 | 190.00 | 2850.00 | 1013.33 | 15199.95 | 180.00 | 2700.00 | 1500.00 | 22500.00 | 99.00 | 1485.00 | 172.00 | 2580.00 | 1485.00 | LUMOS INFRA PVT LTD
16.00 | Laying of one number additional PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of size exceeding 120 Sq. mm, but not exceeding 400 Sq. mm direct in ground in the same trench in one tier horizontal formation including excavation, sand, cushioning, protective covering and refilling the trench etc. as required.
17.00 | Above 185 Sq. mm upto 400 Sq. mm | 24.00 | Meter | 10.00 | 258.00 | 6192.00 | 432.00 | 10368.00 | 200.00 | 4800.00 | 250.00 | 6000.00 | 140.00 | 3360.00 | 276.00 | 6624.00 | 225.00 | 5400.00 | 800.00 | 19200.00 | 99.00 | 2376.00 | 92.00 | 2208.00 | 2208.00 | Gainwell Commosales Private Limited
18.00 | Laying of one number PVC insulated PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ STONEWARE/ METAL PIPE as required.
19.00 | upto 35 Sq. mm | 15.00 | Meter | 10.00 | 70.00 | 1050.00 | 40.00 | 600.00 | 30.00 | 450.00 | 50.00 | 750.00 | 15.00 | 225.00 | 100.00 | 1500.00 | 30.00 | 450.00 | 300.00 | 4500.00 | 63.00 | 945.00 | 69.00 | 1035.00 | 225.00 | Choubay And Co.(Agencies) Pvt.Ltd.
20.00 | Above 185 Sq. mm upto 400 Sq. mm | 45.00 | Meter | 10.00 | 100.00 | 4500.00 | 120.00 | 5400.00 | 70.00 | 3150.00 | 100.00 | 4500.00 | 20.00 | 900.00 | 170.00 | 7650.00 | 50.00 | 2250.00 | 800.00 | 36000.00 | 99.00 | 4455.00 | 115.00 | 5175.00 | 900.00 | Choubay And Co.(Agencies) Pvt.Ltd.
21.00 | Laying of one number PVC insulated PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
22.00 | upto 35 Sq. mm | 15.00 | Meter | 10.00 | 70.00 | 1050.00 | 40.00 | 600.00 | 30.00 | 450.00 | 50.00 | 750.00 | 10.00 | 150.00 | 70.00 | 1050.00 | 30.00 | 450.00 | 400.00 | 6000.00 | 63.00 | 945.00 | 69.00 | 1035.00 | 150.00 | Choubay And Co.(Agencies) Pvt.Ltd.
23.00 | Above 185 Sq. mm upto 400 Sq. mm | 54.00 | Meter | 10.00 | 100.00 | 5400.00 | 120.00 | 6480.00 | 50.00 | 2700.00 | 250.00 | 13500.00 | 20.00 | 1080.00 | 110.00 | 5940.00 | 60.00 | 3240.00 | 900.00 | 48600.00 | 99.00 | 5346.00 | 115.00 | 6210.00 | 1080.00 | Choubay And Co.(Agencies) Pvt.Ltd.
24.00 | Providing and fixing following sizes of class `B' GI pipe with ISI mark in surface/ wall etc. as required.
25.00 | 100 mm (internal dia.) | 27.00 | Meter | 10.00 | 927.00 | 25029.00 | 1200.00 | 32400.00 | 798.00 | 21546.00 | 350.00 | 9450.00 | 900.00 | 24300.00 | 1304.00 | 35208.00 | 800.00 | 21600.00 | 700.00 | 18900.00 | 810.00 | 21870.00 | 1191.00 | 32157.00 | 9450.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
26.00 | Earthing with Copper earth plate 600mm X 600mm X 3 mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 mtr long etc with charcoal or coke and salt complete as required | 6.00 | Set | 10.00 | 9411.00 | 56466.00 | 14400.00 | 86400.00 | 8000.00 | 48000.00 | 10000.00 | 60000.00 | 12500.00 | 75000.00 | 8000.00 | 48000.00 | 12000.00 | 72000.00 | 18000.00 | 108000.00 | 15300.00 | 91800.00 | 20334.00 | 122004.00 | 48000.00 | Mona Generator Services Pvt. Ltd., VIJAYPOWER GENERATORS LIMITED
27.00 | Providing and fixing 50 mm X 5 mm Copper strip on surface or in recess for connections etc. as required | 60.00 | Meter | 10.00 | 1650.00 | 99000.00 | 1426.00 | 85560.00 | 1494.00 | 89640.00 | 850.00 | 51000.00 | 1500.00 | 90000.00 | 1500.00 | 90000.00 | 625.00 | 37500.00 | 800.00 | 48000.00 | 810.00 | 48600.00 | 2185.00 | 131100.00 | 37500.00 | National Engineering
28.00 | Providing and fixing 50mm x 5mm copper strip at 0.50 m. below ground level for connections ,termination with nut bolt etc as required | 36.00 | Meter | 10.00 | 1638.00 | 58968.00 | 1432.00 | 51552.00 | 1793.00 | 64548.00 | 950.00 | 34200.00 | 1550.00 | 55800.00 | 1666.00 | 59976.00 | 725.00 | 26100.00 | 900.00 | 32400.00 | 900.00 | 32400.00 | 2242.00 | 80712.00 | 26100.00 | National Engineering
29.00 | Providing and fixing 50 mm X 5 mm copper. strip in 65 mm dia G.I. pipe from earth electrode including connection with nut, bolt, spring, washer excavation and re-filling etc. as required. | 36.00 | Meter | 10.00 | 1638.00 | 58968.00 | 1888.00 | 67968.00 | 1886.00 | 67896.00 | 950.00 | 34200.00 | 1900.00 | 68400.00 | 2297.00 | 82692.00 | 950.00 | 34200.00 | 1200.00 | 43200.00 | 1350.00 | 48600.00 | 2875.00 | 103500.00 | 34200.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION, National Engineering
30.00 | Earthing with GI earth plate 600mm X 600mm X 6 mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 mtr long etc with charcoal or coke and salt complete as required | 6.00 | Set | 10.00 | 6500.00 | 39000.00 | 7520.00 | 45120.00 | 4000.00 | 24000.00 | 8500.00 | 51000.00 | 6900.00 | 41400.00 | 5000.00 | 30000.00 | 4000.00 | 24000.00 | 10000.00 | 60000.00 | 4500.00 | 27000.00 | 10350.00 | 62100.00 | 24000.00 | VIJAYPOWER GENERATORS LIMITED, National Engineering
31.00 | Supplying and laying 25 mm X 5 mm G.l strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. | 60.00 | Meter | 10.00 | 120.00 | 7200.00 | 100.00 | 6000.00 | 338.00 | 20280.00 | 550.00 | 33000.00 | 140.00 | 8400.00 | 135.33 | 8119.80 | 150.00 | 9000.00 | 400.00 | 24000.00 | 270.00 | 16200.00 | 230.00 | 13800.00 | 6000.00 | S.M.Brothers
32.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 60.00 | Meter | 10.00 | 120.00 | 7200.00 | 108.00 | 6480.00 | 264.00 | 15840.00 | 600.00 | 36000.00 | 140.00 | 8400.00 | 118.66 | 7119.60 | 85.00 | 5100.00 | 250.00 | 15000.00 | 270.00 | 16200.00 | 195.00 | 11700.00 | 5100.00 | National Engineering
33.00 | Providing and fixing 25 mm x 5 mm G. I. strip in 40 mm dia. G. I. pipe from earth electrode as required. | 30.00 | Meter | 10.00 | 120.00 | 3600.00 | 380.00 | 11400.00 | 390.00 | 11700.00 | 650.00 | 19500.00 | 425.00 | 12750.00 | 433.00 | 12990.00 | 385.00 | 11550.00 | 400.00 | 12000.00 | 450.00 | 13500.00 | 713.00 | 21390.00 | 3600.00 | KRISHNA REFRIGERATION
34.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand :4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required. | 5.00 | Cum | 10.00 | 6500.00 | 32500.00 | 12800.00 | 64000.00 | 6000.00 | 30000.00 | 650.00 | 3250.00 | 9500.00 | 47500.00 | 7500.00 | 37500.00 | 5500.00 | 27500.00 | 15000.00 | 75000.00 | 4500.00 | 22500.00 | 11500.00 | 57500.00 | 3250.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
35.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
36.00 | 450 mm width X 62.5 mm depth X 2.0 mm thickness | 107.00 | Mtr | 10.00 | 997.00 | 106679.00 | 780.00 | 83460.00 | 600.00 | 64200.00 | 750.00 | 80250.00 | 800.00 | 85600.00 | 644.48 | 68959.36 | 1500.00 | 160500.00 | 700.00 | 74900.00 | 810.00 | 86670.00 | 920.00 | 98440.00 | 64200.00 | VIJAYPOWER GENERATORS LIMITED
| Total in Figures |  |  |  |  | 13337019.00 |  | 13911548.00 |  | 12943582.00 |  | 13845500.00 |  | 12910296.00 |  | 11877776.99 |  | 12477490.00 |  | 14092700.00 |  | 13943484.00 |  | 15367637.00
Lowest Amount Quoted BY: Mona Generator Services Pvt. Ltd.(11877776.99)

## BOQ Summary
BOQ Summary Details Tender Title: Providing higher capacity DG Set for Operational requirement at CATC, Allahabad Tender ID: 2020_AAI_39593_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Mona Generator Services Pvt. Ltd. | 11877776.99 | L1
| 2 | National Engineering | 12477490.00 | L2
| 3 | Choubay And Co.(Agencies) Pvt.Ltd. | 12910296.00 | L3
| 4 | VIJAYPOWER GENERATORS LIMITED | 12943582.00 | L4
| 5 | KRISHNA REFRIGERATION | 13337019.00 | L5
| 6 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION | 13845500.00 | L6
| 7 | S.M.Brothers | 13911548.00 | L7
| 8 | LUMOS INFRA PVT LTD | 13943484.00 | L8
| 9 | JAKSON AND COMPANY | 14092700.00 | L9
| 10 | Gainwell Commosales Private Limited | 15367637.00 | L10