## BoQ1
Government eProcurement System Created By: Tapan Kumar Bala Created Date/Time: 19-Feb-2020 03:20 PM Tender Title: Relocation of LLZ and Glide path at LGBI airport Guwahati. SH- Electrical works Tender ID: 2020_AAI_40268_1
Tender Inviting Authority: Asst. General Manager (Engg – Elect), AAI, LGBI Airport, Guwahati, Assam – 781015
Name of Work: Relocation of LLZ & Glide path at LGBI airport Guwahati. SH: Electrical works.
Contract No: AAI/AGM(E-E)/NIT-25/2019-20
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals |  | M/s M S Construction
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. Group B | 22.00 | Point |  | 1100.00 | 24200.00 | 650.00 | 14300.00 | 14300.00 | M/s M S Construction
2.00 | Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 115.00 | Mtr. |  | 210.00 | 24150.00 | 210.00 | 24150.00 | 24150.00 | M/s M S Construction, Manish Electricals
3.00 | Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 2 Nos. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 115.00 | Mtr. |  | 320.00 | 36800.00 | 280.00 | 32200.00 | 32200.00 | M/s M S Construction
4.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
4.01 | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 25.00 | Mtr. |  | 140.00 | 3500.00 | 120.00 | 3000.00 | 3000.00 | M/s M S Construction
4.02 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 15.00 | Mtr. |  | 220.00 | 3300.00 | 175.00 | 2625.00 | 2625.00 | M/s M S Construction
4.03 | 2 X 6 sq. mm + 1 X 6 sq. mm earth wire | 20.00 | Mtr. |  | 240.00 | 4800.00 | 350.00 | 7000.00 | 4800.00 | Manish Electricals
4.04 | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 30.00 | Mtr. |  | 400.00 | 12000.00 | 530.00 | 15900.00 | 12000.00 | Manish Electricals
5.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. 25 mm | 50.00 | Mtr. |  | 32.00 | 1600.00 | 120.00 | 6000.00 | 1600.00 | Manish Electricals
6.00 | Supplying and drawing 2 pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. | 25.00 | Mtr. |  | 75.00 | 1875.00 | 50.00 | 1250.00 | 1250.00 | M/s M S Construction
7.00 | Supplying and fixing suitable size GI box with modular plate and cover infront on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 14.00 | Each |  | 300.00 | 4200.00 | 650.00 | 9100.00 | 4200.00 | Manish Electricals
8.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
8.01 | 1 or 2 Module (75mmX75mm) | 2.00 | Each |  | 50.00 | 100.00 | 220.00 | 440.00 | 100.00 | Manish Electricals
8.02 | 8 Module (225mmX75mm) | 4.00 | Each |  | 135.00 | 540.00 | 425.00 | 1700.00 | 540.00 | Manish Electricals
9.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
9.01 | 5/6 A switch | 16.00 | Each |  | 40.00 | 640.00 | 140.00 | 2240.00 | 640.00 | Manish Electricals
9.02 | 3 pin 5/6 A socket outlet | 16.00 | Each |  | 105.00 | 1680.00 | 180.00 | 2880.00 | 1680.00 | Manish Electricals
9.03 | Telephone socket outlet | 2.00 | Each |  | 110.00 | 220.00 | 160.00 | 320.00 | 220.00 | Manish Electricals
9.04 | Electronic type fan regulator | 1.00 | Each |  | 170.00 | 170.00 | 365.00 | 365.00 | 170.00 | Manish Electricals
10.00 | Supplying and fixing 3 pin, 5 A ceiling rose on the existing junction box/ wooden block including connections etc. as required. | 4.00 | Each |  | 30.00 | 120.00 | 50.00 | 200.00 | 120.00 | Manish Electricals
11.00 | Supplying and fixing of following ways surface/ recess mounting, Horizontal 415 V, SPN/TPN MCB distribution board of sheet steel, dust protected, duly powder painted, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required.
11.01 | 2+6 way SPN (pre-wired), Double door | 2.00 | Each |  | 5200.00 | 10400.00 | 5500.00 | 11000.00 | 10400.00 | Manish Electricals
11.02 | 6 way TPN (8 + 18) (pre-wired), Double door | 2.00 | Each |  | 6500.00 | 13000.00 | 12500.00 | 25000.00 | 13000.00 | Manish Electricals
12.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
12.01 | Single pole | 50.00 | Each |  | 210.00 | 10500.00 | 225.00 | 11250.00 | 10500.00 | Manish Electricals
12.02 | Single pole and neutral | 2.00 | Each |  | 450.00 | 900.00 | 550.00 | 1100.00 | 900.00 | Manish Electricals
13.00 | Supplying and fixing following rating, 240/415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 A Four pole | 2.00 | Each |  | 1500.00 | 3000.00 | 2500.00 | 5000.00 | 3000.00 | Manish Electricals
14.00 | Supplying and fixing 20 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 10 A, “C” curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 10.00 | Each |  | 1200.00 | 12000.00 | 1600.00 | 16000.00 | 12000.00 | Manish Electricals
15.00 | Supplying and fixing 2 way MCB metallic enclosure along with 32 A SPN MCB C series 10 KA including connections, testing and commissioning etc. as required. | 8.00 | Each |  | 600.00 | 4800.00 | 750.00 | 6000.00 | 4800.00 | Manish Electricals
16.00 | Supply & fixing of UPVC trunking of size 100 x 50 mm along with accessories such as coupler, Elbow, Tee, internal and external bend etc. in surface complete as required. | 20.00 | Mtr. |  | 480.00 | 9600.00 | 750.00 | 15000.00 | 9600.00 | Manish Electricals
17.00 | Supply of Surface mounted LED Batten fitting in extruded aluminium housing with diffuser and LED tube of lumen output >3420 lumes 4' long with integral electronic driver suitable for operations at 230+/-10% Volts, 50 Hz., PF>=.95 complete as required. | 10.00 | Each |  | 900.00 | 9000.00 | 3500.00 | 35000.00 | 9000.00 | Manish Electricals
18.00 | Supply of outdoor type LED street light fixture of 25 W ±10% (nominal) of lumens output not less than 2375 lumens , minimum lifetime of 50000 burning hours and having aesthetically designed pressure die cast extruded aluminium/aluminium alloy housing, heat sink with general spread optics having IP-66 including accessories such as LED of approved make, electronic gear/driver with surge voltage, open/short circuit protections and power factor correction facility suitable for operation on 140 V to 280 V AC and frequency 50Hz +/-5% etc. complete as per approved makes & enclosed technical specifications. | 10.00 | Each |  | 1800.00 | 18000.00 | 1750.00 | 17500.00 | 17500.00 | M/s M S Construction
19.00 | Supply of ceiling fans of approved makes of 1200mm sweep 5 star rating capacitor type complete with 60cms down rod canopies, hanging shackles, blades and speed regulator (electronic type) suitable for use on 220/240 volts 50hz single phase AC supply confirming to ISS: 374/1979 with upto date amendments (Class - I) and provide with functional insulation including wiring the down rod with 1.5 sqmm PVC insulated copper conductor single core cable etc as required. | 1.00 | Each |  | 2500.00 | 2500.00 | 2500.00 | 2500.00 | 2500.00 | M/s M S Construction, Manish Electricals
20.00 | Supply of 300mm sweep, 900 rpm heavy duty exhaust fan suitable for 230/240 volts, 50hz, single phase A.C supply with all accessories including louvers, shutters etc as required. | 1.00 | Each |  | 2400.00 | 2400.00 | 2800.00 | 2800.00 | 2400.00 | Manish Electricals
21.00 | Installation, testing and commissioning of LED street light fixtures including Supplying and Fixing of 32mm dia x 1.0 mtrs long GI pipe(Medium class) bracket for mounting LED street light fitting on wall including bending the pipe in required shape, wiring with 3C x 1.5 sq. mm copper conductor cable, 2nos. 40mm x 3mm flat iron clamps with nuts and bolts and washer, painting the flat with primer and finish paint etc as required. | 10.00 | Each |  | 600.00 | 6000.00 | 550.00 | 5500.00 | 5500.00 | M/s M S Construction
22.00 | Installation, testing and commissioning of pre-wired, LED fittings of all types, complete with all accessories and tube/lamp etc. directly on ceiling/ wall, including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 11.00 | Each |  | 250.00 | 2750.00 | 50.00 | 550.00 | 550.00 | M/s M S Construction
23.00 | Installation, testing and commissioning of ceiling fan of 1200 mm/1400 mm sizes, 5 star rating complete with down rod, canopies, hanging shackles, blades, capacitor including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required. | 1.00 | Each |  | 200.00 | 200.00 | 100.00 | 100.00 | 100.00 | M/s M S Construction
24.00 | Installation of exhaust fan upto 450mm by making suitable opening in the existing wall, including making the hole to suit the size of above fan, making good the damage, fixing luvers and shutters, connection, testing, commissioning etc as required. | 1.00 | Each |  | 450.00 | 450.00 | 350.00 | 350.00 | 350.00 | M/s M S Construction
25.00 | Supply installation testing and commissioning of 1.5 TR (4500 K.Cal/hr) split type air conditioners 5 star rated with inverter type compressor, operating on refrigrant R-410 non CFC with copper tube condensor and evaporator units, cordless remote hi- wall mounting suitbale for operation on 230V 50 hz, Single pahse, A.C supply complete with filter, standard length drain & refrigerant pipe with insulation & electrical connection with wire, metallic brackets for the indoor unit & wall mounted/ floor mounted stand for outdoor units complete as required. | 6.00 | Each |  | 54000.00 | 324000.00 | 45000.00 | 270000.00 | 270000.00 | M/s M S Construction
26.00 | Supply and fixing of AC Time switch in Polycarbonate enclosure with transparent front cover consisting of Astronomical time switch- 1 No., 25 A 2 Pole contactor- 1 No. , 25 A Modular changeover switch - 1 No., din rail mountable connector (32 A) for connections, interconnection complete as required. | 6.00 | Each |  | 4000.00 | 24000.00 | 6000.00 | 36000.00 | 24000.00 | Manish Electricals
27.00 | Supply and fixing of extra copper refrigerent piping beyond standard length suitable dimension for the 1.5Tr machines complete with suction / liquid line, insulation, electrical cabling, drain pipe, all the accessories as per site requirement. | 12.00 | Mtr. |  | 750.00 | 9000.00 | 600.00 | 7200.00 | 7200.00 | M/s M S Construction
28.00 | Supply installation testing and commissioning of 1 Loop microprocessor based intelligent Analogue Addressable Fire Alarm Control & Indicating Panel having the capacity to handle minimum of 99 detectors & 99 module/ devices, consisting of (i)Network card capable to connect with repeater panel (ii) 24V SMF battery having 24 Hrs backup with charger circuit (iv) 160 character LCD display module etc. as per site requirement. | 1.00 | Each |  | 45000.00 | 45000.00 | 160000.00 | 160000.00 | 45000.00 | Manish Electricals
29.00 | Supply installation testing and commissioning of Analogue Addressable Photo Electric Smoke Detector [of same protocol of FDA Panel] with mounting base as per site requirement. | 6.00 | Each |  | 4000.00 | 24000.00 | 4200.00 | 25200.00 | 24000.00 | Manish Electricals
30.00 | Supply installation testing and commissioning of Analogue Addressable Manual Call Point [of same protocol of FDA Panel] as per site requirement. | 1.00 | Each |  | 4000.00 | 4000.00 | 3000.00 | 3000.00 | 3000.00 | M/s M S Construction
31.00 | Supply installation testing and commissioning of Analogue Addressable Loop powered Sounder cum strobe [of same protocol of FDA Panel] as per site requirement. | 1.00 | Each |  | 4200.00 | 4200.00 | 4300.00 | 4300.00 | 4200.00 | Manish Electricals
32.00 | Supply & fixing of auto dialer i/c programming numbers etc. complete as required. | 1.00 | Each |  | 48000.00 | 48000.00 | 8500.00 | 8500.00 | 8500.00 | M/s M S Construction
33.00 | Supply and drawing of 2C x 1.5 sq mm shielded tinned PVC insulated copper cable in existing conduit as per site requirement. | 50.00 | Mtr. |  | 150.00 | 7500.00 | 90.00 | 4500.00 | 4500.00 | M/s M S Construction
34.00 | Supply and fixing of Carbon Di-oxide Fire Extinguishers of 4.5 Kg. each mounted on wall hooks as per IS 15683:2006 | 2.00 | Each |  | 7000.00 | 14000.00 | 5800.00 | 11600.00 | 11600.00 | M/s M S Construction
35.00 | Supply and fixing of Dry Chemical Fire Extinguishers of 5 Kg. as per IS: 15683:2006 mounted on wall hooks. | 2.00 | Each |  | 4000.00 | 8000.00 | 3000.00 | 6000.00 | 6000.00 | M/s M S Construction
36.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 6.00 | Set |  | 9000.00 | 54000.00 | 5500.00 | 33000.00 | 33000.00 | M/s M S Construction
37.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Mtr. |  | 540.00 | 16200.00 | 380.00 | 11400.00 | 11400.00 | M/s M S Construction
38.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 30.00 | Mtr. |  | 280.00 | 8400.00 | 140.00 | 4200.00 | 4200.00 | M/s M S Construction
39.00 | OUTDOOR FEEDER PILLAR (At Glide Path) Design, Supply, Installation, Testing and Commissioning of outdoor type double door feeder pillar, cubicle type, made out of 2mm thick CRCA sheet steel, totally enclosed, IP-55 protection free standing, dust and vermin proof, compartmentalized, powder coated painting suitable for operation on 3 phase and neutral, 415V, 50 Hz AC system with busbars, mechanical interlocking between the incomer MCCBs & BUS coupler MCCB, interconnections complete as required and as per specifications. (to be installed outside Glide Path Hut) Incomer and Bus coupler (a) 160A, 25KA (Ics=100%Icu) thermal magnetic release type 4 Pole MCCB with suitable size Spreader terminals in both end for cable termination, Extended rotary operating mechanism and having over load and short ckt. protections - 03 Nos. (2 incomers and 1 bus coupler) (b) Multifunction meter (VAF+PF) with RS485, Cl-0.5 - 02 Nos. (c) LED type indication lamps (R-Y-B) - 02 Sets. (d) Mechanical Interlocking (3 Locks & 2 keys system) - 01 set. Busbar (a) 200A, 4 strip TPN high conductivity aluminium bus bars - 01 set. Outgoings (a) 100A, 25KA (Ics=100%Icu) thermal magnetic release type 4 Pole MCCB with suitable size Spreader terminals in both end for cable termination, Direct rotary operating mechanism and having over load and short ckt. protections - 04 Nos. (b) 63A, 25KA (Ics=100%Icu) thermal magnetic release type 4 Pole MCCB with suitable size Spreader terminals in both end for cable termination, Direct rotary operating mechanism and having over load and short ckt. protections - 06 Nos. [Only PTTA Type of Feeder Pillar of approved make is acceptable] | 1.00 | JOB |  | 210000.00 | 210000.00 | 198000.00 | 198000.00 | 198000.00 | M/s M S Construction
40.00 | INDOOR PANEL (UPS INPUT) Design, Supply, Installation, Testing and Commissioning of LT Panel, front openable only, cubicle type, made out of 2mm thick CRCA sheet steel, totally enclosed, IP-42 protection, wall/floor mounted, dust and vermin proof, indoor, compartmentalized, powder coated painting suitable for operation on 3 phase and neutral, 415V, 50 Hz AC system with busbars , interconnections as of MV Panel complete as required and as per specifications. ( 1 each to be installed at Glide Path and Localizer ) Incomer (a) 100A, 25KA (Ics=100%Icu) thermal magnetic release type 4 Pole MCCB with suitable size Spreader terminals in both end for cable termination, Extended rotary operating mechanism and having over load and short ckt. protections - 02 Nos. (b) 125A, 4 Pole motorised automatic transfer switch open execution type along with controller with wire harness and suitable for operation on 440V, 50Hz, AC supply - 01 No. (c) Multifunction meter with RS485, Cl-0.5 - 02 Nos. (d) LED type indication lamps (R-Y-B) - 03 Sets. Busbar (a) 200A, 4 strip TPN high conductivity Copper bus bars - 01 set. Outgoings (a) 63A, 10KA, 4 pole C curve MCB - 04 Nos. (b) 32A, 10KA, 2 pole C curve MCB - 06 Nos. (c) Single Phase Class B SPD having 100 KA capacity, 10/350 micro sec pulse response with Voltage protection level <1.5 kV - 2 Nos. (As per specification enclosed) d) Space for 1 no. Data logger [Only PTTA Type of Panel approved make is Acceptable] | 2.00 | JOB |  | 185000.00 | 370000.00 | 199000.00 | 398000.00 | 370000.00 | Manish Electricals
41.00 | UPS OUTPUT PANEL Design, Supply, Installation, Testing and Commissioning of UPS Panel, front openable only, cubicle type, made out of 2mm thick CRCA sheet steel, totally enclosed, IP-42 protection, wall / floor mounted, dust and vermin proof, indoor, compartmentalized, powder coated painting suitable for operation on single phase and neutral, 230V, 50 Hz AC system with connectors, interconnections complete as required and as per specifications. ( 1 each to be installed at Glide Path and Localizer) (a) 40 A, 10 KA 2 Pole, 'C' Curve MCB as incomer - 1 No. (b) 32 A, 10 kA, 2 Pole 'C' curve MCB as outgoing - 4 Nos. (c) 40 A, 2 Pole dinrai mountable modular chargeover switch - 1 No. (d) 32 Amps, Singe Phase Class 'C' SPD with in built Series filter having multistage modular MOV and as per specifications enclosed. - 1 No. [Only PTTA Type of Panel of approved make is acceptable] | 2.00 | JOB |  | 95000.00 | 190000.00 | 155000.00 | 310000.00 | 190000.00 | Manish Electricals
42.00 | Supply and installation of Data logger for energy monitoring such as harmonics in power supply, power failure events/history, energy graph etc on existing power supply panels complete as required. (Siemens Model No. 7KM2111-1BA00 3AA00 or similar equivalent} | 2.00 | Each |  | 125000.00 | 250000.00 | 48000.00 | 96000.00 | 96000.00 | M/s M S Construction
43.00 | Transportation/ shifting of HT/LT/OFC Cable drum of various sizes from AAI store to operational area by engaging manpower with machinery such as Hydra/ JCB/ Crain/ Truck by taking proper care of cable from any damage during transportation including arranging airport entry passes for vehicles and staff, loading & unloading at site upto a distance of 4km as required. | 10.00 | Job |  | 12000.00 | 120000.00 | 2000.00 | 20000.00 | 20000.00 | M/s M S Construction
44.00 | Supply of 50mm dia (outer) permanantly lubricated HDPE (High Density Polyethylene) telecom duct conforming to BSNL TESEC specification with latest amendments | 5200.00 | Mtr. |  | 210.00 | 1092000.00 | 65.00 | 338000.00 | 338000.00 | M/s M S Construction
45.00 | Laying of 50 mm dia following size of permanetly lubricated HDPE (high density polyethylene) pipe alongwith its necessary accessories like coupler, end plugs, rope, cable sealent etc. below the ground (i/c Road crossing, runway crossings, Cement concrete, Apron Area) at a depth of up to 4 m through HDD method including duct integrity test for continuity as per site requirement and as per specification. | 4800.00 | Mtr. |  | 240.00 | 1152000.00 | 380.00 | 1824000.00 | 1152000.00 | Manish Electricals
46.00 | Laying of single run 12 core armoured OFC cable through pulling blowing in 50 mm dia size existing HDPE pipe complete as per specifications as required. | 5000.00 | Mtr. |  | 70.00 | 350000.00 | 15.00 | 75000.00 | 75000.00 | M/s M S Construction
47.00 | Laying and fixing of one 50 mm dia permenently lubricated HDPE pipe on cable tray/ surface as required. | 200.00 | Mtr. |  | 150.00 | 30000.00 | 20.00 | 4000.00 | 4000.00 | M/s M S Construction
48.00 | Supply, installation, testing and commissioning of Optical Fibre Cable Joint closure including splicing of Optic Fibre Cable ( 12 Fibres ) and testing of fibres conforming to technical specification, checking of continuity submission of report complete as required. etc as requried. | 3.00 | Each |  | 15000.00 | 45000.00 | 7000.00 | 21000.00 | 21000.00 | M/s M S Construction
49.00 | Supply, installation, testing and commissioning of 24 Port LIU ( Patch panel) for Optical Fibre cable Rack mountable/ Wall mountable(outdoor application) complete with splice tray, cable spool, Duplex Adaptor Module panel, Adaptor SC Duplex, SC Duplex Pigtail 1 meter. Job include splicing of core, fixing, testing etc complete as per satisfaction of Engg. -In-Charge. (Make: Schneider or eqv ) | 4.00 | Each |  | 23000.00 | 92000.00 | 14000.00 | 56000.00 | 56000.00 | M/s M S Construction
50.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. (For OFC and HT/LT power cable) | 69.00 | Each |  | 400.00 | 27600.00 | 850.00 | 58650.00 | 27600.00 | Manish Electricals
51.00 | Constructing brick masonry chamber of size 1000mm x 1000mm x 1000mm in cement mortar 1:4 (1 cement : 4 coarse sand) having base PCC foundation 1:4:8 (1 Cement : 4 Coarse Sand : 8 graded stone aggregate) with plastering of walls including excavation of existing surface etc complete as required. (Without Cover) | 13.00 | Each |  | 18000.00 | 234000.00 | 7000.00 | 91000.00 | 91000.00 | M/s M S Construction
52.00 | Constructing brick masonry chamber of size 500mm x 500mm x 500mm in cement mortar 1:4 (1 cement : 4 coarse sand) having base PCC foundation 1:4:8 (1 Cement : 4 Coarse Sand : 8 graded stone aggregate) with plastering of walls including excavation of existing hard/concrete surface etc complete as required. (Without Cover) | 4.00 | Each |  | 12000.00 | 48000.00 | 4000.00 | 16000.00 | 16000.00 | M/s M S Construction
53.00 | Steel work welded in built up section / framed work including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer and one coat of synthetic enamelblack paint using structural steel sections [65 mm x 65 mm x 6 mm MS Angle Iron (Frame for Manhole chamber ) | 348.00 | kg |  | 90.00 | 31320.00 | 90.00 | 31320.00 | 31320.00 | M/s M S Construction, Manish Electricals
54.00 | Steel work welded in built up section / framed work including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer and synthetic enamel black paint using structural steel etc. (10 mm thick MS Sheet). (Cover for Manhole chamber) | 1177.50 | kg |  | 90.00 | 105975.00 | 80.00 | 94200.00 | 94200.00 | M/s M S Construction
55.00 | Supply of 3C x 95 Sqmm. size 11 KV(UE) grade, PVC insulated and PVC sheathed Aluminium conductor armoured XLPE power cable generally confirming to IS 7098 Part II - 1988 with up to date amendments as required. | 3700.00 | Mtr. |  | 680.00 | 2516000.00 | 680.00 | 2516000.00 | 2516000.00 | M/s M S Construction, Manish Electricals
56.00 | Supply of following size LT power cable of 1.1 KV grade aluminium conductor XLPE insulated PVC sheathed armoured cable confirming to IS 7098 Part I-1988 with upto date amendment as required.
56.01 | 3.5C x 185 sq. mm. | 1500.00 | Mtr. |  | 690.00 | 1035000.00 | 610.00 | 915000.00 | 915000.00 | M/s M S Construction
56.02 | 3.5C x 50 sq. mm. | 500.00 | Mtr. |  | 300.00 | 150000.00 | 185.00 | 92500.00 | 92500.00 | M/s M S Construction
56.03 | 4 C x 35 Sqmm. | 100.00 | Mtr. |  | 225.00 | 22500.00 | 160.00 | 16000.00 | 16000.00 | M/s M S Construction
57.00 | Supply of 110mm dia (O.D.) HDPE (High Density Polyethylene) duct of grade PE80, PN6 ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984:1995 with latest ammendments complete as required. | 450.00 | Mtr. |  | 690.00 | 310500.00 | 650.00 | 292500.00 | 292500.00 | M/s M S Construction
58.00 | Laying of 110 mm dia (O.D) HDPE (High Density Polyethylene) duct direct in ground up to a depth of 50 cm under hard/concrere/bituminous surface including groove cutting, getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. Further, refilling the groove with cement concrete 1:3:6(1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) after laying the pipe complete with fitting, cutting and jointing etc. as required and finishing the top surcace matching to existing surfaces i/c curing etc. complete as required. | 115.00 | Mtr. |  | 510.00 | 58650.00 | 430.00 | 49450.00 | 49450.00 | M/s M S Construction
59.00 | Laying of 110mm dia HDPE (high density polyethylene) pipe alongwith all accessories like coupler, socket, bend etc. below the ground (i/c Road crossing, runway/ taxi crossings, Cement concrete Apron Area) at a depth of not less than 1.0 mtr through HDD method including duct integrity test for continuity as per site requirement and as per specifications complete as required. | 320.00 | Mtr. |  | 600.00 | 192000.00 | 800.00 | 256000.00 | 192000.00 | Manish Electricals
60.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 kV grade of size Upto 120 sq. mm direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc. as required. | 3000.00 | Mtr. |  | 320.00 | 960000.00 | 340.00 | 1020000.00 | 960000.00 | Manish Electricals
61.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 kV grade of size Upto 120 sq. mm in the existing RCC/HUME/ METAL pipe as required. | 350.00 | Mtr. |  | 40.00 | 14000.00 | 20.00 | 7000.00 | 7000.00 | M/s M S Construction
62.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 kV grade of size Upto 120 sq. mm in the existing masonary open duct as required. | 70.00 | Mtr. |  | 40.00 | 2800.00 | 15.00 | 1050.00 | 1050.00 | M/s M S Construction
63.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
63.01 | Upto 35 Sqmm. | 100.00 | Mtr. |  | 320.00 | 32000.00 | 280.00 | 28000.00 | 28000.00 | M/s M S Construction
63.02 | Above 35 sq. mm and upto 95 sq. mm | 220.00 | Mtr. |  | 320.00 | 70400.00 | 310.00 | 68200.00 | 68200.00 | M/s M S Construction
63.03 | Above 95 sq. mm and upto 185 sq. mm | 1040.00 | Mtr. |  | 340.00 | 353600.00 | 310.00 | 322400.00 | 322400.00 | M/s M S Construction
64.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
64.01 | Above 35 sq. mm and upto 95 sq. mm | 30.00 | Mtr. |  | 40.00 | 1200.00 | 15.00 | 450.00 | 450.00 | M/s M S Construction
64.02 | Above 95 sq. mm and upto 185 sq. mm | 150.00 | Mtr. |  | 40.00 | 6000.00 | 20.00 | 3000.00 | 3000.00 | M/s M S Construction
65.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
65.01 | Above 35 sq. mm and upto 95 sq. mm | 30.00 | Mtr. |  | 50.00 | 1500.00 | 15.00 | 450.00 | 450.00 | M/s M S Construction
65.02 | Above 95 sq. mm and upto 185 sq. mm | 70.00 | Mtr. |  | 50.00 | 3500.00 | 20.00 | 1400.00 | 1400.00 | M/s M S Construction
66.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 120.00 | Mtr. |  | 50.00 | 6000.00 | 80.00 | 9600.00 | 6000.00 | Manish Electricals
67.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 30.00 | Mtr. |  | 50.00 | 1500.00 | 90.00 | 2700.00 | 1500.00 | Manish Electricals
68.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray cable tray with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. 300 mm width X 50 mm depth X 1.6 mm thickness | 15.00 | Mtr. |  | 1200.00 | 18000.00 | 750.00 | 11250.00 | 11250.00 | M/s M S Construction
69.00 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for 3C X 95 sqmm. , XLPE aluminium conductor cable of 11 kV grade as required. | 6.00 | Each |  | 12000.00 | 72000.00 | 18000.00 | 108000.00 | 72000.00 | Manish Electricals
70.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 3C X 95 sqmm., XLPE aluminium conductor cable of 11 kV grade as required. | 5.00 | Each |  | 9000.00 | 45000.00 | 8000.00 | 40000.00 | 40000.00 | M/s M S Construction
71.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
71.01 | 4 C x 35 Sqmm. | 2.00 | Each |  | 1500.00 | 3000.00 | 1500.00 | 3000.00 | 3000.00 | M/s M S Construction, Manish Electricals
71.02 | 3.5 C x 50 Sqmm. | 2.00 | Each |  | 2000.00 | 4000.00 | 1900.00 | 3800.00 | 3800.00 | M/s M S Construction
71.03 | 3.5C x 185 sq. mm. | 3.00 | Each |  | 3000.00 | 9000.00 | 2300.00 | 6900.00 | 6900.00 | M/s M S Construction
72.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.
72.01 | 3.5 x 185 sq.mm. | 2.00 | Each |  | 1000.00 | 2000.00 | 650.00 | 1300.00 | 1300.00 | M/s M S Construction
72.02 | 3.5 x 70 sq.mm. | 2.00 | Each |  | 700.00 | 1400.00 | 350.00 | 700.00 | 700.00 | M/s M S Construction
72.03 | 3.5 x 50 sq.mm. | 10.00 | Each |  | 500.00 | 5000.00 | 290.00 | 2900.00 | 2900.00 | M/s M S Construction
72.04 | 4 x 35 sq.mm. | 2.00 | Each |  | 500.00 | 1000.00 | 220.00 | 440.00 | 440.00 | M/s M S Construction
72.05 | 4 x 10 sq.mm. | 2.00 | Each |  | 250.00 | 500.00 | 195.00 | 390.00 | 390.00 | M/s M S Construction
73.00 | Supply of C.I isolating transformer housing box, water tight round type, metal container of outside size 330 mm height 450 mm made of 10 mm thick cast iron moulding all round, except the top surface, which is 15 mm thick, cast irom moulding suitable to receive a light fitting base plate on the top and underground housing associated with transformer, power cable and having two clear holes on sides surfaces at 180 center 75 mm above bottom surface suitable to recieve of 50 mm dia( outer dia) HDPE/G.I pipe and including checks and nuts as required and another hole at 175 mm from the bottom of the CI box to receive one no.15 mm dia "B" class GI pipe and check and nut as required. The box should have two SS earth bolts of M10 X 30mm tapped inside near the hole away from the hole center and having a drain hole at the bottom suitable tapped to recieve 15 mm dia"B" class GI pipe and having clear opening of 220 mm at the top surface and 6 nos.M10 tapped hole at the hole center 260 mmm to receive fitting base plate and bolts and conforming to technical specifications, terms and conditions etc. as specified in tender document complete as required. | 12.00 | Each |  | 5200.00 | 62400.00 | 4000.00 | 48000.00 | 48000.00 | M/s M S Construction
74.00 | Supply of 200 watt,6.6A/6.6A, 5000V, 50 Hz individual lamp series type Isolating Trasnformer suitable for PAPI lamp encapsulated in polyester resin & finally molded in neoprene rubber with primary and secondary connection leads confirming to technical specifications, terms & conditions etc. as specified in tender document complete as required. | 12.00 | Each |  | 6000.00 | 72000.00 | 4000.00 | 48000.00 | 48000.00 | M/s M S Construction
75.00 | Supply of 3 lamps PAPI unit with breakable couplings,legs,connecting secondary leads, base plates, all required hardware i/c supply of lamps and confirming to technical specifications, terms & conditions etc. as specified in tender document complete as required. | 4.00 | set |  | 160000.00 | 640000.00 | 180000.00 | 720000.00 | 640000.00 | Manish Electricals
76.00 | Supply of 5 KV grade ESNA connector and suitable for fileld attachment with 5KV grade PVC insulated ,PVC Shethed single core 6 sq mm copper conductor cable confirming to technical specifications etc. as required. | 12.00 | Set |  | 400.00 | 4800.00 | 380.00 | 4560.00 | 4560.00 | M/s M S Construction
77.00 | Installation of transformer housing boxes with a base concrete of 1:3:6 of size 630 x 630 x 100 mm thick all round concrete of 1:2:4 150 mm thick the top sloped with 1:2:4 cement including providing and fixing 250 mm long 15 mm dia "B" Class GI pipe with check nut for drainage of water including excavation of hard/soft soil and refilling etc complete as required. | 12.00 | Each |  | 3000.00 | 36000.00 | 1750.00 | 21000.00 | 21000.00 | M/s M S Construction
78.00 | Installation of 04 Nos. 3 lamp PAPI unit (01 job) with base plates & positioning of checking sticks ( as mentioned in item no.74 & 75), supply of all required materials, providing civil foundations for pedestal, PCC pedestal up to 1m all around the complete PAPI installtion with 1:2:4 cement concrete of 100 mm thick , supply, crimping & moulding of secondary leads, connections/inter-connections with isolating transformers complete as per site rtequirements i/c testing , commissioning and confirming to technical specifications, terms & conditions etc complete as required. | 1.00 | JOB |  | 120000.00 | 120000.00 | 40000.00 | 40000.00 | 40000.00 | M/s M S Construction
79.00 | Making connections of 5 KV grade, 6 sq mm Copper conductor AFL cables with ESNA connector i/c crimping & fixing , applying HT tape complete as required. | 12.00 | set |  | 250.00 | 3000.00 | 250.00 | 3000.00 | 3000.00 | M/s M S Construction, Manish Electricals
80.00 | Laying of one number PVC insulated and PVC shethed/XLPE power cable of 5 KV grade of 6 sqmm size in the existing RCC/GI/HUME/METAL pipe etc as required. | 60.00 | Mtr. |  | 30.00 | 1800.00 | 10.00 | 600.00 | 600.00 | M/s M S Construction
81.00 | Dismantaling of existing PAPI units from its existing location without damaging the components and handing over the same to AAI Store. | 4.00 | Each |  | 10000.00 | 40000.00 | 500.00 | 2000.00 | 2000.00 | M/s M S Construction
82.00 | Supply and installation of 5 mm thick 330 mm dia size round type M.S. base plate on top of the transformer housing box having 6 Nos M10 holes at the hole center of 260 mm, 15 mm dia hole at the center of the base plate dully painted with anti corrosive paint and with 6 Nos of M10 SS bolts. | 12.00 | Each |  | 600.00 | 7200.00 | 800.00 | 9600.00 | 7200.00 | Manish Electricals
83.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 60.00 | Mtr. |  | 30.00 | 1800.00 | 30.00 | 1800.00 | 1800.00 | M/s M S Construction, Manish Electricals
84.00 | S/L of Earth connection from earth electrode with 6 SWG GI wire in 15 mm dia G.I pipe (Class-B ) etc. as required. | 40.00 | Mtr. |  | 210.00 | 8400.00 | 180.00 | 7200.00 | 7200.00 | M/s M S Construction
85.00 | Laying of 50 mm dia (OD) HDPE pipe alongwith all accessories direct in ground upto a depth of 75 cm including excavation of trench and back filling of excavated earth after laying of pipe complete as required. | 60.00 | Mtr. |  | 150.00 | 9000.00 | 150.00 | 9000.00 | 9000.00 | M/s M S Construction, Manish Electricals
| Total in Figures |  |  |  |  | 12068040.00 |  | 11189530.00
Lowest Amount Quoted BY: M/s M S Construction(11189530.00)

## BOQ Summary
BOQ Summary Details Tender Title: Relocation of LLZ and Glide path at LGBI airport Guwahati. SH- Electrical works Tender ID: 2020_AAI_40268_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s M S Construction | 11189530.00 | L1
| 2 | Manish Electricals | 12068040.00 | L2