## BoQ1
Government eProcurement System Created By: Bijendra Singh Meena Created Date/Time: 03-Mar-2020 04:20 PM Tender Title: Replacement of ILS System at Dibrugarh Airport. SH- Electrical works Tender ID: 2020_AAI_40613_1
Tender Inviting Authority: Sr. Manager (Engg. Elect.), AAI, Dibrugarh Airport.
Name of Work: Replacement of ILS System at Dibrugarh Airport. SH: Electrical works.
Contract No: AAI/DIB/ENGG(E)/ NIT-08/2019-20
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SHARMA TRADE AGENCY
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of following size XLPE insulated PVC Sheathed, armoured Aluminium conductor cable of 1.1KV grade confirming to IS:7098 with up to date amendments etc. as required.
1.10 | 2C x 10 sq.mm | 110.00 | mtr | 100.00 | 65.00 | 7150.00 | 7150.00 | SHARMA TRADE AGENCY
1.20 | 4C x 25 sq.mm | 380.00 | mtr | 100.00 | 132.00 | 50160.00 | 50160.00 | SHARMA TRADE AGENCY
1.30 | 3.5C x 70 sq.mm | 320.00 | mtr | 100.00 | 256.00 | 81920.00 | 81920.00 | SHARMA TRADE AGENCY
1.40 | 3.5C x 185 sq.mm | 3850.00 | mtr | 100.00 | 572.00 | 2202200.00 | 2202200.00 | SHARMA TRADE AGENCY
2.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS:14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
2.10 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 650.00 | mtr | 100.00 | 195.00 | 126750.00 | 126750.00 | SHARMA TRADE AGENCY
2.20 | 160 mm dia (OD-160 mm & ID-135 mm nominal) | 2685.00 | mtr | 100.00 | 440.00 | 1181400.00 | 1181400.00 | SHARMA TRADE AGENCY
3.00 | Laying of one number XLPE power cable of 1.1 kV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
3.10 | Upto 35 sq.mm | 50.00 | mtr | 100.00 | 300.00 | 15000.00 | 15000.00 | SHARMA TRADE AGENCY
3.20 | Above 35 sq.mm and upto 95 sq.mm | 10.00 | mtr | 100.00 | 350.00 | 3500.00 | 3500.00 | SHARMA TRADE AGENCY
3.30 | Above 95 sq.mm and upto 185 sq.mm | 270.00 | mtr | 100.00 | 350.00 | 94500.00 | 94500.00 | SHARMA TRADE AGENCY
4.00 | Laying of one number XLPE armoured power cable of 1.1 KV grade of following size in the existing masonry open duct as required:
4.10 | Upto 35 sq.mm | 20.00 | mtr | 100.00 | 20.00 | 400.00 | 400.00 | SHARMA TRADE AGENCY
4.20 | Above 35 sq.mm and upto 95 sq.mm | 6.00 | mtr | 100.00 | 30.00 | 180.00 | 180.00 | SHARMA TRADE AGENCY
4.30 | Above 95 sq.mm and upto 185 sq.mm | 15.00 | mtr | 100.00 | 40.00 | 600.00 | 600.00 | SHARMA TRADE AGENCY
5.00 | Laying of one number XLPE armoured power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/ DWC HDPE pipe as required.
5.10 | Upto 35 sq.mm | 510.00 | mtr | 100.00 | 25.00 | 12750.00 | 12750.00 | SHARMA TRADE AGENCY
5.20 | Above 35 sq.mm and upto 95 sq.mm | 240.00 | mtr | 100.00 | 35.00 | 8400.00 | 8400.00 | SHARMA TRADE AGENCY
5.30 | Above 95 sq.mm and upto 185 sq.mm | 3065.00 | mtr | 100.00 | 45.00 | 137925.00 | 137925.00 | SHARMA TRADE AGENCY
6.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
6.10 | Upto 35 sq.mm | 50.00 | mtr | 100.00 | 30.00 | 1500.00 | 1500.00 | SHARMA TRADE AGENCY
6.20 | Above 35 sq.mm and upto 95 sq.mm | 20.00 | mtr | 100.00 | 90.00 | 1800.00 | 1800.00 | SHARMA TRADE AGENCY
6.30 | Above 95 sq. mm and upto 185 sq. mm | 25.00 | mtr | 100.00 | 100.00 | 2500.00 | 2500.00 | SHARMA TRADE AGENCY
7.10 | Design, supply, installation, testing and commissioning of totally enclosed double door feeder pillar, made of 14 SWG CRCA sheet steel, totally enclosed, compartmentalized, standing on a MS Angle frame suitably fixed on floor foundation, dust and vermin proof, powder coated painting, suitable for operation on 3 phase and neutral, 415 V, 50 Hz AC system with busbars, connection and interconnections including supply & installation of following items and as per specifications- Incoming : 200 Amp., 4 Pole, MCCB (Ics=100%Icu, 35 kA), spreader links and extendable ON/OFF rotary handle - 02 Nos. CT's of ratio 200/5 Amps.-2 Set (1 Set of 3 Nos.) Digital Ammeter with selector switch - 2 set Digital Voltmeter with selector switch- 2 set Phase indication LED Lamps with MCBs- 6 Nos. Red ON indication LED Lamps with MCBs- 2 Nos. Green OFF indication LED Lamps with MCBs- 2 Nos. Bus coupler : 200 Amp., 4 Pole, MCCB having (Ics=100%Icu, 35 kA), spreader links and extendable ON/OFF rotary handle.- 01 No. Red ON indication LED Lamps with MCBs- 1 Nos. Green OFF indication LED Lamps with MCBs - 1 Nos. Bus-Bars : 4-Pole Aluminium bus bars of minimum of 400 Amps. Capacity with heat shrinkable coloured sleeves & i/c. DMC /SMC bus bars supports at required intervals complete for cross section, size supports and their spacing etc. Outgoings : 125 Amp., 4 Pole, MCCB having (Ics=100%Icu, 25 kA), spreader links and extendable ON/OFF rotary handle. - 03 Nos. 63 Amp., 4 Pole, MCCB having (Ics=100%Icu, 25 kA), spreader links and extendable ON/OFF rotary handle. - 01 Nos. others items & accessories-as required. | 2.00 | job | 100.00 | 175000.00 | 350000.00 | 350000.00 | SHARMA TRADE AGENCY
7.20 | Design, supply, installation, testing and commissioning of totally enclosed panel, made of 14 SWG CRCA sheet steel, totally enclosed, compartmentalized, standing on a MS Angle frame suitably fixed on floor, dust and vermin proof, powder coated painting, suitable for operation on 3 phase and neutral, 415 V, 50 Hz AC system with busbars, connection and interconnections including supply & installation of following items and as per specifications- Incoming : 125 Amp., 4 Pole, MCCB having (Ics=100%Icu, 25 kA), spreader links and extendable ON/OFF rotary handle. - 03 Nos.(NOTE: 2 nos. for ATS and 01 no for direct connection to B/B including mech. interlocking with ATS incomers) CT's of ratio 125/5 Amps.-2 Set (1 Set of 3 Nos.) Digital Ammeter with selector switch - 2 set Digital Voltmeter with selector switch- 2 set Phase indication LED Lamps with MCBs- 6 Nos. Red ON indication LED Lamps with MCBs- 3 Nos. Green OFF indication LED Lamps with MCBs- 3 Nos. 100A FP Automatic Transfer Switch(ATS)without enclosure - 1 no. Bus-Bars : 4-Pole Aluminium bus bars of minimum of 400 Amps. Capacity with heat shrinkable coloured sleeves & i/c. DMC /SMC bus bars supports at required intervals complete for cross section, size supports and their spacing etc. Outgoings : 100 Amp., 4 Pole, MCCB having (Ics=100%Icu, 25 kA), spreader links and extendable ON/OFF rotary handle. -04 Nos. Surge protection device: TPN Surge protection device (SPD) having 100KA 10/350 micro seconds neutral to earth, 50 KA 10/350 micro sec line to neutral- 1 no. others items & accessories-as required. | 2.00 | job | 100.00 | 290000.00 | 580000.00 | 580000.00 | SHARMA TRADE AGENCY
8.00 | Supplying and making end termination with brass compression gland and aluminium lugs size for following size of XLPE armoured aluminium conductor cable of 1.1 KV grade as required.
8.10 | 2C x 10 sq.mm | 4.00 | Set | 100.00 | 150.00 | 600.00 | 600.00 | SHARMA TRADE AGENCY
8.20 | 4C x 25 sq.mm | 12.00 | Set | 100.00 | 200.00 | 2400.00 | 2400.00 | SHARMA TRADE AGENCY
8.30 | 3.5 x 70 sq.mm | 12.00 | Set | 100.00 | 300.00 | 3600.00 | 3600.00 | SHARMA TRADE AGENCY
8.40 | 3.5 x 185 sq.mm | 12.00 | Set | 100.00 | 600.00 | 7200.00 | 7200.00 | SHARMA TRADE AGENCY
9.00 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.10 | 3.5 x 185 sq.mm | 4.00 | Set | 100.00 | 2000.00 | 8000.00 | 8000.00 | SHARMA TRADE AGENCY
10.00 | Providing, laying and fixing of following dia GI pipe (medium class) in ground complete with GI fittings including trenching (75 cm deep) and refilling etc. as required.
10.10 | 100 mm dia | 50.00 | mtr | 100.00 | 1100.00 | 55000.00 | 55000.00 | SHARMA TRADE AGENCY
11.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 3.00 | Cum | 100.00 | 1800.00 | 5400.00 | 5400.00 | SHARMA TRADE AGENCY
12.00 | Providing and laying in position cement concrete 1:3:6 (1 cement : 2 coarse sand : 6 graded stone aggregate 20 mm nominal size) etc as required. | 2.00 | Cum | 100.00 | 900.00 | 1800.00 | 1800.00 | SHARMA TRADE AGENCY
13.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 12.00 | Set | 100.00 | 5500.00 | 66000.00 | 66000.00 | SHARMA TRADE AGENCY
14.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement:2 coarse sand:4 graded stone aggregate 20 mm nominal size) of size 60 cm x 60 cm at the bottom and 50 cm x 50 cm at the top with a thickness of 10 cm including inscription duly engraved as required. | 15.00 | Each | 100.00 | 450.00 | 6750.00 | 6750.00 | SHARMA TRADE AGENCY
15.00 | Supplying and laying 25 mm X 5 mm G.I strip below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm). | 60.00 | mtr | 100.00 | 125.00 | 7500.00 | 7500.00 | SHARMA TRADE AGENCY
16.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 10.00 | mtr | 100.00 | 160.00 | 1600.00 | 1600.00 | SHARMA TRADE AGENCY
17.00 | Providing and fixing 6 SWG dia G.I. wire on ground, surface or in recess for loop earthing along with existing suface/ recessed conduit/ submain wiring/ cable as required | 20.00 | mtr | 100.00 | 30.00 | 600.00 | 600.00 | SHARMA TRADE AGENCY
18.00 | Supply of 160 mm dia (OD), minimum 7.7 mm thick, PE 63 HDPE pipes as per relavent IS and technical specification of the tender complete as required. | 380.00 | mtr | 100.00 | 620.00 | 235600.00 | 235600.00 | SHARMA TRADE AGENCY
19.00 | Laying of 160mm dia (OD) HDPE with HDD trenchless method direct in ground in all type soil including suitable size PP rope coupling of pipe, etc. Complete in all respect as per specification. (HDPE Pipe is not inclusive) | 380.00 | mtr | 100.00 | 1500.00 | 570000.00 | 570000.00 | SHARMA TRADE AGENCY
20.00 | Supply & Fixing of full round RCC joint chamber with diameter of 85cm and height of 100cm and thickness of 7.5cm round top cover with diameter of 100cm and thickness of 5cm etc complete as required | 6.00 | each | 100.00 | 18000.00 | 108000.00 | 108000.00 | SHARMA TRADE AGENCY
21.00 | Supply of 1.5 TR five star split type inverter air conditioners fitted with high EER twin rotary - BLDC compressors, operating on refrigrant R-410A or higher wall mounting suitable for operation on 230V, 50 Hz, Single phase, AC supply, complete with filter, drain & refrigerant pipe with insulation & electrical connection with wire complete as reqd. (Note : cost of drain (UPVC), regrigerant piping with insulation and electrical cable upto 10 feet length is included in this item) | 4.00 | each | 100.00 | 45000.00 | 180000.00 | 180000.00 | SHARMA TRADE AGENCY
22.00 | Installation, testing and commissoning of 1.5/2.0 TR split type air conditioner i/c Copper piping work, providing stand for outdoor unit, compelete with wall cutting, hole cutting, plastering etc. as reqd. | 4.00 | each | 100.00 | 3000.00 | 12000.00 | 12000.00 | SHARMA TRADE AGENCY
23.00 | Dismantling and re-installation of 1.5 TR/ 2.0 TR capacity Split type air-conditioners units with existing refrigerant piping including mounting of indoor and out door units, drain piping arrangements, charging of refrigerant gas, insulation of refrigerant piping with extended polythylene / PVC piping etc. complete as required. | 8.00 | Job | 100.00 | 4000.00 | 32000.00 | 32000.00 | SHARMA TRADE AGENCY
24.00 | Supply and Fixing of extra copper piping and cable and for 1.5 TR Split AC including chipping and minor civil work complete with all accessories as required. | 30.00 | mtr | 100.00 | 1100.00 | 33000.00 | 33000.00 | SHARMA TRADE AGENCY
25.00 | Supply and Fixing of extra drain piping UPVC 25mm with insulation of suitable size for 1.5/2.0 TR Split AC including chipping and minor civil work complete with all accessories as required. | 30.00 | mtr | 100.00 | 100.00 | 3000.00 | 3000.00 | SHARMA TRADE AGENCY
26.00 | SITC of Timers for A.C. of 1.5/2.0 TR Capacity (5 Star Rating) up to 4 Hours automatic changing operation complete as required. | 6.00 | each | 100.00 | 3000.00 | 18000.00 | 18000.00 | SHARMA TRADE AGENCY
27.00 | Supply, installation, testing and commissioning of 2 KVA wall/ Floor mounting stablizer with TDR three step auto with high / low cut off complete as required suitable for input voltage from 150 to 280 V giving out put 200 to 240 at 50HZ AC supply etc. as required. | 12.00 | each | 100.00 | 2400.00 | 28800.00 | 28800.00 | SHARMA TRADE AGENCY
| Total in Figures |  |  |  |  | 6245485.00
Lowest Amount Quoted BY: SHARMA TRADE AGENCY(6245485.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of ILS System at Dibrugarh Airport. SH- Electrical works Tender ID: 2020_AAI_40613_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SHARMA TRADE AGENCY | 6245485.00 | L1