## BoQ1
Government eProcurement System Created By: Rohit Verma Created Date/Time: 24-Feb-2020 05:05 PM Tender Title: Provision of CCTV system including 3 years all inclusive comprehensive maintenance contract (AICMC) after DLP of 3 years for RED Office Complex and AAI Residential Colony at Guwahati Airport Tender ID: 2020_AAI_41154_1
Tender Inviting Authority: Airports Authority of India
Name of Work: Provision of CCTV system including 3 years all inclusive comprehensive maintenance contract (AICMC) after DLP of 3 years for RED Office Complex and AAI Residential Colony at Guwahati Airport.
Contract No: AAI/ELECT/GHY/CCTV/NIT02/1920
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | G S Computel Pvt Ltd |  | Hue Service Pvt Ltd |  | Binary Solutions Pvt Ltd
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH A: SITC of CCTV system SITC of following : (i) 64 channel NVR with minimum Quad-core embedded processor, Embedded LINUX OS or Windows, 1 HDMI up to 3840X2160 resolution output, With one channel audio input and one channel audio output, suitable For Live view of 16 Nos,1080P cameras and recording playback, 1GBPS network Card, should support HTTP, TCP/IP, IPv4/IPv6, NTP, DHCP,DNS, IP Filter, PPPoE, DDNS, FTP, Alarm Server, IP Search, P2P, network throughput Input 320 Mbps; Output 320 Mbps, Recording Mode Schedule (Regular/Continuous, Motion Detection, Alarm); Manual; Stop, the NVR should able to monitor from anywhere using the mobile apps for both Apple® and Android ™ devices, should Support at least 12 user access the NVR simultaneously, etc. complete as required. Make : Bosch, Pelco, Ultrak, Honeywell (ii) 64 TB internal inbuilt storage supports Surveillance grade HDDs (8 TB Surveillance HDD each) (iii) 2 kVA, 1 Phase, 50Hz, 230V, IGBT Based Online UPS with inbuilt 12V SMF batteries, minimum back up 30 minutes, suitable to input voltage range of 170V to 280V and frequency range 40 hz to 60 hz etc. complete as required,. Make : Emersion, Vertiv,APC,Numeric (iv) 17U Floor Standing Rack has steel sheet punched, formed, welded and Powder coated, 14001 Certified Company & UL Listed, welded frame with side panel and vented top cover, 600MM Wide & 1000MM Deep, Conforms to DIN 41494 or Equivalent EIA /ISO / EN/CEA Standard, 1 No.PDU , 1Ph, 230V, 32A, 50/60Hz, Zero U standard with minimum 6 or 12 Indian Round Pin 5/15A sockets, two Circuits of 16A MCB, etc. complete as required. (v) Indoor Managed Network Switch 20 ports ,10/100/1000T PoE and 4 Combo ports. Minimum PoE power budget 185Watt or better, min 56Gbps or higher Switching capacity, min 41Mpps or higher forwarding rate, Port Mirroring ,IEEE 802.1d Spanning-Tree, IEEE 802.1w Rapid Spanning-Tree, IEEE 802.1s Multiple Spanning-Tree, Broadcast Storm Protection, Port Based VLAN, Support SNMPv1/v2c/v3 , Web-based configuration, Compliant UL 1950,UL94V-0,WEEE, IEC 68-2-32, IEC 68-2-29, IEC 68-2-36,, FCC/EN55022 Class A, VCCI Class A,C-Tick, EN60950 (TUV), EN55024, CE, CSA / CUL and RoHS, loaded with 2 Nos of SM 1G SFP Transceivers, etc. complete as required. (vi) OFC cable termination including LIU with Pigtail ,Patch cord with SC/LC connectors, complete as required. ( applicable for OFC cable termination) (vii) CAT 6 cable termination including Patch Panel,Patch cord with RJ 45 connectors etc. complete as required. (applicable for CAT6 cable termination) | 1.00 | JOB | 100.00 | 622603.00 | 622603.00 | 492894.00 | 492894.00 | 653733.00 | 653733.00 | 492894.00 | Hue Service Pvt Ltd
2.00 | SITC of full HD LED Monitor of size not less than 43 inches including wall- bracket complete as required. Make: LG, Samsung, Sony, Bosch, Ultrak, Pelco | 1.00 | JOB | 100.00 | 33600.00 | 33600.00 | 26600.00 | 26600.00 | 35280.00 | 35280.00 | 26600.00 | Hue Service Pvt Ltd
3.00 | SITC of indoor dome type CCTV camera of 2 MP, 1/2.8" Progressive Scan CMOS; H.265, 0 Lux with IR range 20 m or Higher ;30fps/60fps(1920×1080); 3mm fixed lens; 120dB WDR;3 streams; 3D DNR; BLC; IP66;IK10; PoE; Built-in micro SD/SDHC slot; with accessories as per specification, with video analytic: Face Detection, Object Abandoned, Object Missing, Intrusion, cyber secured UL/FCC/EN / RoHS certified with mounting/fixing accessories including software, termination with existing CAT 6/ OFC cable, etc. complete as per actual site requirement. Make : Bosch, Pelco, Ultrak, Honeywell, | 36.00 | JOB | 100.00 | 28560.00 | 1028160.00 | 22610.00 | 813960.00 | 29988.00 | 1079568.00 | 813960.00 | Hue Service Pvt Ltd
4.00 | SITC of outdoor bullet type CCTV camera of 2 MP IR Bullet Camera, 1/2.8" progressive scan CMOS, vari-focal 2.8~ 12mm,120dB WDR, 60 m IR Range (Internal/External), PoE, Built-in micro SD/SDHC slot, Housing - IP66 , IK10, H.265,Cyber Security Hardware chipset for private key, ONVIF, video analytic lic: Motion Detection, Video Tampering, Face Detection, Audio Detection, Object Abandoned, object missing supported outdoor bullet camera with mounting/fixing accessories including software,termination with existing CAT 6/ OFC cable,etc. complete as per actual site requirement. Make : Bosch, Pelco, Ultrak, Honeywell, | 20.00 | JOB | 100.00 | 46200.00 | 924000.00 | 36575.00 | 731500.00 | 48510.00 | 970200.00 | 731500.00 | Hue Service Pvt Ltd
5.00 | SITC of following : (i) Indoor Managed Network Switch with 8 ports 10/100/1000T PoE, 2 combo ports , minimum 75 watt PoE or better, min 20Gbps or higher Switching capacity, min 14Mpps or higher forwarding rate, Port Based VLAN, support Broadcast Storm Protection, Port Mirroring ,IEEE 802.1d Spanning-Tree, IEEE 802.1w Rapid Spanning-Tree,IEEE 802.1s Multiple Spanning-Tree, Web-based configuration, Complaint of UL 1950,UL94V-0,WEEE, IEC 68-2-32, IEC 68-2-29, IEC 68-2-36, FCC/EN55022 Class A, VCCI Class A,C-Tick, EN60950 (TUV), EN55024, CE, CSA / CUL and RoHS, loaded with 2 Nos of SM 1G SFP Transceivers etc.complete as required. (ii) 600VA, 1 Phase, 50Hz, 230V, Line-Inetractive UPS with 12V SMF inbuilt battery back up of 30 minutes suitable to input voltage range of 220 V to 230 V and frequency range 50 hz to 60 hz, etc. complete as required . Make : Emersion, Vertiv, APC,Numeric (iii) 6U Wall Mount Rack has steel sheet punched, formed, welded and Powder coated, 14001 Certified company & UL Listed, welded frame with side panel and vented top cover, 550MM Wide & 600MM Deep, conforms to DIN 41494 or Equivalent EIA /ISO / EN/CEA Standard, 1 No.of PDU, 1Ph, 230V, 8A, with 6 Indian Round Pin 5A sockets, 8A Fuse, etc.complete as required. (iv) OFC cable termination including LIU with Pigtail ,Patch cord with SC/LC connectors, etc. complete as required. ( applicable for OFC cable termination) (v) CAT 6 cable termination including Patch Panel,Patch cord with RJ 45 connectors etc. complete as required. (applicable for CAT6 cable termination) | 5.00 | JOB | 100.00 | 93558.00 | 467790.00 | 74066.00 | 370330.00 | 98236.00 | 491180.00 | 370330.00 | Hue Service Pvt Ltd
6.00 | SITC of following components : (i) Indoor Managed Network Switch 20ports , 10/100/1000T PoE and 4 Combo ports. Minimum PoE power budget 185Watt or better, min 56Gbps or higher Switching capacity, min 41Mpps or higher forwarding rate, Port Mirroring ,IEEE 802.1d Spanning-Tree, IEEE 802.1w Rapid Spanning-Tree,IEEE 802.1s Multiple Spanning-Tree, Broadcast Storm Protection, Port Based VLAN, Support SNMPv1/v2c/v3 , Web-based configuration, Compliant UL 1950,UL94V-0,WEEE, IEC 68-2-32, IEC 68-2-29, IEC 68-2-36,, FCC/EN55022 Class A, VCCI Class A,C-Tick, EN60950 (TUV), EN55024, CE, CSA / CUL and RoHS, loaded with 2 Nos of SM 1G SFP Transceivers, etc. complete as required. (ii) 600VA, 1 Phase, 50Hz, 230V, Line-Inetractive UPS with 12V SMF inbuilt battery back up of 30 minutes suitable to input voltage range of 220 V to 230 V and frequency range 50 hz to 60 hz, etc. complete as required . Make : Emersion, Vertiv, APC,Numeric (iii) 6U Wall Mount Rack has steel sheet punched, formed, welded and Powder coated, 14001 Certified company & UL Listed, welded frame with side panel and vented top cover, 550MM Wide & 600MM Deep, conforms to DIN 41494 or Equivalent EIA /ISO / EN/CEA Standard, 1 No.of PDU, 1Ph, 230V, 8A, with 6 Indian Round Pin 5A sockets, 8A Fuse etc. complete as required. (iv) OFC cable termination including LIU with Pigtail ,Patch cord with SC/LC connectors,etc. complete as required. ( applicable for OFC cable termination) (v) CAT 6 cable termination including Patch Panel,Patch cord with RJ 45 connectors, etc. complete as required. (applicable for CAT6 cable termination) | 1.00 | JOB | 100.00 | 107179.00 | 107179.00 | 84850.00 | 84850.00 | 112538.00 | 112538.00 | 84850.00 | Hue Service Pvt Ltd
7.00 | Supply of 4 pairs, Unshielded Twisted Pair, Category 6, TIA / EIA 568-C.2, 23 AWG solid bare copper or better, Polyethylene, Sheath Fire retardant PVC Compound (FRPVC) Flame Rating : 60 deg. C As per UL 1685 CM/CMR, Minimum 250Mhz (certified) support up to 600 MHz, UL Verified, ISO 9001 and 14001 certified Make : RALLISON/ DELTON/ RHINO/ CM/ POLYCAB/ LEGRAND/ UNICAB/ AVOCAB/ RR KABEL/ GEMSCAB/ CORDS/ SCHNEIDER | 1000.00 | Mtrs. | 100.00 | 30.00 | 30000.00 | 24.00 | 24000.00 | 32.00 | 32000.00 | 24000.00 | Hue Service Pvt Ltd
8.00 | Supply of CAT 6, 4-Pair of Solid Insulated Copper 23 AWG, ANSI/TIA/EIA-568 and ISO/IEC 11801, Flammability Test: CM, Conductor Dia. Nom. (mm) : 0.565, Polyester Binder, Outer Diameter: 7.30mm +-0.2, Tensile Strength (Mpa): ≥13.8, Frequency /Attenuation /NEXT/ PSNEXT/ ACRF /PSACRF /RL/DELAY Tested upto 250 Mhz, ISO 9001:2008, ISO 9001:14001, ISO 50001 certified manufacturing unit Make : RALLISON/ DELTON/ RHINO/ CM/ POLYCAB/ LEGRAND/ UNICAB/ AVOCAB/ RR KABEL/ GEMSCAB/ CORDS/ SCHNEIDER | 200.00 | Mtrs. | 100.00 | 123.00 | 24600.00 | 97.00 | 19400.00 | 129.00 | 25800.00 | 19400.00 | Hue Service Pvt Ltd
9.00 | Supply of fiber optic cable, with numbers of core not less then 6, Single Mode, OS2, Armored, Loose Tube – Unitube, CSTA, Jelly Filled, 9/ 125, Telcordia’s GR-20 and ITU-T 652.D Compliance, OS2, BELLCORE GR 20 / IEC 794-1, Cable must have Water blocking compound, Maximum Crush resistance Not less than 2000N/100mm, High density polyethylene, anti - termite, anti - rodent suitable for direct burial application., Polymer Coating over Corrugated Steel tape, As per ANSI/TIA-568-C.3 and ISO/IEC-11801, ICEA-640 Make : CRYSTAL / RALLISON / KEI / WORLDCAB / RAVIN / DELTON / DYNAMIC / RHINO / CMI / POLYCAB / UNICAB / AVOCAB / RR KABEL / GEMSCAB / HAVELLS / BONTON/ CORDS | 2000.00 | Mtrs. | 100.00 | 52.00 | 104000.00 | 41.00 | 82000.00 | 55.00 | 110000.00 | 82000.00 | Hue Service Pvt Ltd
10.00 | Supply of 3 Core, 1.5 SQMM copper conductor XLPE insulated PVC sheathed armoured cable confirming to IS 7098 Part I-1988 with upto date amendment as required. Make : RALLISON/ DELTON/ RHINO/ CM/ POLYCAB/ UNICAB/ AVOCAB/ RR KABEL/ GEMSCAB/ CORDS/ SCHNEIDER | 200.00 | Mtrs. | 100.00 | 160.00 | 32000.00 | 126.00 | 25200.00 | 58.00 | 11600.00 | 11600.00 | Binary Solutions Pvt Ltd
11.00 | Supply and fixing of 25 mm of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as per technical specifications complete as required. | 800.00 | Meter | 100.00 | 42.00 | 33600.00 | 36.00 | 28800.00 | 44.00 | 35200.00 | 28800.00 | Hue Service Pvt Ltd
12.00 | Drawing of CAT 6, 4 pairs, UTP or SF/UTP cable in the existing surface/recessed steel /PVC conduit as per technical specifications complete as required. | 800.00 | Meter | 100.00 | 55.00 | 44000.00 | 23.00 | 18400.00 | 58.00 | 46400.00 | 18400.00 | Hue Service Pvt Ltd
13.00 | Laying and fixing of one number CAT 6, 4 pairs, UTP or SF/UTP cable or OFC on wall surface as per technical specifications complete as required. | 200.00 | Meter | 100.00 | 60.00 | 12000.00 | 30.00 | 6000.00 | 63.00 | 12600.00 | 6000.00 | Hue Service Pvt Ltd
14.00 | Laying of one number OFC in the existing RCC/ HUME/ METAL/HDPE pipe as per technical specifications complete as required. | 1800.00 | Meter | 100.00 | 156.00 | 280800.00 | 73.00 | 131400.00 | 164.00 | 295200.00 | 131400.00 | Hue Service Pvt Ltd
15.00 | Supplying and laying of 25 mm dia (nominal), PN 12.5 pressure rating, ISI marked HDPE pipe (PE 100) along with all accessories like socket, bend, couplers etc. conforming to relevant IS complete with fitting and cutting, jointing etc.direct in ground (25 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 1800.00 | Meter | 100.00 | 60.00 | 108000.00 | 48.00 | 86400.00 | 63.00 | 113400.00 | 86400.00 | Hue Service Pvt Ltd
16.00 | Supplying and laying of 25 mm dia (nominal), PN 12.5 pressure rating, ISI marked HDPE pipe (PE 100) along with all accessories under the road/ drain/ hard standing i/c excavation , laying of pipe,back filling of earth and making good the road/ surface / drain similar to existing one complete as per site requirements. | 100.00 | Meter | 100.00 | 60.00 | 6000.00 | 48.00 | 4800.00 | 63.00 | 6300.00 | 4800.00 | Hue Service Pvt Ltd
17.00 | Supplying and fixing of 25 mm dia (nominal), PN 12.5 pressure rating, ISI marked HDPE pipe (PE 100) along with all accessories on wall/surface for cable protection etc.as per technical specifications complete as required. | 100.00 | Meter | 100.00 | 60.00 | 6000.00 | 48.00 | 4800.00 | 63.00 | 6300.00 | 4800.00 | Hue Service Pvt Ltd
18.00 | Supplying and fixing 25 mm dia PVC flexible pipe along with all accessories like coupler etc. as per technical specifications complete as required. | 400.00 | Mtrs. | 100.00 | 42.00 | 16800.00 | 33.00 | 13200.00 | 44.00 | 17600.00 | 13200.00 | Hue Service Pvt Ltd
19.00 | SITC of following components (i) 16 channel NVR with minimum Quad-core embedded processor, Embedded LINUX OS / Windows OS, 1 HDMI up to 3840×2160 resolution output, with one channel audio input and one channel audio output, suitable for live view of 16 Nos. 1080P cameras and recording playback, 1 GBPS network Card, should support HTTP, TCP/IP,IPv4/IPv6, NTP, DHCP, DNS, IP Filter, PPPOE, DDNS DDNS, FTP, Alarm Sever, IP Search, P2P, onboard 16 ports POEIEEE802.3at, network throughput Input 320 Mbps; Output 320 Mbps, Recording Mode Schedule (Regular/ Continuous, Motion Detection, Alarm); the NVR should be able to monitor from anywhere using the mobile apps for both Apple® and Android™ devices, should support at least 12 user access the NVR simultaneously etc. complete as required. Make : Bosch, Pelco, Ultrak, Honeywell (ii)16 TB internal storage supports Surveillance grade HDDs expandable upto 64 TB (8TB Surveillance HDD each) (iii) 2 kVA, 1 Phase, 50Hz, 230V, IGBT Based Online UPS with inbuilt 12V SMF batteries, minimum back up of 30 minutes, suitable to input voltage range of 170V to 280V and frequency range 40 hz to 60 hz complete as required . Make : Emersion, Vertiv,APC, Numeric (iv) 6U Wall Mount Rack has steel sheet punched, formed, welded and Powder coated, 14001 Certified company & UL Listed, welded frame with side panel and vented top cover, 550MM Wide & 600MM Deep, conforms to DIN 41494 or Equivalent EIA /ISO / EN/CEA Standard, 1 No.of PDU, 1Ph, 230V, 8A, with 6 Indian Round Pin 5A sockets, 8A Fuse etc. complete as required. (v) Indoor Managed Network Switch with 8*10/100/1000T PoE, 2 combo ports , minimum 75 watt PoE or better, min 20Gbps or higher Switching capacity, min 14Mpps or higher forwarding rate, Port Based VLAN, support Broadcast Storm Protection, Port Mirroring ,IEEE 802.1d Spanning-Tree, IEEE 802.1w Rapid Spanning-Tree,IEEE 802.1s Multiple Spanning-Tree, Web-based configuration, Complaint of UL 1950,UL94V-0,WEEE, IEC 68-2-32, IEC 68-2-29, IEC 68-2-36, FCC/EN55022 Class A, VCCI Class A,C-Tick, EN60950 (TUV), EN55024, CE, CSA / CUL and RoHS, loaded with 2 Nos of SM 1G SFP Transceivers etc. complete as required. (vi) OFC cable termination including LIU with Pigtail ,Patch cord with SC/LC connectors, complete as required. ( applicable for OFC cable termination) (vii) CAT 6 cable termination including Patch Panel,Patch cord with RJ 45 connectors etc. complete as required. (applicable for CAT6 cable termination) | 1.00 | JOB | 100.00 | 306582.00 | 306582.00 | 242710.00 | 242710.00 | 321911.00 | 321911.00 | 242710.00 | Hue Service Pvt Ltd
20.00 | SITC of following components (i) Industrial Grade Managed Switch with minimum 4x10/100 Base-T PoE+ ports and 2x100/1000X SFP ports. Minimum PoE budget should be 120Watt, min. 4.8 Gbps, Console port: RJ45 x 1 or Equivalent. Min 2K MAC address table and support 2K VLAN simultaneously, 48 VDC Redundant power inputs. Min. IP 30/31 Metal Case, Switch enclosure should be with Aluminium Shell, DIN Rail / Wall mount support, Operating Temperature: -10 - 75ºC , Storage Temperature: -40 - 85ºC, Switch Should be UL, EN61000-4-2, EN61000-4-3, EN61000-4-4, EN61000-4-5, EN60068-2-27, EN60068-2-6, RoHS and NEMA TS2, Rapid Ring Protection /resiliency technology as per the IEEE 802.17 / RPR / ERPS or equivalent technology providing the convergence time as per the standards specified above for less than/sub 50 millisecond convergence. VLAN IEEE 802.1Q, GVRP, double tagging (Q-in-Q), Port Based VLAN, LACP, RSTP, MSTP, loaded with 2 Nos of SM 1G SFP Transceivers. (ii) 600VA, 1 Phase, 50Hz, 230V, Line-Inetractive UPS with 12V SMF inbuilt battery back up of 30 minutes suitable to input voltage range of 220 V to 230 V and frequency range 50 hz to 60 hz, etc. complete as required . Make : Emersion, Vertiv, APC,Numeric (iii) OFC cable termination including LIU with Pigtail ,Patch cord with SC/LC connectors, etc, complete as required. ( applicable for OFC cable termination) (iv) CAT 6 cable termination including Patch Panel,Patch cord with RJ 45 connectors etc. complete as required. (applicable for CAT6 cable termination) (v) Pole mount Enclosure of size 06UH x 600W x 500D, All Round welded construction with through design degree opening with concealed hinges, Front Hinged Single Door with Hood Provision, 130, Top with Rain Canopy and 1 no. Fan Provision, Bottom flush type gland plate, with rear wall for wall mounting provision, Foam Gasketing,, 04 number 19" recess angle, Finish RAL 7035 STR, Rain Canopy of size 600W x 500D -1 No, Pole mounting bracket -2 Nos., Pole clamp 'C' Channel Bracket- 4 Nos., IP54 Inlet/Outlet Filter - Snap type with PU Gasket Overall Grill Size -148 x 148 - 2 Nos., Filter Hood for 148 x 148 Filter -1 No., Fan-1 No., Power Distribution Unit - 06 Amp 6 x Sockets (vi) Power Input Line surge protector (vii) Data (Ethernet) line Surge Protector | 3.00 | JOB | 100.00 | 170643.00 | 511929.00 | 135092.00 | 405276.00 | 179175.00 | 537525.00 | 405276.00 | Hue Service Pvt Ltd
21.00 | Supply,Erection of Galvanized pole made out of 150 mm nominal dia medium class GI pipe of 6 metre long with clear hight above ground level not less than 5 mtr. including earthing connection complete as required. The pole shall be installed in RCC foundation 1:2:4 i.e 1cement : 2coarse sand :4 graded stone of size 1200mm X 400mm X 400mm and P.C.C foundation of 1:4:8 i.e 1cement :4coarse sand: 8 graded stone of size 150mm X 600mm X 600mm by laying iron bar mesh including providing two numbers 25 mm dia 1.0 metre long HDPE pipe to carry loop in loop out cables etc.complete as required. GI Pipe make - PRAKASH SURYA / TATA/ HSL/ SAIL/ JINDAL | 3.00 | JOB | 100.00 | 33600.00 | 100800.00 | 26700.00 | 80100.00 | 35280.00 | 105840.00 | 80100.00 | Hue Service Pvt Ltd
22.00 | SITC of point to point 5 Ghz 800 Mbps or Higher Outdoor Wireless Radio , Radio- 802.11ac/n/a Radio Frequency Range: 5.150 -5.250GHz 5.250 - 5.350GHz 5.470 - 5.725GHz 5.725 - 5.825GHz Tx Power 27dBm Rx Sensitivity 867Mbps: -67dBm@10% PER 300M: -74dBm@10% PER 54M: -78dBm@10% PER 1M: -98dBm@10% PER, Antenna-25dBi dual-polarized panel directional antenna Beam width (HPBW) Horizontal: >10°, Vertical:>10° Open space up to 1~45km or better, Interfaces-1 x 10/100/1000 Base-T Ethernet Gigabit LAN with Passive PoE Grounding Terminal, Security - Integrated Firewall WPA/WPA2; WPA-PSK / WPA2-PSK Encryption; 64/128-bit WEP, Enclosure Die-cast Aluminium, Ingress protection IP67 , Lighting Protection 8kV or Higher , ESD Protection 16kV or Higher, Power 24VDC or PoE, CE, FCC, RoHS Compliant. Make : Cisco, Ubiquiti, Aruba, WIS | 1.00 | JOB | 100.00 | 61320.00 | 61320.00 | 48545.00 | 48545.00 | 64386.00 | 64386.00 | 48545.00 | Hue Service Pvt Ltd
23.00 | Remote Viewer (i) SITC of client Machine PC i7 8Gen Processor 8 GB RAM. 1TB internal HDD , 1 GBPS NIC, 4GB Dedicated Graphics Card with 32 Inch Monitor, NVR Viewer software for view multi NVR in a single software over Internet/Intranet. Main video viewing screen capable of showing 1, 4, 9, 16, and other customized split salvos of live or recorded video. Standard presets shall be customizable to the user preferences, Capable of saving current salvo as a View and allowing the user to drag this view at any later point in time, Capable of exporting user selected image or video clips in encripted formats. Capable of attaching a digital signature for authentication of exported clips etc. complete as required. PC make - HP / DELL / WIPRO / IBM (ii) 600VA, 1 Phase, 50Hz, 230V, Line-Inetractive UPS with 12V SMF inbuilt battery back up of 30 minutes suitable to input voltage range of 220 V to 230 V and frequency range 50 hz to 60 hz, etc. complete as required . Make : Emersion, Vertiv, APC,Numeric and Mobile Viewing Software capable to view live and recorded video on mobile, and steaming data route through Indian, UK and US servers, declaration pertaining to this shall be provided by both OEM and agency. | 1.00 | JOB | 100.00 | 158256.00 | 158256.00 | 125286.00 | 125286.00 | 166169.00 | 166169.00 | 125286.00 | Hue Service Pvt Ltd
24.00 | SH B: 3 years all inclusive CMC (AI CMC) for CCTV system after defect liability period of 3 years All inclusive CMC for the system 1st year after 3 years DLP (Excluding GST) @ 5% of (A) | 1.00 | JOB | 100.00 | 251001.00 | 251001.00 | 193323.00 | 193323.00 | 262537.00 | 262537.00 | 193323.00 | Hue Service Pvt Ltd
25.00 | All inclusive CMC for the system 2nd year after 3 years DLP (Excluding GST)@ 6% of (A) | 1.00 | JOB | 100.00 | 301201.00 | 301201.00 | 231987.00 | 231987.00 | 315044.00 | 315044.00 | 231987.00 | Hue Service Pvt Ltd
26.00 | All inclusive CMC for the system 3rd year after 3 years DLP (Excluding GST) @7% of (A) | 1.00 | JOB | 100.00 | 351401.00 | 351401.00 | 270652.00 | 270652.00 | 367551.00 | 367551.00 | 270652.00 | Hue Service Pvt Ltd
| Total in Figures |  |  |  |  | 5923622.00 |  | 4562413.00 |  | 6195862.00
Lowest Amount Quoted BY: Hue Service Pvt Ltd(4562413.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of CCTV system including 3 years all inclusive comprehensive maintenance contract (AICMC) after DLP of 3 years for RED Office Complex and AAI Residential Colony at Guwahati Airport Tender ID: 2020_AAI_41154_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Hue Service Pvt Ltd | 4562413.00 | L1
| 2 | G S Computel Pvt Ltd | 5923622.00 | L2
| 3 | Binary Solutions Pvt Ltd | 6195862.00 | L3