## BoQ1
Government eProcurement System Created By: Hemant Bhavsar Created Date/Time: 28-Feb-2020 11:45 AM Tender Title: Misc unforeseen Electrical works. SH- Replacement of faulty LT Power Cable for T-2 Car Park area and Main Approach road of T 1 at SVPI Airport, Ahmedabad Tender ID: 2020_AAI_41155_1
Tender Inviting Authority: Asstt. Gen. Manager (Engg.-Elect), Airports Authority of India, S.V.P.I. Airport, Ahmedabad
Name of Work: Misc. unforeseen Electrical works. SH:- Replacement of faulty LT Power Cable for T-2 Car Park area and Main Approach road of T-1 at SVPI Airport, Ahmedabad.
Contract No: 079-22858057
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ABHISHEK ASSOCIATES |  | Manish Electricals |  | Techno Electricals |  | Taral Electricals |  | BR Power Control and Automation Services |  | jaydeep agency corporation |  | RVD INFRA SOLUTION PVT.LTD. |  | Yash Energy Pvt. Ltd |  | Ascent Electrification Engineers |  | INDIAN ELECTRIC CORPORATION |  | TRINITY ENGINEERS
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 3.5 core x 150 sqmm sizes LT power cable of 1.1 KV grade of aluminium conductor XLPE insulated PVC sheathed armoured cable confirming to IS 7098 (part-1) 1988 with upto date amendment as required. | 1500.00 | Mtr. |  | 429.00 | 643500.00 | 487.00 | 730500.00 | 449.00 | 673500.00 | 433.00 | 649500.00 | 448.00 | 672000.00 | 600.00 | 900000.00 | 511.00 | 766500.00 | 432.00 | 648000.00 | 486.79 | 730185.00 | 417.00 | 625500.00 | 492.00 | 738000.00 | 625500.00 | INDIAN ELECTRIC CORPORATION
2.00 | Supply of 3.5 core x 70 sqmm sizes LT power cable of 1.1 KV grade of aluminium conductor XLPE insulated PVC sheathed armoured cable confirming to IS 7098 (part-1) 1988 with upto date amendment as required. | 120.00 | Mtr. |  | 240.00 | 28800.00 | 253.00 | 30360.00 | 239.00 | 28680.00 | 247.00 | 29640.00 | 286.00 | 34320.00 | 500.00 | 60000.00 | 285.00 | 34200.00 | 246.00 | 29520.00 | .96 | 115.20 | 234.00 | 28080.00 | 272.00 | 32640.00 | 115.20 | Ascent Electrification Engineers
3.00 | Supply of 3.5 core x 50 sqmm sizes LT power cable of 1.1 KV grade of aluminium conductor XLPE insulated PVC sheathed armoured cable confirming to IS 7098 (part-1) 1988 with upto date amendment as required. | 290.00 | Mtr. |  | 177.00 | 51330.00 | 183.00 | 53070.00 | 179.00 | 51910.00 | 179.00 | 51910.00 | 185.00 | 53650.00 | 400.00 | 116000.00 | 209.00 | 60610.00 | 182.00 | 52780.00 | .96 | 278.40 | 172.00 | 49880.00 | 200.00 | 58000.00 | 278.40 | Ascent Electrification Engineers
4.00 | Supply of 3.5 core x 35 sqmm sizes LT power cable of 1.1 KV grade of aluminium conductor XLPE insulated PVC sheathed armoured cable confirming to IS 7098 (part-1) 1988 with upto date amendment as required. | 85.00 | Mtr. |  | 136.00 | 11560.00 | 148.00 | 12580.00 | 155.00 | 13175.00 | 142.00 | 12070.00 | 130.00 | 11050.00 | 300.00 | 25500.00 | 162.00 | 13770.00 | 139.00 | 11815.00 | .96 | 81.60 | 133.00 | 11305.00 | 154.00 | 13090.00 | 81.60 | Ascent Electrification Engineers
5.00 | Supply of 4 core x 25 sqmm sizes LT power cable of 1.1 KV grade of aluminium conductor XLPE insulated PVC sheathed armoured cable confirming to IS 7098 (part-1) 1988 with upto date amendment as required. | 135.00 | Mtr. |  | 124.00 | 16740.00 | 101.00 | 13635.00 | 128.00 | 17280.00 | 128.00 | 17280.00 | 131.00 | 17685.00 | 275.00 | 37125.00 | 147.00 | 19845.00 | 93.00 | 12555.00 | .96 | 129.60 | 121.00 | 16335.00 | 140.00 | 18900.00 | 129.60 | Ascent Electrification Engineers
6.00 | Supply of 4 core x 10 sqmm sizes LT power cable of 1.1 KV grade of aluminium conductor XLPE insulated PVC sheathed armoured cable confirming to IS 7098 (part-1) 1988 with upto date amendment as required. | 65.00 | Mtr. |  | 79.00 | 5135.00 | 70.00 | 4550.00 | 69.00 | 4485.00 | 83.00 | 5395.00 | 98.00 | 6370.00 | 110.00 | 7150.00 | 93.00 | 6045.00 | 81.00 | 5265.00 | .96 | 62.40 | 78.00 | 5070.00 | 90.00 | 5850.00 | 62.40 | Ascent Electrification Engineers
7.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of size upto 35 sq. mm in the existing. RCC/HUME/STONEWARE/METAL/DWC pipe as required. | 285.00 | Mtr. |  | 20.00 | 5700.00 | 30.00 | 8550.00 | 55.00 | 15675.00 | 29.00 | 8265.00 | 91.00 | 25935.00 | 20.00 | 5700.00 | 73.00 | 20805.00 | 32.00 | 9120.00 | 1.15 | 327.75 | 40.00 | 11400.00 | 40.00 | 11400.00 | 327.75 | Ascent Electrification Engineers
8.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of size exceeding Above 35 sq. mm and upto 95 sq. mm. mm in the existing. RCC/HUME/STONEWARE/METAL/DWC pipe as required. | 410.00 | Mtr. |  | 20.00 | 8200.00 | 30.00 | 12300.00 | 55.00 | 22550.00 | 38.00 | 15580.00 | 91.00 | 37310.00 | 25.00 | 10250.00 | 73.00 | 29930.00 | 40.00 | 16400.00 | 1.28 | 524.80 | 50.00 | 20500.00 | 46.00 | 18860.00 | 524.80 | Ascent Electrification Engineers
9.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of size exceeding Above 95 sq. mm and upto 185 sq. mm in the existing. RCC/HUME/STONEWARE/METAL/DWC pipe as required. | 1500.00 | Mtr. |  | 20.00 | 30000.00 | 50.00 | 75000.00 | 55.00 | 82500.00 | 32.00 | 48000.00 | 70.00 | 105000.00 | 30.00 | 45000.00 | 73.00 | 109500.00 | 50.00 | 75000.00 | 74.78 | 112170.00 | 65.00 | 97500.00 | 52.00 | 78000.00 | 30000.00 | ABHISHEK ASSOCIATES
10.00 | Supplying and fixing of 120 mm dia (OD-120 mm & ID-103 mm nominal) size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. on wall surface with suitable size clamped with 20/25 mm x 3 mm flat iron clamp. complete as required. | 100.00 | Mtr. |  | 119.00 | 11900.00 | 290.00 | 29000.00 | 200.00 | 20000.00 | 150.00 | 15000.00 | 183.00 | 18300.00 | 120.00 | 12000.00 | 219.00 | 21900.00 | 188.00 | 18800.00 | 230.40 | 23040.00 | 275.00 | 27500.00 | 156.00 | 15600.00 | 11900.00 | ABHISHEK ASSOCIATES
11.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size above 35 sq. mm and upto 95 sq. mm in the existing masonry open duct as required. | 25.00 | Mtr. |  | 20.00 | 500.00 | 30.00 | 750.00 | 45.00 | 1125.00 | 24.00 | 600.00 | 37.00 | 925.00 | 25.00 | 625.00 | 97.00 | 2425.00 | 30.00 | 750.00 | 1.15 | 28.75 | 40.00 | 1000.00 | 40.00 | 1000.00 | 28.75 | Ascent Electrification Engineers
12.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size above 35 sq. mm and upto 95 sq. mm (clamped with suitable tie belt) on cable tray as required. | 75.00 | Mtr. |  | 20.00 | 1500.00 | 90.00 | 6750.00 | 45.00 | 3375.00 | 36.00 | 2700.00 | 37.00 | 2775.00 | 25.00 | 1875.00 | 97.00 | 7275.00 | 50.00 | 3750.00 | 1.05 | 78.75 | 50.00 | 3750.00 | 52.00 | 3900.00 | 78.75 | Ascent Electrification Engineers
13.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required 50 mm dia | 80.00 | Mtr. |  | 430.00 | 34400.00 | 540.00 | 43200.00 | 455.00 | 36400.00 | 409.00 | 32720.00 | 526.00 | 42080.00 | 400.00 | 32000.00 | 427.00 | 34160.00 | 417.00 | 33360.00 | 525.88 | 42070.40 | 506.00 | 40480.00 | 360.00 | 28800.00 | 28800.00 | TRINITY ENGINEERS
14.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required 100 mm dia | 90.00 | Mtr. |  | 826.00 | 74340.00 | 900.00 | 81000.00 | 1255.00 | 112950.00 | 848.00 | 76320.00 | 729.00 | 65610.00 | 750.00 | 67500.00 | 732.00 | 65880.00 | 866.00 | 77940.00 | 806.78 | 72610.20 | 653.00 | 58770.00 | 831.00 | 74790.00 | 58770.00 | INDIAN ELECTRIC CORPORATION
15.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc with charcoal/ coke and salt as required. | 6.00 | Each |  | 3125.00 | 18750.00 | 7000.00 | 42000.00 | 6565.00 | 39390.00 | 5298.00 | 31788.00 | 2479.00 | 14874.00 | 3800.00 | 22800.00 | 7320.00 | 43920.00 | 6750.00 | 40500.00 | 6001.00 | 36006.00 | 11000.00 | 66000.00 | 4180.00 | 25080.00 | 14874.00 | BR Power Control and Automation Services
16.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/submain wiring/ cable as required. | 4100.00 | Mtr. |  | 8.00 | 32800.00 | 23.00 | 94300.00 | 28.00 | 114800.00 | 22.00 | 90200.00 | 18.00 | 73800.00 | 30.00 | 123000.00 | 18.00 | 73800.00 | 15.00 | 61500.00 | 23.04 | 94464.00 | 22.50 | 92250.00 | 9.00 | 36900.00 | 32800.00 | ABHISHEK ASSOCIATES
17.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3½ X 150 sq. mm (50mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 6.00 | Each |  | 204.00 | 1224.00 | 800.00 | 4800.00 | 450.00 | 2700.00 | 471.00 | 2826.00 | 496.00 | 2976.00 | 300.00 | 1800.00 | 305.00 | 1830.00 | 1498.00 | 8988.00 | 676.80 | 4060.80 | 1250.00 | 7500.00 | 300.00 | 1800.00 | 1224.00 | ABHISHEK ASSOCIATES
18.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3½ X 70 sq. mm (35mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Each |  | 146.00 | 292.00 | 600.00 | 1200.00 | 450.00 | 900.00 | 389.00 | 778.00 | 415.00 | 830.00 | 275.00 | 550.00 | 305.00 | 610.00 | 853.00 | 1706.00 | 460.90 | 921.80 | 500.00 | 1000.00 | 174.00 | 348.00 | 292.00 | ABHISHEK ASSOCIATES
19.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3½ X 50 sq. mm (35mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 5.00 | Each |  | 121.00 | 605.00 | 400.00 | 2000.00 | 400.00 | 2000.00 | 324.00 | 1620.00 | 372.00 | 1860.00 | 200.00 | 1000.00 | 366.00 | 1830.00 | 766.00 | 3830.00 | 393.60 | 1968.00 | 350.00 | 1750.00 | 148.00 | 740.00 | 605.00 | ABHISHEK ASSOCIATES
20.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3½ X 35 sq. mm (32mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Each |  | 99.00 | 198.00 | 350.00 | 700.00 | 400.00 | 800.00 | 265.00 | 530.00 | 345.00 | 690.00 | 200.00 | 400.00 | 366.00 | 732.00 | 573.00 | 1146.00 | 345.60 | 691.20 | 300.00 | 600.00 | 110.00 | 220.00 | 198.00 | ABHISHEK ASSOCIATES
21.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4 X 25 sq. mm (28mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 4.00 | Each |  | 83.00 | 332.00 | 350.00 | 1400.00 | 400.00 | 1600.00 | 259.00 | 1036.00 | 329.00 | 1316.00 | 200.00 | 800.00 | 366.00 | 1464.00 | 541.00 | 2164.00 | 307.20 | 1228.80 | 250.00 | 1000.00 | 104.00 | 416.00 | 332.00 | ABHISHEK ASSOCIATES
22.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4 X 10 sq. mm (25mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 13.00 | Each |  | 57.00 | 741.00 | 240.00 | 3120.00 | 350.00 | 4550.00 | 235.00 | 3055.00 | 284.00 | 3692.00 | 100.00 | 1300.00 | 305.00 | 3965.00 | 431.00 | 5603.00 | 240.00 | 3120.00 | 250.00 | 3250.00 | 55.00 | 715.00 | 715.00 | TRINITY ENGINEERS
23.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 2 X 16 sq. mm (22mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 1.00 | Each |  | 33.00 | 33.00 | 180.00 | 180.00 | 350.00 | 350.00 | 206.00 | 206.00 | 247.00 | 247.00 | 100.00 | 100.00 | 305.00 | 305.00 | 326.00 | 326.00 | 201.60 | 201.60 | 200.00 | 200.00 | 53.00 | 53.00 | 33.00 | ABHISHEK ASSOCIATES
24.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 2 X 10 sq. mm (19mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 6.00 | Each |  | 33.00 | 198.00 | 180.00 | 1080.00 | 300.00 | 1800.00 | 194.00 | 1164.00 | 1198.00 | 7188.00 | 100.00 | 600.00 | 366.00 | 2196.00 | 286.00 | 1716.00 | 144.00 | 864.00 | 150.00 | 900.00 | 40.00 | 240.00 | 198.00 | ABHISHEK ASSOCIATES
25.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 2 X 6 sq. mm (19mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Each |  | 33.00 | 66.00 | 180.00 | 360.00 | 300.00 | 600.00 | 147.00 | 294.00 | 200.00 | 400.00 | 100.00 | 200.00 | 366.00 | 732.00 | 643.00 | 1286.00 | 144.00 | 288.00 | 150.00 | 300.00 | 40.00 | 80.00 | 66.00 | ABHISHEK ASSOCIATES
26.00 | Supply, Installation, Testing & Commissioning of outdoor type weather proof compartmentalised floor mounted cubicle Feeder Piller board having Min.Size:1300mm(L) X 1500mm(H) X 450mm (D) made from 2mm thick CRCA sheet with double door and inbuilt locking arrangement, dust & vermin proof, duly phosphatized followed with powder coat painting, IP - 54, having MS channel based frame made of size 75 x 75 x 6 mm of required length, duly grouted in available PCC foundation suitable for operation on 3 Phase, 415V , 50 Hz A.C. supply including provision of 3mm Gland plate etc. comprising of following incoming and outgoing switch gears, terminal blocks for incoming & outgoing cables, all connections (incoming & outgoing to cable alley) with suitable rated solid copper conductor cable / Al. bus bar followed with fixing of 02 nos. 20 x 3mm copper strip earthing passing through the panel for connecting 02 nos. earth bus, accessories etc. complete all as required and as specified: Incomer 02 No. 125 Amp, 4P 36 KA MCCB of Thermal magnetic trip unit (TMD) Ics = 100 % Icu along with spreader terminals and extended rotary handle. 01 No. 125 Amp, 4P on load change over switch. Suitable size aluminium bus bar (Minimum 150 Amp). CT 125/5, 15VA, Accu Cl - 1.0 0 to 150 Amp Digital Single Phase Ammeter, Accu Cl - 1.0 Ammeter selector switch. 0-500V Digital Single Phase Voltmeter, Accu Cl - 1.0 Voltmeter selector switch. 3P, 415V, 40kA, TYPE 2 SPD. R,Y,B - Phase Indication lamp LED Type. Control MCB 6A SP 10KA C_Curve. Neutral link. Outgoing 01 No. 63 Amp, 4P, 30 KA MCCB with power terminal TPN 4 way. 03 Nos. 40 Amp, 4P, 30 KA MCCB with power terminal KUT 10. 03 Nos. 40 Amp, DP, 300 mA RCCB with power terminal KUT 10. 10 Nos. 16 Amp, DP, 10 KA MCB with power terminal KUT 6. Provision of Digital / Manual Timer Switch. | 2.00 | Job |  | 157530.00 | 315060.00 | 135000.00 | 270000.00 | 169763.00 | 339526.00 | 119153.00 | 238306.00 | 150568.00 | 301136.00 | 100000.00 | 200000.00 | 210000.00 | 420000.00 | 190600.00 | 381200.00 | 139776.00 | 279552.00 | 155500.00 | 311000.00 | 130065.00 | 260130.00 | 200000.00 | jaydeep agency corporation
27.00 | Supply, Installation, Testing & Commissioning of outdoor type weather proof compartmentalised floor mounted cubicle Feeder Pillar board having Min.Size:1300mm(L) X 1500mm(H) X 450mm (D) made from 2mm thick CRCA sheet with double door and inbuilt locking arrangement, dust & vermin proof, duly phosphatized followed with powder coat painting, IP - 54, having MS channel based frame made of size 75 x 75 x 6 mm of required length, duly grouted in available PCC foundation suitable for operation on 3 Phase, 415V , 50 Hz A.C. supply including provision of 3mm Gland plate etc. comprising of following incoming and outgoing switch gears, terminal blocks for incoming & outgoing cables, all connections (incoming & outgoing to cable alley) with suitable rated solid copper conductor cable / Al. bus bar followed with fixing of 02 nos. 20 x 3mm copper strip earthing passing through the panel for connecting 02 nos. earth bus, accessories etc. complete all as required and as specified: Incomer 02 Nos. 125 Amp, 4P 36 KA MCCB of Thermal magnetic trip unit (TMD) Ics = 100 % Icu along with spreader terminals and extended rotary handle. 01 No. 125 Amp, 4P on load change over switch. Suitable size aluminium bus bar (Minimum 150 Amp). CT 125/5, 15VA, Accu Cl - 1.0 0 to 150 Amp Digital Single Phase Ammeter, Accu Cl - 1.0 Ammeter selector switch. 0-500V Digital Single Phase Voltmeter, Accu Cl - 1.0 Voltmeter selector switch. 3P, 415V, 40kA, TYPE 2 SPD. R,Y,B - Phase Indication lamp LED Type. Control MCB 6A SP 10KA C_Curve. Neutral link. Outgoing 02 Nos. 63 Amp, 4P, 30 KA MCCB with power terminal TPN 4 way. 04 Nos. 40 Amp, 4P, 30 KA MCCB with power terminal KUT 10. 08 Nos. 16 Amp, DP, 10 KA MCB with power terminal KUT 6. | 1.00 | Job |  | 163630.00 | 163630.00 | 125000.00 | 125000.00 | 222323.00 | 222323.00 | 117975.00 | 117975.00 | 131957.00 | 131957.00 | 100000.00 | 100000.00 | 230000.00 | 230000.00 | 203700.00 | 203700.00 | 150624.00 | 150624.00 | 155500.00 | 155500.00 | 130065.00 | 130065.00 | 100000.00 | jaydeep agency corporation
28.00 | Providing and laying in position cement concrete 1:3:6 (1 cement : 2 coarse sand : 6 graded stone aggregate 40 mm nominal size) for foundation of feeder pillar complete all as required & as specified. | 2.00 | Cum |  | 1000.00 | 2000.00 | 6000.00 | 12000.00 | 4500.00 | 9000.00 | 1413.00 | 2826.00 | 5578.00 | 11156.00 | 2800.00 | 5600.00 | 4880.00 | 9760.00 | 2090.00 | 4180.00 | 4320.00 | 8640.00 | 6500.00 | 13000.00 | 6540.00 | 13080.00 | 2000.00 | ABHISHEK ASSOCIATES
29.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 meter in width, and lift upto 1.5 meter, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 meter. | 5.00 | Cum |  | 1500.00 | 7500.00 | 1100.00 | 5500.00 | 1225.00 | 6125.00 | 1177.00 | 5885.00 | 1859.00 | 9295.00 | 550.00 | 2750.00 | 610.00 | 3050.00 | 998.00 | 4990.00 | 662.40 | 3312.00 | 500.00 | 2500.00 | 1435.00 | 7175.00 | 2500.00 | INDIAN ELECTRIC CORPORATION
30.00 | Supplying and laying of 63 mm dia (OD-63 mm & ID-51 mm nominal) size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc..direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 450.00 | Mtr. |  | 226.00 | 101700.00 | 175.00 | 78750.00 | 156.00 | 70200.00 | 139.00 | 62550.00 | 345.00 | 155250.00 | 200.00 | 90000.00 | 146.00 | 65700.00 | 101.00 | 45450.00 | 91.20 | 41040.00 | 165.00 | 74250.00 | 70.00 | 31500.00 | 31500.00 | TRINITY ENGINEERS
31.00 | Supplying and laying of 120 mm dia (OD-120 mm & ID-103 mm nominal) size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc..direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 1350.00 | Mtr. |  | 279.00 | 376650.00 | 280.00 | 378000.00 | 229.00 | 309150.00 | 199.00 | 268650.00 | 360.00 | 486000.00 | 250.00 | 337500.00 | 183.00 | 247050.00 | 213.00 | 287550.00 | 201.60 | 272160.00 | 270.00 | 364500.00 | 156.00 | 210600.00 | 210600.00 | TRINITY ENGINEERS
32.00 | Supply and fixing of 63 Amp, 4 pole, 415 Volt manual change over switch in the existing UPS panel for National flag installation as per site requirement and as directed by E.I/C. | 1.00 | Each |  | 3421.00 | 3421.00 | 18000.00 | 18000.00 | 4533.00 | 4533.00 | 2586.00 | 2586.00 | 4308.00 | 4308.00 | 2500.00 | 2500.00 | 4880.00 | 4880.00 | 5865.00 | 5865.00 | 3500.00 | 3500.00 | 5006.00 | 5006.00 | 3151.00 | 3151.00 | 2500.00 | jaydeep agency corporation
| Total in Figures |  |  |  |  | 1948805.00 |  | 2139635.00 |  | 2213952.00 |  | 1797255.00 |  | 2299985.00 |  | 2211625.00 |  | 2304669.00 |  | 2056755.00 |  | 1884345.05 |  | 2097576.00 |  | 1821123.00
Lowest Amount Quoted BY: Taral Electricals(1797255.00)

## BOQ Summary
BOQ Summary Details Tender Title: Misc unforeseen Electrical works. SH- Replacement of faulty LT Power Cable for T-2 Car Park area and Main Approach road of T 1 at SVPI Airport, Ahmedabad Tender ID: 2020_AAI_41155_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Taral Electricals | 1797255.00 | L1
| 2 | TRINITY ENGINEERS | 1821123.00 | L2
| 3 | Ascent Electrification Engineers | 1884345.05 | L3
| 4 | ABHISHEK ASSOCIATES | 1948805.00 | L4
| 5 | Yash Energy Pvt. Ltd | 2056755.00 | L5
| 6 | INDIAN ELECTRIC CORPORATION | 2097576.00 | L6
| 7 | Manish Electricals | 2139635.00 | L7
| 8 | jaydeep agency corporation | 2211625.00 | L8
| 9 | Techno Electricals | 2213952.00 | L9
| 10 | BR Power Control and Automation Services | 2299985.00 | L10
| 11 | RVD INFRA SOLUTION PVT.LTD. | 2304669.00 | L11