## BoQ1
Government eProcurement System Created By: KASI R Created Date/Time: 10-Feb-2020 12:25 PM Tender Title: Improvement of Air Conditioning System, Water Cooler at terminal and ancillary building at Coimbatore International Airport Tender ID: 2020_AAI_41324_1
Tender Inviting Authority: Asst.Gen.Manager(E-E), AAI, Coimbatore International Airport.
Name of Work: Improvement of Air Conditioning System, Water Cooler at terminal and ancillary building at Coimbatore International Airport
Contract No: 2020_AAI_41324 _1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | C P MONCHESTER ELECTRICALS |  | VOLKS ENERGIE PVT LTD |  | HEAT CRAFT ENGINEERS PVT LTD |  | ABS AIRCON ENGINEERS PRIVATE LIMITED
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Erection, testing, balancing and commissioning of 16.5-16.7 TR capacity ductable Hi ceiling mounting type split air conditioning units, suitable to operate with 440V, 50 Hz A/C supply with all the accessories (ceiling suspended or floor mounted) as specified and required and incorporating the following. a) 16.5-16.7 TR capacity package unit with Hermitic scroll compressors including all accessories. b) Air-cooled condenser with suitable size fans . c) Drive motors of suitable capacity air-cooled. d) Micro processor control panel (adoptable to BMS system incopporating all features) with automatic capacity control unit to regulate the capacity, safety controls, control wiring, motor starter etc., e) Thermostat expansion valve. f) Integral mounting frame for all the equipments. g) Refrigerant piping and valves. h) First charging of refrigerant (R-410 or R -32) and refrigerant oil. i) Vibration Isolation pads. j)Inter connected cabling & piping between indoor units and outdoor units up to adistance of 5 mtrs. k) Drain piping (Hard PVC) to the nearest drain point. l) prewired starters for the Ac plant as per the manufactureres design | 3.00 | Job |  | 300000.00 | 900000.00 | 315000.00 | 945000.00 | 273029.00 | 819087.00 | 281938.00 | 845814.00 | 819087.00 | HEAT CRAFT ENGINEERS PVT LTD
2.00 | Design, Supply, Erection, testing, balancing and commissioning of minimum 11 TR (Nominal ) capacity ductable Hi ceiling mounting type split air conditioning units, suitable to operate with 440V, 50 Hz A/C supply with all the accessories (ceiling suspended or floor mounted) as specified and required and incorporating the following. a) 11 TR (Nominal) capacity package unit with Hermitic scroll compressors of minimum 5.5 TR each including all accessories. b) Air-cooled condenser with suitable size fans . c) Drive motors of suitable capacity air-cooled. d) Micro processor control panel (adoptable to BMS system incopporating all features) with automatic capacity control unit to regulate the capacity, safety controls, control wiring, motor starter etc., e) Thermostat expansion valve. f) Integral mounting frame for all the equipments. g) Refrigerant piping and valves. h) First charging of refrigerant (R-410 or R -32) and refrigerant oil. i) Vibration Isolation pads. j) Inter connected cabling & piping between indoor units and outdoor units up to adistance of 5 mtrs. k) Drain piping (Hard PVC) to the nearest drain point. l) prewired starters for the Ac plant as per the manufactureres design | 2.00 | Job |  | 200000.00 | 400000.00 | 225000.00 | 450000.00 | 189083.00 | 378166.00 | 203262.00 | 406524.00 | 378166.00 | HEAT CRAFT ENGINEERS PVT LTD
3.00 | Supply, Fabrication, handle and errect GSS ducting of convertional rectangular ducting as per drawing complete with all fittings, such tee, bonds, special off chutes turning vanes, splitter damper inspection doors, transformation pieces etc., as required as per IS 655 including suspension and supporting arrangement for ducts complete as required. 0.63mm (24G) | 15.00 | Sqmm |  | 1050.00 | 15750.00 | 1800.00 | 27000.00 | 1300.00 | 19500.00 | 855.00 | 12825.00 | 12825.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
4.00 | Supply, Fabrication, handle and errect GSS ducting of convertional rectangular ducting as per drawing complete with all fittings, such tee, bonds, special off chutes turning vanes, splitter damper inspection doors, transformation pieces etc., as required as per IS 655 including suspension and supporting arrangement for ducts complete as required. 0.80mm (22G) | 15.00 | Sqmm |  | 950.00 | 14250.00 | 2000.00 | 30000.00 | 1425.00 | 21375.00 | 1007.00 | 15105.00 | 14250.00 | C P MONCHESTER ELECTRICALS
5.00 | Supply and fixing refrigerant pipe line For Hard drawn copper pipe set for 11 TR & 16.7 TR Ductable AC including bracing and painting as per standard colours etc as required. | 150.00 | Mtr |  | 950.00 | 142500.00 | 900.00 | 135000.00 | 1850.00 | 277500.00 | 2909.00 | 436350.00 | 135000.00 | VOLKS ENERGIE PVT LTD
6.00 | Supply & laying of Inter Connecting power cable/ Communication cable including drain pipe with proper insulation for 11 TR & 16.7 TR Ductable AC as per the OEM recommendations and as per site conditions etc. as required. | 150.00 | Mtr |  | 120.00 | 18000.00 | 250.00 | 37500.00 | 425.00 | 63750.00 | 1659.00 | 248850.00 | 18000.00 | C P MONCHESTER ELECTRICALS
7.00 | Supplying & fixing of powder coated extruded aluminium Supply Air Grills with aluminium volume control dampers as per specifications. | 10.00 | sqm |  | 4500.00 | 45000.00 | 6000.00 | 60000.00 | 9470.00 | 94700.00 | 9243.00 | 92430.00 | 45000.00 | C P MONCHESTER ELECTRICALS
8.00 | Supplying & fixing of powder coated extruded aluminium Return Air Grills with louvers but without volume control dampers complete as required. | 10.00 | sqm |  | 4500.00 | 45000.00 | 4000.00 | 40000.00 | 8210.00 | 82100.00 | 9103.00 | 91030.00 | 40000.00 | VOLKS ENERGIE PVT LTD
9.00 | Supply and Installation of MS Collar damper for supply air duct | 8.00 | job |  | 3000.00 | 24000.00 | 5000.00 | 40000.00 | 1975.00 | 15800.00 | 4267.00 | 34136.00 | 15800.00 | HEAT CRAFT ENGINEERS PVT LTD
10.00 | Acoustic Insulation of ducting 10 mm thick open cell Nitrile rubber internal surface of the duct, all joints to be sealed with Aluminium self addhessive tape. | 10.00 | sqm |  | 300.00 | 3000.00 | 500.00 | 5000.00 | 1105.00 | 11050.00 | 1016.00 | 10160.00 | 3000.00 | C P MONCHESTER ELECTRICALS
11.00 | Thermal Insulation of ducting 9 mm thick closed cell Nitrile rubber external surface of the duct, all joints to be sealed with Aluminium self addhessive tape. | 15.00 | sqm |  | 450.00 | 6750.00 | 523.00 | 7845.00 | 665.00 | 9975.00 | 509.00 | 7635.00 | 6750.00 | C P MONCHESTER ELECTRICALS
12.00 | Supply and installation of FLEXIBLE CANVASS CONNECTION & FILTER Canvass connection for Ductable air conditioner complete as required. | 4.00 | each |  | 3000.00 | 12000.00 | 2500.00 | 10000.00 | 3050.00 | 12200.00 | 3951.00 | 15804.00 | 10000.00 | VOLKS ENERGIE PVT LTD
13.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. (a) Upto 35 sq. mm (clamped with 1mm thick saddle) | 35.00 | Mtr |  | 60.00 | 2100.00 | 150.00 | 5250.00 | 56.00 | 1960.00 | 94.00 | 3290.00 | 1960.00 | HEAT CRAFT ENGINEERS PVT LTD
14.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. (b) Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 135.00 | Mtr |  | 90.00 | 12150.00 | 200.00 | 27000.00 | 95.00 | 12825.00 | 192.00 | 25920.00 | 12150.00 | C P MONCHESTER ELECTRICALS
15.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing tray as required. (a) Upto 35 Sq.mm | 50.00 | Mtr |  | 60.00 | 3000.00 | 80.00 | 4000.00 | 54.00 | 2700.00 | 98.00 | 4900.00 | 2700.00 | HEAT CRAFT ENGINEERS PVT LTD
16.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing tray as required. (b) Above 35 sq. mm and upto 95 sq. mm | 335.00 | Mtr |  | 60.00 | 20100.00 | 120.00 | 40200.00 | 72.00 | 24120.00 | 168.00 | 56280.00 | 20100.00 | C P MONCHESTER ELECTRICALS
17.00 | Supply and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/XLPE aluminium conductor cable of 1.1 KV grade as required. 3 1/2 X 25 Sq.mm | 4.00 | set |  | 600.00 | 2400.00 | 450.00 | 1800.00 | 920.00 | 3680.00 | 1129.00 | 4516.00 | 1800.00 | VOLKS ENERGIE PVT LTD
18.00 | Supply and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/XLPE aluminium conductor cable of 1.1 KV grade as required. 3 1/2 X 50 Sq.mm | 6.00 | set |  | 900.00 | 5400.00 | 500.00 | 3000.00 | 1150.00 | 6900.00 | 2114.00 | 12684.00 | 3000.00 | VOLKS ENERGIE PVT LTD
19.00 | Supply and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/XLPE aluminium conductor cable of 1.1 KV grade as required. 3 1/2 X 95 Sq.mm | 4.00 | set |  | 1200.00 | 4800.00 | 800.00 | 3200.00 | 1897.00 | 7588.00 | 2641.00 | 10564.00 | 3200.00 | VOLKS ENERGIE PVT LTD
20.00 | Supply of SMDB of 8 way withoutgoing capacity of 250A with Ics withstand capacity of 36ka & IP-43 protection ready to use with suitable metering and cabling extenstions i/c other accessories (MCCB incomer suitable DU250 & DU250C MCCB). Model: L&T DA62D1084CZZ0 or equalent. | 2.00 | No's |  | 60000.00 | 120000.00 | 60000.00 | 120000.00 | 118160.00 | 236320.00 | 41077.00 | 82154.00 | 82154.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
21.00 | Fixing of 8 way SMDB IP-43 sheet steel MCCB distribution board 415volts on surface/recess complete as reuired. | 2.00 | No's |  | 2000.00 | 4000.00 | 2000.00 | 4000.00 | 2250.00 | 4500.00 | 2104.00 | 4208.00 | 4000.00 | C P MONCHESTER ELECTRICALS, VOLKS ENERGIE PVT LTD
22.00 | Supply of following rate MCCB suitable to operate 415V 50Hz (for SMDB) supply complete etc. as required. TP, 250A (Model: L&T DU250 , Icu=36 kA) | 2.00 | No's |  | 4000.00 | 8000.00 | 9000.00 | 18000.00 | 11825.00 | 23650.00 | 16743.00 | 33486.00 | 8000.00 | C P MONCHESTER ELECTRICALS
23.00 | Supply of following rate MCB suitable to operate 415V 50Hz supply complete etc. as required "C" TP 80A, 15kA | 8.00 | No's |  | 2500.00 | 20000.00 | 4500.00 | 36000.00 | 5023.00 | 40184.00 | 5294.00 | 42352.00 | 20000.00 | C P MONCHESTER ELECTRICALS
24.00 | Supply of following rate MCB suitable to operate 415V 50Hz supply complete etc. as required "C" TP 100A, 15kA | 8.00 | No's |  | 3500.00 | 28000.00 | 4500.00 | 36000.00 | 5353.00 | 42824.00 | 7977.00 | 63816.00 | 28000.00 | C P MONCHESTER ELECTRICALS
25.00 | Fixing of (250 A) rating 415 V, MCCB in the existing SMDB complete with connections, testing,comissioning etc. as required./ Three Ploe | 2.00 | No's |  | 250.00 | 500.00 | 10000.00 | 20000.00 | 1500.00 | 3000.00 | 210.00 | 420.00 | 420.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
26.00 | Fixing of (100/80 A) rating 415 V, miniature circuit Breaker in the existing SMDB DB complete with connections, testing,comissioning etc. as required.Three Pole | 16.00 | No's |  | 250.00 | 4000.00 | 4000.00 | 64000.00 | 280.00 | 4480.00 | 210.00 | 3360.00 | 3360.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
27.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required | 150.00 | Mtr |  | 35.00 | 5250.00 | 28.00 | 4200.00 | 40.00 | 6000.00 | 67.00 | 10050.00 | 4200.00 | VOLKS ENERGIE PVT LTD
| Total in Figures |  |  |  |  | 1865950.00 |  | 2173995.00 |  | 2225934.00 |  | 2574663.00
Lowest Amount Quoted BY: C P MONCHESTER ELECTRICALS(1865950.00)

## BOQ Summary
BOQ Summary Details Tender Title: Improvement of Air Conditioning System, Water Cooler at terminal and ancillary building at Coimbatore International Airport Tender ID: 2020_AAI_41324_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | C P MONCHESTER ELECTRICALS | 1865950.00 | L1
| 2 | VOLKS ENERGIE PVT LTD | 2173995.00 | L2
| 3 | HEAT CRAFT ENGINEERS PVT LTD | 2225934.00 | L3
| 4 | ABS AIRCON ENGINEERS PRIVATE LIMITED | 2574663.00 | L4