## BoQ1
Government eProcurement System Created By: Ganesh Yadav Created Date/Time: 17-Mar-2020 11:51 AM Tender Title: Air-conditioning work. Tender ID: 2020_AAI_42770_1
Tender Inviting Authority: AGM (E-E), Civil Airport, Gorakhpur.
Name of Work: Provision of Air-Conditioning of Terminal Building for RCS Operation at Kushinagar Airport.
Contract No: AAI/Kushi./Engg.-Elect./VRF/2019-20/
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Industrial Traders |  | Blue Star Limited |  | VOLKS ENERGIE PVT LTD |  | UNITY ENGINEERS |  | Sai Cooling Point Private Limited |  | Ingenious Industries |  | M/S COOLING CENTER |  | SAI H.V.A.C. SYSTEM |  | VOLGA AIR TECHNOLOGIES |  | S G TECHNOFAB PVT LTD |  | Shambhavi Enterprises
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, lifting,shifting,local transport,port clearance,insurance,installation, testing and commissioning, of VRV/VRF outdoor units (ODU) with R410A refrigerant complete with hermetic SCROLL Inverter compressor, anti corresive fin heat exchanger, refrigerant shut off valves,safety devices, inverter controller, multi step function to meet load fluctuation, axial flow quiet operation condenser fans, MS support stand suitable for ODU with 2 coats of synthetic primer and 1 coat of enamel paint , starter panel, microprocessor based control panel, modular type construction, safety devices, controls, fault alarm indications, memory storage, hydrophilic coated condenser coil with copper tube and copper header, condenser guard, fan guard, CRC coated outer casing, vibration isolators, compressor jacket; as per the specification The VRV sytems should have both heating & cooling modes. The COP at AHRI conditions shall not be less than 3.1 & IEER not less than 6.5. The ODU must deliver COP of minimum 4.7 at 50% load. Contractor need to get the COP tested at NABL/AHRI Certified Laboratory. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50 Deg C Ambient temperatures without tripping. The capacity shall be as indicated below. MAKE --- LG / Mitsuibishi Electric / Voltas/Equivalent AAI approved make
1.01 | Terminal Building for Departure:- 80 HP with All inverter compressor (20 HP 4 nos only or any other combination totalling to 80HP as suggested by OEM ) | 1.00 | No | 2000000.00 | 1500000.00 | 1500000.00 | 1168686.00 | 1168686.00 | 1100000.00 | 1100000.00 | 1254600.00 | 1254600.00 | 1142643.00 | 1142643.00 | 1265040.00 | 1265040.00 | 956400.00 | 956400.00 | 1597330.00 | 1597330.00 | 1117800.00 | 1117800.00 | 913469.00 | 913469.00 | 1683795.00 | 1683795.00 | 913469.00 | S G TECHNOFAB PVT LTD
1.02 | Guest House at Arrival:- 20 HP with All inverter compressor | 1.00 | No | 25000.00 | 436000.00 | 436000.00 | 347085.00 | 347085.00 | 350000.00 | 350000.00 | 330300.00 | 330300.00 | 285661.00 | 285661.00 | 337050.00 | 337050.00 | 239100.00 | 239100.00 | 420350.00 | 420350.00 | 287400.00 | 287400.00 | 228367.00 | 228367.00 | 430995.00 | 430995.00 | 228367.00 | S G TECHNOFAB PVT LTD
1.03 | Terminal Building for Departure - For Treated Fresh Air:- 22 HP with All inverter compressor | 1.00 | No | 550000.00 | 812000.00 | 812000.00 | 349992.00 | 349992.00 | 370000.00 | 370000.00 | 360000.00 | 360000.00 | 349277.00 | 349277.00 | 382690.00 | 382690.00 | 247100.00 | 247100.00 | 455380.00 | 455380.00 | 298680.00 | 298680.00 | 234730.00 | 234730.00 | 479701.00 | 479701.00 | 234730.00 | S G TECHNOFAB PVT LTD
2.00 | VRV / VRF INDOOR UNIT:- Supply, installation and commissioning of 4-way cassette type direct expansion indoor units with individual blade control for all the four directions including blower, TEFC blower motor, suitable for operation on 240 ± 10% volts, 1 phase, 50 Hz A.C. supply, copper tube aluminium finned direct expansion cooling coil, pre filters, electronic expansion valve with cordless remote and control wiring, drain connections with anti-vibration mountings, Fresh Air connection etc., as required and as per schedule of equipment and specifications. Cooling Capacity MAKE --- LG / Mitsuibishi Electric / Equivalent AAI approved make
2.01 | 1.0 TR Nominal Capacity | 10.00 | No | 25500.00 | 34500.00 | 345000.00 | 26017.00 | 260170.00 | 34000.00 | 340000.00 | 19500.00 | 195000.00 | 26370.00 | 263700.00 | 31080.00 | 310800.00 | 30500.00 | 305000.00 | 34613.00 | 346130.00 | 32175.00 | 321750.00 | 29700.00 | 297000.00 | 34395.00 | 343950.00 | 195000.00 | UNITY ENGINEERS
2.02 | 1.28 TR Nominal Capacity | 9.00 | No | 28000.00 | 34500.00 | 310500.00 | 26136.00 | 235224.00 | 35000.00 | 315000.00 | 21500.00 | 193500.00 | 28044.00 | 252396.00 | 33180.00 | 298620.00 | 32500.00 | 292500.00 | 35568.00 | 320112.00 | 32994.00 | 296946.00 | 30039.00 | 270351.00 | 35595.00 | 320355.00 | 193500.00 | UNITY ENGINEERS
2.03 | 1.57 TR Nominal Capacity | 6.00 | No | 29500.00 | 34500.00 | 207000.00 | 26712.00 | 160272.00 | 37500.00 | 225000.00 | 22000.00 | 132000.00 | 28812.00 | 172872.00 | 34140.00 | 204840.00 | 33500.00 | 201000.00 | 37242.00 | 223452.00 | 33813.00 | 202878.00 | 30378.00 | 182268.00 | 37990.00 | 227940.00 | 132000.00 | UNITY ENGINEERS
2.04 | 2.0TR Nominal Capacity | 18.00 | No | 51175.00 | 34500.00 | 621000.00 | 26831.00 | 482958.00 | 39500.00 | 711000.00 | 22250.00 | 400500.00 | 29500.00 | 531000.00 | 34980.00 | 629640.00 | 35500.00 | 639000.00 | 40358.00 | 726444.00 | 34515.00 | 621270.00 | 30717.00 | 552906.00 | 38990.00 | 701820.00 | 400500.00 | UNITY ENGINEERS
2.05 | 4TR Nominal Capacity | 6.00 | No | 54625.00 | 37000.00 | 222000.00 | 28576.00 | 171456.00 | 42000.00 | 252000.00 | 31700.00 | 190200.00 | 33660.00 | 201960.00 | 40200.00 | 241200.00 | 39500.00 | 237000.00 | 43495.00 | 260970.00 | 38025.00 | 228150.00 | 32412.00 | 194472.00 | 41395.00 | 248370.00 | 171456.00 | Blue Star Limited
3.00 | VRV / VRF PIPING & ELECTRICAL WORK:- Supply & installation of 18G, hard drawn copper Refrigerant piping, duly insulated with closed cell elastomeric nitrile rubber insulation, class-o, covered with fiber glass cloth and two layers of shield coating, complete with elbows, T joints, sleeves etc., with GSS slotted rail supporting arrangement and GI clamp for individual pipes.
3.01 | 54.1 mm OD (Insulation = 19mm thick) | 1.00 | Mtr. | 2670.00 | 2320.00 | 2320.00 | 2000.00 | 2000.00 | 1300.00 | 1300.00 | 2350.00 | 2350.00 | 1059.00 | 1059.00 | 1812.00 | 1812.00 | 2500.00 | 2500.00 | 1550.00 | 1550.00 | 1500.00 | 1500.00 | 1906.00 | 1906.00 | 1390.00 | 1390.00 | 1059.00 | Sai Cooling Point Private Limited
3.02 | 41.3 mm OD (Insulation = 19mm thick) | 35.00 | Mtr. | 2240.00 | 1850.00 | 64750.00 | 1695.00 | 59325.00 | 1200.00 | 42000.00 | 2120.00 | 74200.00 | 897.00 | 31395.00 | 1573.00 | 55055.00 | 1480.00 | 51800.00 | 1425.00 | 49875.00 | 1450.00 | 50750.00 | 1350.00 | 47250.00 | 1320.00 | 46200.00 | 31395.00 | Sai Cooling Point Private Limited
3.03 | 34.9 mm OD (Insulation = 19mm thick) | 20.00 | Mtr. | 2120.00 | 1600.00 | 32000.00 | 1458.00 | 29160.00 | 1000.00 | 20000.00 | 1410.00 | 28200.00 | 781.00 | 15620.00 | 1200.00 | 24000.00 | 1380.00 | 27600.00 | 1305.00 | 26100.00 | 1250.00 | 25000.00 | 1020.00 | 20400.00 | 1210.00 | 24200.00 | 15620.00 | Sai Cooling Point Private Limited
3.04 | 28.6 mm OD (Insulation = 19mm thick) | 50.00 | Mtr. | 1870.00 | 1450.00 | 72500.00 | 1212.00 | 60600.00 | 900.00 | 45000.00 | 940.00 | 47000.00 | 663.00 | 33150.00 | 999.00 | 49950.00 | 990.00 | 49500.00 | 1102.00 | 55100.00 | 1050.00 | 52500.00 | 748.00 | 37400.00 | 1100.00 | 55000.00 | 33150.00 | Sai Cooling Point Private Limited
3.05 | 22.2 mm OD (Insulation = 13mm thick) | 50.00 | Mtr. | 1450.00 | 1044.00 | 52200.00 | 983.00 | 49150.00 | 800.00 | 40000.00 | 705.00 | 35250.00 | 513.00 | 25650.00 | 900.00 | 45000.00 | 940.00 | 47000.00 | 1035.00 | 51750.00 | 632.00 | 31600.00 | 628.00 | 31400.00 | 950.00 | 47500.00 | 25650.00 | Sai Cooling Point Private Limited
3.06 | 19.1 mm OD (Insulation = 13mm thick) | 70.00 | Mtr. | 1270.00 | 925.00 | 64750.00 | 881.00 | 61670.00 | 700.00 | 49000.00 | 590.00 | 41300.00 | 481.00 | 33670.00 | 800.00 | 56000.00 | 890.00 | 62300.00 | 918.00 | 64260.00 | 455.00 | 31850.00 | 506.00 | 35420.00 | 870.00 | 60900.00 | 31850.00 | VOLGA AIR TECHNOLOGIES
3.07 | 15.9 mm OD (Insulation = 13mm thick) | 80.00 | Mtr. | 970.00 | 800.00 | 64000.00 | 754.00 | 60320.00 | 600.00 | 48000.00 | 530.00 | 42400.00 | 400.00 | 32000.00 | 700.00 | 56000.00 | 840.00 | 67200.00 | 765.00 | 61200.00 | 378.00 | 30240.00 | 438.00 | 35040.00 | 750.00 | 60000.00 | 30240.00 | VOLGA AIR TECHNOLOGIES
3.08 | 12.7 mm OD (Insulation = 13mm thick) | 80.00 | Mtr. | 860.00 | 550.00 | 44000.00 | 686.00 | 54880.00 | 500.00 | 40000.00 | 470.00 | 37600.00 | 266.00 | 21280.00 | 550.00 | 44000.00 | 790.00 | 63200.00 | 675.00 | 54000.00 | 315.00 | 25200.00 | 329.00 | 26320.00 | 625.00 | 50000.00 | 21280.00 | Sai Cooling Point Private Limited
3.09 | 9.5 mm OD (Insulation = 13mm thick) | 80.00 | Mtr. | 750.00 | 444.00 | 35520.00 | 636.00 | 50880.00 | 450.00 | 36000.00 | 410.00 | 32800.00 | 201.00 | 16080.00 | 450.00 | 36000.00 | 730.00 | 58400.00 | 625.00 | 50000.00 | 224.00 | 17920.00 | 281.00 | 22480.00 | 550.00 | 44000.00 | 16080.00 | Sai Cooling Point Private Limited
3.10 | 6.4 mm OD (Insulation = 13mm thick) | 80.00 | Mtr. | 700.00 | 345.00 | 27600.00 | 576.00 | 46080.00 | 300.00 | 24000.00 | 350.00 | 28000.00 | 140.00 | 11200.00 | 350.00 | 28000.00 | 680.00 | 54400.00 | 530.00 | 42400.00 | 156.00 | 12480.00 | 231.00 | 18480.00 | 310.00 | 24800.00 | 11200.00 | Sai Cooling Point Private Limited
4.00 | Supply, fixing and commissioning of imported refrigerant joint / Branch distibutors indoor to outdoor complete with nitrile rubber insulation, supporting etc. | 17.00 | Set | 6500.00 | 4060.00 | 69020.00 | 4856.00 | 82552.00 | 4000.00 | 68000.00 | 4120.00 | 70040.00 | 2150.00 | 36550.00 | 3220.00 | 54740.00 | 3500.00 | 59500.00 | 2800.00 | 47600.00 | 5640.00 | 95880.00 | 5835.00 | 99195.00 | 4800.00 | 81600.00 | 36550.00 | Sai Cooling Point Private Limited
5.00 | Supply, Installation & testing of PVC pipes for drain pipes with 9 mm thick insulation upto the shaft as per specifications and approved drawings from the each indoor unit to respective drain pointed as indicated in the layout drawing.
5.01 | 50 mm dia | 10.00 | Mtr. | 410.00 | 139.00 | 1390.00 | 424.00 | 4240.00 | 250.00 | 2500.00 | 260.00 | 2600.00 | 132.00 | 1320.00 | 240.00 | 2400.00 | 240.00 | 2400.00 | 485.00 | 4850.00 | 303.00 | 3030.00 | 191.00 | 1910.00 | 174.95 | 1749.50 | 1320.00 | Sai Cooling Point Private Limited
5.02 | 40 mm Dia | 30.00 | Mtr. | 320.00 | 116.00 | 3480.00 | 364.00 | 10920.00 | 200.00 | 6000.00 | 175.00 | 5250.00 | 110.00 | 3300.00 | 220.00 | 6600.00 | 215.00 | 6450.00 | 412.00 | 12360.00 | 125.00 | 3750.00 | 162.00 | 4860.00 | 151.00 | 4530.00 | 3300.00 | Sai Cooling Point Private Limited
5.03 | 32 mm Dia | 50.00 | Mtr. | 290.00 | 87.00 | 4350.00 | 339.00 | 16950.00 | 180.00 | 9000.00 | 140.00 | 7000.00 | 91.00 | 4550.00 | 215.00 | 10750.00 | 200.00 | 10000.00 | 343.00 | 17150.00 | 108.00 | 5400.00 | 110.00 | 5500.00 | 126.00 | 6300.00 | 4350.00 | Industrial Traders
5.04 | 25 mm Dia | 90.00 | Mtr. | 210.00 | 69.00 | 6210.00 | 280.00 | 25200.00 | 150.00 | 13500.00 | 120.00 | 10800.00 | 78.00 | 7020.00 | 210.00 | 18900.00 | 165.00 | 14850.00 | 220.00 | 19800.00 | 86.00 | 7740.00 | 99.00 | 8910.00 | 125.00 | 11250.00 | 6210.00 | Industrial Traders
6.00 | Supply & installation of 2 coreX 1.5 Sq.mm control cum transmission wiring interconnecting outdoor units to all indoor units wiring through PVC FRLS conduit . | 400.00 | Mtr. | 195.00 | 69.00 | 27600.00 | 161.00 | 64400.00 | 120.00 | 48000.00 | 105.00 | 42000.00 | 85.00 | 34000.00 | 180.00 | 72000.00 | 220.00 | 88000.00 | 103.00 | 41200.00 | 133.00 | 53200.00 | 104.00 | 41600.00 | 140.00 | 56000.00 | 27600.00 | Industrial Traders
7.00 | Electrical power & Control cabling complete with earthing .The isolator switch to the outdoor units . Power & control cable should be 1.1 KV grade Cu conductor, PVC armoured cables . Cable price should include cost of end termination also. Please note power shall be terminated through a suitable isolator near the outdoor unit by other agency.
7.01 | 4C x 25 sqmm - CU Armoured | 120.00 | Mtr. | 1200.00 | 850.00 | 102000.00 | 992.00 | 119040.00 | 750.00 | 90000.00 | 825.00 | 99000.00 | 978.00 | 117360.00 | 1200.00 | 144000.00 | 1100.00 | 132000.00 | 1412.00 | 169440.00 | 1047.00 | 125640.00 | 886.00 | 106320.00 | 895.00 | 107400.00 | 90000.00 | VOLKS ENERGIE PVT LTD
7.02 | 4C x 16 sqmm - CU Armoured | 100.00 | Mtr. | 950.00 | 580.00 | 58000.00 | 619.00 | 61900.00 | 600.00 | 60000.00 | 530.00 | 53000.00 | 596.00 | 59600.00 | 750.00 | 75000.00 | 650.00 | 65000.00 | 862.00 | 86200.00 | 688.00 | 68800.00 | 610.00 | 61000.00 | 535.00 | 53500.00 | 53000.00 | UNITY ENGINEERS
7.03 | 4C x 10 sqmm - CU Armoured | 25.00 | Mtr. | 750.00 | 348.00 | 8700.00 | 424.00 | 10600.00 | 400.00 | 10000.00 | 380.00 | 9500.00 | 413.00 | 10325.00 | 404.00 | 10100.00 | 450.00 | 11250.00 | 596.00 | 14900.00 | 504.00 | 12600.00 | 442.00 | 11050.00 | 370.00 | 9250.00 | 8700.00 | Industrial Traders
7.04 | 4C x 6 sqmm - CU Armoured | 20.00 | Mtr. | 600.00 | 232.00 | 4640.00 | 305.00 | 6100.00 | 300.00 | 6000.00 | 240.00 | 4800.00 | 257.00 | 5140.00 | 251.20 | 5024.00 | 350.00 | 7000.00 | 353.00 | 7060.00 | 338.00 | 6760.00 | 304.00 | 6080.00 | 234.00 | 4680.00 | 4640.00 | Industrial Traders
8.00 | Electrical power & Control cabling complete with earthing for indoor unit. Power & control cable should be 1.1 KV grade Cu conductor, PVC Flexible cables . Cable price should include cost of end termination also. Please note power shall be terminated through a suitable isolator near the Indoor unit by other agency.
8.01 | 3C x 6Sqmm - Cu Flexible cable | 40.00 | Mtr. | 370.00 | 128.00 | 5120.00 | 203.00 | 8120.00 | 180.00 | 7200.00 | 235.00 | 9400.00 | 182.00 | 7280.00 | 190.00 | 7600.00 | 240.00 | 9600.00 | 375.00 | 15000.00 | 261.00 | 10440.00 | 373.00 | 14920.00 | 255.00 | 10200.00 | 5120.00 | Industrial Traders
8.02 | 3C x 4Sqmm - Cu Flexible cable | 30.00 | Mtr. | 290.00 | 87.00 | 2610.00 | 153.00 | 4590.00 | 130.00 | 3900.00 | 205.00 | 6150.00 | 128.00 | 3840.00 | 120.00 | 3600.00 | 220.00 | 6600.00 | 219.00 | 6570.00 | 207.00 | 6210.00 | 319.00 | 9570.00 | 205.00 | 6150.00 | 2610.00 | Industrial Traders
8.03 | 3C x 2.5Sqmm - Cu Flexible cable | 30.00 | Mtr. | 210.00 | 58.00 | 1740.00 | 119.00 | 3570.00 | 90.00 | 2700.00 | 150.00 | 4500.00 | 87.00 | 2610.00 | 90.00 | 2700.00 | 180.00 | 5400.00 | 135.00 | 4050.00 | 151.00 | 4530.00 | 275.00 | 8250.00 | 162.00 | 4860.00 | 1740.00 | Industrial Traders
9.00 | Supply and fixing of following GI flats / wires including all necessary fixing accessories and effective connections with copper riveting / welding etc as approved
9.01 | 8 SWG GI wire | 200.00 | Mtr. | 95.00 | 11.50 | 2300.00 | 59.00 | 11800.00 | 20.00 | 4000.00 | 18.00 | 3600.00 | 28.00 | 5600.00 | 65.00 | 13000.00 | 30.00 | 6000.00 | 118.00 | 23600.00 | 125.00 | 25000.00 | 41.00 | 8200.00 | 139.00 | 27800.00 | 2300.00 | Industrial Traders
10.00 | SITC of circular/cabinet inline fan complete with motor, cabling between starter and fan etc.
10.01 | 500CFM with 10mm Static | 1.00 | No | 22400.00 | 5200.00 | 5200.00 | 9644.00 | 9644.00 | 17000.00 | 17000.00 | 9200.00 | 9200.00 | 8400.00 | 8400.00 | 12000.00 | 12000.00 | 11000.00 | 11000.00 | 8473.00 | 8473.00 | 13500.00 | 13500.00 | 9705.00 | 9705.00 | 10900.00 | 10900.00 | 5200.00 | Industrial Traders
10.02 | 400CFM with 10mm Static | 2.00 | Nos | 20500.00 | 4900.00 | 9800.00 | 4856.00 | 9712.00 | 16000.00 | 32000.00 | 8500.00 | 17000.00 | 7420.00 | 14840.00 | 12000.00 | 24000.00 | 9000.00 | 18000.00 | 6760.00 | 13520.00 | 13500.00 | 27000.00 | 8575.00 | 17150.00 | 9900.00 | 19800.00 | 9712.00 | Blue Star Limited
10.03 | 300CFM with 10mm Static | 1.00 | No | 19500.00 | 4600.00 | 4600.00 | 3814.00 | 3814.00 | 14000.00 | 14000.00 | 6900.00 | 6900.00 | 6370.00 | 6370.00 | 12000.00 | 12000.00 | 7000.00 | 7000.00 | 5435.00 | 5435.00 | 12500.00 | 12500.00 | 7445.00 | 7445.00 | 8400.00 | 8400.00 | 3814.00 | Blue Star Limited
10.04 | 200CFM with 6mm Static | 1.00 | No | 12700.00 | 4400.00 | 4400.00 | 3814.00 | 3814.00 | 13000.00 | 13000.00 | 6800.00 | 6800.00 | 5530.00 | 5530.00 | 12000.00 | 12000.00 | 5500.00 | 5500.00 | 4566.00 | 4566.00 | 10500.00 | 10500.00 | 6880.00 | 6880.00 | 7550.00 | 7550.00 | 3814.00 | Blue Star Limited
10.05 | 100CFM with 6mm Static | 1.00 | No | 9500.00 | 4060.00 | 4060.00 | 2831.00 | 2831.00 | 13000.00 | 13000.00 | 6400.00 | 6400.00 | 4200.00 | 4200.00 | 12000.00 | 12000.00 | 4000.00 | 4000.00 | 3871.00 | 3871.00 | 10500.00 | 10500.00 | 6315.00 | 6315.00 | 7200.00 | 7200.00 | 2831.00 | Blue Star Limited
11.00 | M.S. Structure/ Work
11.01 | Supplying,Installing,Testing and Commissioning of MS structure work which will make the entire system as complete and functional and prove the practical results as per the design guidelines with all lead and lifts, M.S.plate /channels etc.for fixing different equipments as per instruction of Consultant/Engineer-in-charge.Inclusive of 2 coats of red oxide paint and black finish as per standards to avoid rusting of MS steel. | 200.00 | Kg | 65.00 | 98.00 | 19600.00 | 144.00 | 28800.00 | 160.00 | 32000.00 | 110.00 | 22000.00 | 90.00 | 18000.00 | 115.00 | 23000.00 | 140.00 | 28000.00 | 118.00 | 23600.00 | 85.00 | 17000.00 | 110.00 | 22000.00 | 128.00 | 25600.00 | 17000.00 | VOLGA AIR TECHNOLOGIES
12.00 | Electrical panel for AC
12.01 | Incomer 1 no of 400A,TP&N MCCB,36kA with Thermal Magnetic Release with rotary drive kit including door interlock,defeat and pad locking facility having overloadand short circuit protection. 1 set of (0-500V) Voltmeter, accuracy class. 1.0 with Voltmeter Selector Switch and indicating lamp with 3 nos. 1 set of (0-400A) Ammeter, Accuracy Class. 1.0 with 3 nos. 400/5A CTs and Ammeter selector switch. Bus bars 500A, TPN, Cu Bus bar with 100% Neutral as that of Phases, of suitable size with insulation sleeves. Outgoing 12 nos of 63A,TP&N MCB,36kA withThermal Magnetic Release with rotary drive kit including door interlock,defeat and padlocking facility having overload and short circuit protection. Note:- Panel shall be manufactured as per IEC 61439 for incomer ratings above 250 A . | 1.00 | Job | 425000.00 | 290000.00 | 290000.00 | 111814.00 | 111814.00 | 125000.00 | 125000.00 | 212000.00 | 212000.00 | 95000.00 | 95000.00 | 144788.00 | 144788.00 | 88000.00 | 88000.00 | 60000.00 | 60000.00 | 172500.00 | 172500.00 | 187127.00 | 187127.00 | 274962.00 | 274962.00 | 60000.00 | SAI H.V.A.C. SYSTEM
| Total in Figures |  |  |  |  | 5547960.00 |  | 4250319.00 |  | 4585100.00 |  | 4033140.00 |  | 3871448.00 |  | 4731899.00 |  | 4186550.00 |  | 5395648.00 |  | 4346394.00 |  | 3793646.00 |  | 5590597.50
Lowest Amount Quoted BY: S G TECHNOFAB PVT LTD(3793646.00)

## BOQ Summary
BOQ Summary Details Tender Title: Air-conditioning work. Tender ID: 2020_AAI_42770_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | S G TECHNOFAB PVT LTD | 3793646.00 | L1
| 2 | Sai Cooling Point Private Limited | 3871448.00 | L2
| 3 | UNITY ENGINEERS | 4033140.00 | L3
| 4 | M/S COOLING CENTER | 4186550.00 | L4
| 5 | Blue Star Limited | 4250319.00 | L5
| 6 | VOLGA AIR TECHNOLOGIES | 4346394.00 | L6
| 7 | VOLKS ENERGIE PVT LTD | 4585100.00 | L7
| 8 | Ingenious Industries | 4731899.00 | L8
| 9 | SAI H.V.A.C. SYSTEM | 5395648.00 | L9
| 10 | Industrial Traders | 5547960.00 | L10
| 11 | Shambhavi Enterprises | 5590597.50 | L11