## BoQ1
Government eProcurement System Created By: VENKATACHALAPATHI A T Created Date/Time: 09-Mar-2020 11:02 AM Tender Title: Replacement of Blower for Sewage Treatment Plant at Chennai International Airport Sub Head Replacement of Aeration Blowers for STP and Fire Static Tank pumps at Chennai Airport Tender ID: 2020_AAI_43008_1
Tender Inviting Authority: Asst.Gen.Manager (Engg-Elect)-VI,AEMD.
Name of Work: Replacement of Blower for Sewage Treatment Plant at Chennai International Airport. Sub Head: Replacement of Aeration Blowers for STP and Fire Static Tank pumps at Chennai Airport.
Contract No: AAI/CHE/AMED-VI/2019-20/03
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CHENNAI ENGINEERING SERVICES
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Replacement of existing Submerged Packed Bed Reactor (SPBR) Air Blower of Capacity: 600 CFM, Pressure: 7.4 PSIG for 4700 mm wg and coupled drive motor of suitable capacity (miminum 40 HP) including standard accessories confirming to Technical Specifications and modification of interconnecting air pipe line, installation on existing CC bed, earth connection, testing, commissioning etc., complete as required. | 2.00 | Job |  | 347499.00 | 694998.00 | 694998.00 | CHENNAI ENGINEERING SERVICES
2.00 | Replacement of existing Equalization Tank (EQT) Air Blower of Capacity: 385 CFM, Pressure: 7.1 PSIG for 3600 mm wg and coupled drive motor of suitable capacity (miminum 25 HP) including standard accessories confirming to Technical Specifications and modification of interconnecting air pipe line, installation on existing CC bed, earth connection, testing, commissioning etc., complete as required. | 2.00 | Job |  | 292719.00 | 585438.00 | 585438.00 | CHENNAI ENGINEERING SERVICES
3.00 | Replacement of existing Aerobic Digester (AD) Air Blower of Capacity:191 CFM, Pressure: 7.1 PSIG for 4150 mm wg and coupled drive motor of suitable capacity (miminum 12.5 HP) including standard accessories confirming to Technical Specifications and modification of interconnecting air pipe line, installation on existing CC bed, earth connection, testing, commissioning etc., complete as required. | 2.00 | Job |  | 176859.00 | 353718.00 | 353718.00 | CHENNAI ENGINEERING SERVICES
4.00 | Supply of Heavy duty exhaust fan of 18", 1400 RPM, 240V, 50Hz Single phase confirming to Technical Specifications etc., complete as required. | 2.00 | Nos |  | 3999.00 | 7998.00 | 7998.00 | CHENNAI ENGINEERING SERVICES
5.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc as required. Group C | 2.00 | Point |  | 599.00 | 1198.00 | 1198.00 | CHENNAI ENGINEERING SERVICES
6.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. Upto 450 mm sweep. | 2.00 | Each |  | 299.00 | 598.00 | 598.00 | CHENNAI ENGINEERING SERVICES
7.00 | Making of wall cut-out for exhaust fan up to 50 cm dia making good, cement finishing matching the surface, emulsion painting including disposal of malba complete etc as required. | 1.00 | Job |  | 1499.00 | 1499.00 | 1499.00 | CHENNAI ENGINEERING SERVICES
8.00 | Supply of Open well type submersible Pump Set of Suitable rating for discharge 33LPS @ 16 Mtr head with SS strainer,CED coated component , SS shaft using anti-friction bearing, energy efficient type operated on 3 Phase, 415V, 50Hz AC power supply with discharge outlet of of suitable dia with the specified minimum discharge capacity including loading, unloading at site etc complete as required. a) 15HP (Model: KOS-1537+, Make:Kirloskar) Location: 1. Old Fire Station & 2. New Fire Station | 6.00 | No |  | 40219.00 | 241314.00 | 241314.00 | CHENNAI ENGINEERING SERVICES
9.00 | Supply of GI piping and plumbing accessories as per technical specification etc., complete as required. a) 100mm GI ' B' class Pipe (Make: TATA) | 54.00 | Mtrs |  | 1399.00 | 75546.00 | 75546.00 | CHENNAI ENGINEERING SERVICES
10.00 | b) 100mm GI Elbow Threaded | 10.00 | No |  | 1299.00 | 12990.00 | 12990.00 | CHENNAI ENGINEERING SERVICES
11.00 | c) 100mm GI Pipe Nipple | 2.00 | No |  | 889.00 | 1778.00 | 1778.00 | CHENNAI ENGINEERING SERVICES
12.00 | d) 100mm Butterfly Valve | 2.00 | No |  | 2719.00 | 5438.00 | 5438.00 | CHENNAI ENGINEERING SERVICES
13.00 | e) 100mm GI Threaded (SCREWED) Flange | 14.00 | No |  | 659.00 | 9226.00 | 9226.00 | CHENNAI ENGINEERING SERVICES
14.00 | f) 100 mm Bronze Screwed Check Valve | 2.00 | No |  | 7149.00 | 14298.00 | 14298.00 | CHENNAI ENGINEERING SERVICES
15.00 | g) 100 mm GI Long Bend | 8.00 | No |  | 719.00 | 5752.00 | 5752.00 | CHENNAI ENGINEERING SERVICES
16.00 | h) 100mm Rubber Gasket | 10.00 | No |  | 69.00 | 690.00 | 690.00 | CHENNAI ENGINEERING SERVICES
17.00 | i) Red Oxide Primer (Make: Berger, 421 or equivalent) | 5.00 | Ltr |  | 139.00 | 695.00 | 695.00 | CHENNAI ENGINEERING SERVICES
18.00 | j) Red paint (Make: Berger, K70 Industrial Enamel or equivalent) | 5.00 | Ltr |  | 259.00 | 1295.00 | 1295.00 | CHENNAI ENGINEERING SERVICES
19.00 | Supply of 6 Core X 4 Sq.mm PVC Insulated, Round Sheathed, Un-Armoured, Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade 1100 Volts as per IS: 694:1990 etc., complete as required. Make: Polycab | 200.00 | Mtr |  | 249.00 | 49800.00 | 49800.00 | CHENNAI ENGINEERING SERVICES
20.00 | Restoration of faulty LT MCC panel including cleaning, de-rusting, spray painting of cubicle panels, Supply, installation, tesing, commisioning of all damaged components of Starter panel cubicles for pumps (15HP) with associated control wiring, ferrules & terminal blocks there protection accesories,LED indication Lamps, push botton etc., as required for 3 phase, 4 wire, 50 Hz supply system with complete technical/quality/workmanship compliance to LT panel technical specifications including connections, interconnections etc complete as required. Location:1. Old Fire Station & 2. New Fire Station | 6.00 | Job |  | 18999.00 | 113994.00 | 113994.00 | CHENNAI ENGINEERING SERVICES
21.00 | Provision of cable junction box, bakelite terminal block, wall mounting L-angle clamp with accessories, cable termination works including erection, installation, testing, commissioning etc., complete as required. | 6.00 | Job |  | 1499.00 | 8994.00 | 8994.00 | CHENNAI ENGINEERING SERVICES
22.00 | Replacement of old fire station static tank open well submersible pump of 15HP capacity including dismantling of existing pump and delivery line, erection of new pump along including delivery pipeline, pipe fittings, plumbing accessories, termination of cable, testing, commissioning etc complete as required. | 2.00 | Job |  | 3399.00 | 6798.00 | 6798.00 | CHENNAI ENGINEERING SERVICES
23.00 | Dismantling of open well type submersible pump from existing Sump at cowl bazar pump room along with delivery pipe line, PCC column clearing malba including transport, loading, unloading and handover in dismantle store at Old WTP etc complete as required. | 4.00 | Jobs |  | 9999.00 | 39996.00 | 39996.00 | CHENNAI ENGINEERING SERVICES
24.00 | Supplying and fixing of fabricated M.S. cable tray of size 300mm width using L-channel 50X50X5mm,Flat channel 25X5mm suspended on brick work column including painting, Conduit clamp holes confirming to technical specification etc., complete as required. | 20.00 | Mtr |  | 849.00 | 16980.00 | 16980.00 | CHENNAI ENGINEERING SERVICES
25.00 | Supplying and fixing of 40mm size medium class FRLS PVC conduit along with accessories in existing MS cable tray, using U-bolt clamps or surface/reccess including cutting the wall/floor and making good the same in case of recessed conduit etc., complete as required. | 66.00 | Mtr |  | 149.00 | 9834.00 | 9834.00 | CHENNAI ENGINEERING SERVICES
26.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Upto 35 sq.mm | 188.00 | R/M |  | 9.00 | 1692.00 | 1692.00 | CHENNAI ENGINEERING SERVICES
27.00 | Supply and erection of Fabricated Structural steel work column of approved design (using frame with minimum 5 mm thick MS-Channel and MS-Angle) with welded sections, truss, frame work of vertical height upto 3.5 mtr, frame width of 0.4 Mtr including hoisting, fixing in position, Anchor Fastener in welded base plates, painting with approved steel primer and two coat enamal paint for erection of 100 mm dia GI water pipe line which should be safe enough to handle vibrations of 15 HP pump water discharge pipeline etc complete as required. (Design should be pre-approved by Engineering-in-charge). | 325.00 | Kg |  | 99.00 | 32175.00 | 32175.00 | CHENNAI ENGINEERING SERVICES
28.00 | Installation, Testing and Commisioning of following capacity open well submersible pump in static tank (max depth of 5 Mtr) at including cable termination, drawing of cable along the pipe, erection of delivery pipe line, associated accessories, fixing of flanges, Elbows, couplings on existing MS frame structure rigidly using U-bolt clamps etc., complete as required. a) Open well Submersible- 15HP | 4.00 | Job |  | 5819.00 | 23276.00 | 23276.00 | CHENNAI ENGINEERING SERVICES
| Total in Figures |  |  |  |  | 2318008.00
Lowest Amount Quoted BY: CHENNAI ENGINEERING SERVICES(2318008.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Blower for Sewage Treatment Plant at Chennai International Airport Sub Head Replacement of Aeration Blowers for STP and Fire Static Tank pumps at Chennai Airport Tender ID: 2020_AAI_43008_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CHENNAI ENGINEERING SERVICES | 2318008.00 | L1