## BoQ1
Government eProcurement System Created By: SYED TANWEER ASHRAF Created Date/Time: 19-May-2020 02:32 PM Tender Title: Construction of Technical Block cum Control Tower at Gaya Airport, Gaya. SH Provision of D.G Sets and substation equipments Tender ID: 2020_AAI_43578_1
Tender Inviting Authority: SM ( Engg. Elect), AAI, Gaya Airport, Gaya
Name of Work: Construction of Technical Block cum Control Tower at Gaya Airport, Gaya. (SH: Provision of D.G Sets & sub-station equipments)
Contract No: 0631-2210043
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Konstelec Engineers Pvt. Ltd. |  | UNIQUE TRANSFORMER SERVICE INDUSTRIES |  | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION |  | CANELA ENTERPRISES PVT LTD |  | AT AND T ENGINEERS PVT LTD
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying of following size of XLPE insulated PVC sheathed armoured power cable of aluminium conductor confirming to IS: 7098 Part - II -1985 with latest amendments etc. as required. (a) 3 core X 300 Sqmm. - 33 KV Grade (E). | 5000.00 | Mtr. |  | 1504.00 | 7520000.00 | 1250.00 | 6250000.00 | 1700.00 | 8500000.00 | 1600.00 | 8000000.00 | 1476.00 | 7380000.00 | 6250000.00 | UNIQUE TRANSFORMER SERVICE INDUSTRIES
2.00 | Supply of HDPE Pipes of 160 mm dia as per IS: 4984 : 2016 of Material Grade : PE 63 & Pressure Rating of PN 8 etc as required. | 4800.00 | Mtr. |  | 284.00 | 1363200.00 | 800.00 | 3840000.00 | 350.00 | 1680000.00 | 1025.00 | 4920000.00 | 708.00 | 3398400.00 | 1363200.00 | Konstelec Engineers Pvt. Ltd.
3.00 | Making horizontal boring by HDD method suitable for laying of 160 mm dia. (min.) HDPE Pipe at a min. depth of 1.2 meter below the common ground surface level i/c drawing & laying of HDPE Pipe etc complete as required ( Supply of HDPE pipe not included). | 4800.00 | Mtr. |  | 1010.00 | 4848000.00 | 150.00 | 720000.00 | 800.00 | 3840000.00 | 900.00 | 4320000.00 | 578.00 | 2774400.00 | 720000.00 | UNIQUE TRANSFORMER SERVICE INDUSTRIES
4.00 | Laying of one no. XLPE/PVC insulated PVC sheathed power cable of 33 KV of size exceeding 120 Sqmm but not exceeding 400 Sqmm in the existing RCC/hume/stone ware/GI/HDPE Pipe as required | 4800.00 | Mtr. |  | 126.00 | 604800.00 | 150.00 | 720000.00 | 450.00 | 2160000.00 | 250.00 | 1200000.00 | 105.00 | 504000.00 | 504000.00 | AT AND T ENGINEERS PVT LTD
5.00 | Laying of one no. XLPE/PVC insulated PVC sheathed power cable of 33 KV of size exceeding 120 Sqmm but not exceeding 400 Sqmm in the existing masonary open duct. | 200.00 | Mtr. |  | 126.00 | 25200.00 | 150.00 | 30000.00 | 100.00 | 20000.00 | 250.00 | 50000.00 | 105.00 | 21000.00 | 20000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
6.00 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 33 kV grade as required.
6.01 | 3 core X 300 Sqmm. | 8.00 | Each |  | 46949.00 | 375592.00 | 25000.00 | 200000.00 | 20000.00 | 160000.00 | 32000.00 | 256000.00 | 31863.00 | 254904.00 | 160000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
7.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement: 2 coarse: 4 graded stone aggregate 20 mm niminal size) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10 cm including inscription duly engraved as required. | 20.00 | Each |  | 726.00 | 14520.00 | 560.00 | 11200.00 | 300.00 | 6000.00 | 1000.00 | 20000.00 | 552.00 | 11040.00 | 6000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
8.00 | Constructing masonry Chamber 120x120x100 cm inside, in brick work with common burnt clay F.P.S bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) , i/c necessary excavation, foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard design. | 15.00 | Each |  | 8320.00 | 124800.00 | 23040.00 | 345600.00 | 1200.00 | 18000.00 | 12000.00 | 180000.00 | 26250.00 | 393750.00 | 18000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
9.00 | Supply, Installation, testing and Commissioning of indoor type 500 KVA,3 Phase oil immersed natural cooled (ONAN) double wound with copper wire, continuous rated core type 33 KV/433 V, 50 Hz with off load tap changer +/- 7.5 % in 2.5% step transformer, delta connected on HT side and Star connected on LT side with vector group DYn11, cable box for HT & MV termination suitable for 33 KV, 3 core x 300 Sq.mm.XLPE cable on HT side and 1.1 KV, 3.5 core upto 400 Sq. mm cable connection arrangement on LT side complete with all accessories. Buchnolz relay and first fill of filtered oil and confirming to IS:1180 Level 2 & additional specifications etc as required. | 2.00 | Job |  | 961775.00 | 1923550.00 | 1650000.00 | 3300000.00 | 900000.00 | 1800000.00 | 1400000.00 | 2800000.00 | 948094.00 | 1896188.00 | 1800000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
10.00 | Supplying, Installation, testing and commissioning of indoor type floor mounted metal clad, 33 KV panel with 4 No. VCBs, totally enclosed & fully interlocked, horizontal draw out, horizontal isolation type breaker as per IS 13118, as amended up to date and additional specifications, having capacities as mentioned below, single break, trip free mechanism, manually/motorized charged and auto/ manually closing breaker suitable for use on 33 KV, 3 Phase,630A, 25kA/3 sec. 50 Hz, A.C supply, with short circuit fault level of 500 MVA, complete with self contained, fully interlocked, rack-in and rack-out mechanism, air insulated but encapsulated Copper bus bars with Sleeving of 1600 Amps capacity, breaker featured with mechanical ON/OFF indicator with hand trip device, spring release coil, shunt trip coil and auxiliary switch of 6 NO + 6 NC and equipped with following switchgears & accessories i/c POWER PACK connections suitable for 3 CoreX 300 sq. mm HT XLPE insulated, 33 KV cable (cable entry from bottom side), end termination with heat shrinkable jointing material etc as required. ( Note- Cost of end termination not included in this item.) (for new Substation) INCOMER PANEL (a)2 No. - 33 KV,630 Amps,25 KA, three pole vacuum circuit breaker having rupturing capacity of 500 MVA having rear entry cable and box suitable to receive 3 core X 300 Sqmm 33 KV XLPE Cable alongwith the following acessary in each breaker panel. (b) 1600 Amps air insulated but encapsulated with PVC insulated heat shrinnkable sleeves, Copper busbar on top portion of the panel. (c) Necessary strip heaters with thermostat and an isolator suitable to operate on 230 V, 50 Hz, AC Supply for moisture absorption purpose. (d) 50/1+1 A dual Ratio cast Resin CT having 15 VA output 5 P 10 accuacy class for protection and class 0.5 for metering - 3 Nos. (the CT ratings shall be suitable as per system design /site requirement). (e) 33 Kv/110V fully withdrawable type 3 phase 3 limb PT with automatic shutters with an output of 100 VA / phase. Class- I accuracy complete with HT/LT fuses - 1 No. (the PT ratings shall be suitable as per OEM system design /site requirement). (f) Numerical,communicable,drawout type relay with MODBUS protocol-51/50N/50/51N, Master trip relay, Trp Circuit Supervision Relay, Auxiliary relay etc. (g) Digital Ammeter with selector switch. (h) Digital Voltmeter with selector switch. (i) Indication lamps for on/off indication and trip healthy.spring charged,Auto trip,CB Test position, R/Y/B indication (LED type). (j) All wiring necessary for the above including interconnection for buchholz relay alarm and trip on outgoing feedres. (k) Test Terminal blocks, fuses and labels. (i) Push button for trip circuit health check,3 Pin 15 A Socket +Switch , Auxiliary contacts,12 window annunciator & necessary trip power supply/ Power pack etc. j) Any other accessories & instruments e.g Multifunction Meters, frequency meters etc complete as required. OUTGOING PANELS (a) 2 Nos.- 33 KV, 630 Amps,25 KA three pole vacuum circuit breaker having rupturing capacity of 500 MVA having rear entry cable and box suitable to receive 3 core X 300 Sqmm 33 KV XLPE Cable alongwith the following acessary in each breaker panel. (b) 1600 Amps air insulated but encapsulated with PVC insulated heat shrinnkable sleeves, Copper busbar on top portion of the panel (common for incoming and outgoing panel). (c) Necessary strip heaters with thermostat and an isolator suitable to operate on 230 V, 50 Hz, AC Supply for moisture absorption purpose. (d) 50/1+1A dual Ratio cast Resin CT having 15 VA output 5p 10 accuacy class for protection and class 0.5 for metering - 3 Nos./ or as per manufacturer's design as per site requirement. (e) Numerical,communicable,drawout type relay with MODBUS protocol-51/50N/50/51N, Master trip relay, Trp Circuit Supervision Relay, Auxiliary relay etc. (f) Digital Ammeter with selector switch. (g) Digital Voltmeter with selector switch. (i) Indication lamps for on/off indication and trip healthy.spring charged,Auto trip,CB Test position, R/Y/B indication (LED type). (j) All wiring necessary for the above including interconnection for buchholz relay alarm and trip on outgoing feedres. (k) Test Terminal blocks, fuses and labels. (i) Push button for trip circuit health check,3 Pin 15 A Socket +Switch , Auxiliary contacts,12 window annunciator & necessary trip power supply/ Power pack etc complete as required | 1.00 | Job |  | 3259425.00 | 3259425.00 | 4200000.00 | 4200000.00 | 1500000.00 | 1500000.00 | 3100000.00 | 3100000.00 | 3036000.00 | 3036000.00 | 1500000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
11.00 | Supplying, Installation, testing and commissioning of indoor type floor mounted metal clad, 33 KV panel with 1 No. VCB (as outgoing) totally enclosed & fully interlocked, horizontal draw out, horizontal isolation type breaker as per IS 13118, as amended up to date and additional specifications, having capacities as mentioned below, single break, trip free mechanism, manually/motorized charged and auto/ manually closing breaker suitable for use on 33 KV, 3 Phase,1250A,25kA/3 sec. 50 Hz, A.C supply with short circuit fault level of 500 MVA, complete with self contained, fully interlocked, rack-in and rack-out mechanism, air insulated but encapsulated Copper bus bars with Sleeving of 2000 Amps capacity, breaker featured with mechanical ON/OFF indicator with hand trip device, spring release coil, shunt trip coil and auxiliary switch of 6 NO + 6 NC and equipped with following switchgears & accessories i/c POWER PACK connections suitable for 3 CoreX 300 sq. mm HT XLPE insulated, 33 KV cable (cable entry from bottom side), end termination with heat shrinkable jointing material etc as required with following: ( Note- Cost of end termination not included in this item.) (Note: This panel has to be integrated with the existing 33 KV VCB Panel of Siemens make) OUTGOING PANELS (a) 1 Nos. 1250 Amps three pole vacuum circuit breaker having rupturing capacity of 500 MVA at 33 KV having rear entry cable and box suitable to receive 3 core X 300 Sqmm 33 KV XLPE Cable alongwith the following acessary in the breaker panel. (b) 2000 Amps air insulated but encapsulated with PVC insulated heat shrinnkable sleeves, Copper busbar on top portion of the panel (common for incoming and outgoing panel). (c) Necessary strip heaters with thermostat and an isolator suitable to operate on 230 V, 50 Hz, AC Supply for moisture absorption purpose. (d) 50/1+1 A dual Ratio cast Resin CT having 100 VA output 5p 10 accuacy class for protection and class 1 for metering - 3 Nos. (the CT ratings shall be suitable as per system design /site requirement). (e) Protection arrangement with 2 Nos. O/C, and 1 No. E/F IDMT relay with shunt trip on 24/30 V DC supply system. (f) 96 mm X 96 mm Ammeter with selector switch. (g) 96 mm X 96 mm Voltmeter with selector switch. (h) Indication lamps for on/off indication and trip healthy indication (LED type). (i) All wiring necessary for the above including interconnection with the existing outgoing VCB panels. (j) All necessary connections /provisions as required as per site condition for extension of /integration with the existing VCB Panel etc as required. | 2.00 | Job |  | 785325.00 | 1570650.00 | 1400000.00 | 2800000.00 | 57777.00 | 115554.00 | 1050000.00 | 2100000.00 | 690150.00 | 1380300.00 | 115554.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
12.00 | SITC of Adapter Panel for extension of/ integration with the existing 33 KV VCB Panel board of Siemens make outgoings including complete connections,interconnections & other provisions whatever required as per site condition (If required) | 1.00 | Job |  | 99875.00 | 99875.00 | 150000.00 | 150000.00 | 300000.00 | 300000.00 | 600000.00 | 600000.00 | 868125.00 | 868125.00 | 99875.00 | Konstelec Engineers Pvt. Ltd.
13.00 | Design, manufacture Supply, Installation, Testing and Commissioning of main LT panel, cubicle type, made of 2 mm thick sheet steel, totally enclosed, IP 52, free standing, floor mounting, dust and vermin proof ,indoor, compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al.busbars extensible on both sides, interconnections including supply & installation of following items and as per Technical specification: INCOMER 2 Nos. ACB, 1000 A, FP, 50 kA, (for Transformers) motor wound spring charged closing mechanism,drawout type ACB with Microprocessor based release having short circuit, over current, earth fault, zone selective interlocking features with communication port RS 485 2 Nos. ACB, 1000 A, FP, 50 kA, (for DG Sets) motor wound spring charged closing mechanism,drawout type ACB with Microprocessor based release having short circuit, over current, earth fault, zone selective interlocking features with communication port RS 485 4 nos. Intelligent multi function digital meter to read V,A,KVA, KW, KVAR, PF, Hz etc with communication facility ( RS485 port ) and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with HRC control fuses/MCBs. 4 nos. Digital Voltmeter suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos of HRC control fuses/MCBs.. 4 Sets Indication Lamps (1 Set for each ACB), LED type, R,Y,B and breaker 'ON' , 'OFF', 'TRIP' lamps 4 nos. Digital Ammeter of suitable range (to measure 0-2500A), for 3 phase 4 wire operation with LED display and selector switch and CT ratio programmable and auto ranging along with 3 nubmers of class 1.0, 15 VA suitable range CTs. 4 nos. of current transformer Class 0.5, 15 VA for IPFC Relay. Bus Bars 01 set of Bus bars, 1250 Amps, TPN, Aluminium Bus bars Bus coupler 1000 A, FP, 50 kA, motor wound spring charged closing mechanism,drawout type ACB with Microprocessor based release having short circuit, over current, earth fault zone selective interlocking features with communication port RS 485.- 1 No. Indication Lamps, LED type 'ON' , 'OFF', 'TRIP' lamps with HRC control fuses/MCBs etc for bus coupler Accessories for Electrical Interlocking Micro PLC & other necessary accessories for electrical & Mechanical interlocking among 2 Nos Incomers for transformer, 2 Nos. Incomers for DG Sets and Bus coupler as required shall be provided including interconnection etc as required. Outgoing 3 Nos. MCCB, 630 A, 50 kA, Four Pole, with microprocessor based release having over Current,Short Circuit,Earth Fault Protection module. (Ics=100%Icu) 4 Nos. MCCB, 400 A, 50 kA, Four Pole, with microprocessor based release having over Current,Short Circuit,Earth Fault Protection module. (Ics=100 %Icu) 2 Nos. MCCB, 250 A, 50 kA, Four Pole, with microprocessor based release having over Current,Short Circuit,Earth Fault Protection module. (Ics=100 %Icu) 2 Nos. MCCB, 200 A, 36 kA, Four Pole, with microprocessor based release having over Current,Short Circuit,Earth Fault Protection module. (Ics=100 %Icu) 10 Nos. MCCB, 100A,36 kA, Four Pole, with microprocessor based release having over Current,Short Circuit,Earth Fault Protection module.(Ics=100 %Icu) 8 Nos. MCCB, 63 A, 25 kA, Four Pole , with Thermal magnetic release(Ics=100 %Icu) 29 nos. Intelligent multi function digital meter to read V,A,KVA, KW, KVAR, PF, Hz etc with communication facility ( RS485 port ) and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with HRC control fuses/MCBs. 29 Sets (1 set for each MCCB) of Extended Rotary operating mechanism, terminal extension spreaders and 'ON' (Red) indication lamp (LED type) with HRC control fuse/MCBs Components for AMF operation of D.G Sets Provision for Auto mains Failure System operation capable of Auto/ Manual mode operation, protection, measurement, display of electrical & D.G parameters complete with AMF Relay,Master trip relay , phase reversal, engine start relay,cranking relay, auxiliary relays, Auxiliary Contactors, Push Button etc i/c all the necessary provisions one set each for 2 D.G Sets to achieve AMF function as described in the technical specification. Other Components & Accessories Indicating lamps "Load on set" "Load on Mains" for each DG set Emergency stop push button for each DG set and transformer Engine start / stop / push button for each DG set Auto / Manual selector switch 12 window annunciator for each DG set faults 1 No. common hooter Battery charger for each D.G Sets with inbuilt trickle & boost facility, DC Ameter, DC Voltmeter, Selector switch etc Any other provision / component & accessories required for proper synchronisation operation & control i.c AMF function at Panel end etc as required. | 1.00 | Job |  | 3642920.00 | 3642920.00 | 3722120.00 | 3722120.00 | 3000000.00 | 3000000.00 | 3800000.00 | 3800000.00 | 2968350.00 | 2968350.00 | 2968350.00 | AT AND T ENGINEERS PVT LTD
14.00 | CAPACITOR PANEL Design, Supply, Installation, Testing and Commissioning of Automatic Power Factor Corrector Panel, 250 kVAR, 3ph, 415v, totally enclosed, free standing, floor mounting, dust and vermin proof, cubicle type to be fabricated out of min. 2 mm thick Sheet steel, with provision for capacitor mounting arrangement inside the panel with Aluminium Busbars, interconnections, adequate number of louvers and powder coated with approved shade including supply & installation of following components and as per technical specifications: INCOMER 1 Nos. MCCB, 630, 50 kA, Four Pole, with microprocessor based release having over Current,Short Circuit,Earth Fault Protection module. (Ics=100%Icu) 1 no. Intelligent multi function digital meter to read V,A,KVA, KW, KVAR, PF, Hz etc with communication facility (RS485 port) and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with HRC control fuses. 1 Set of 630A TPN Aluminium conductor busbar. 1 Set of Digital Voltmeter suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos of HRC control fuses/MCBs. 1 Set of Indication Lamps, LED type, R,Y,B and breaker 'ON' , 'OFF' & 'TRIP' lamps 1 Set of Digital Ammeter of suitable range for 3 phase 4 wire operation with LED display and selector switch and suitable CT ratio programmable and auto ranging along with 3 nubmers of class 1.0, 15 VA CTs. Microprocessor based intelligent, 14 step APFC relay with PF display and adjustable setting CAPACITORS 3 Nos. 50 KVAR Super Heavy duty capacitor units. 2 Nos. 25 KVAR Super Heavy duty capacitor units. 4 Nos. 10 KVAR Super Heavy duty capacitor units. 2 Nos. 5 KVAR Super Heavy duty capacitor units. OUTGOING SWITCHGEARS & OTHER COMPONENTS 3 Nos. 160 A, TP MCCB, 50 KA.thermal magnetic release with overload setting (Ics=100 %Icu) 2 Nos. 100 A, TP MCCB, 50 KA.thermal magnetic release with overload setting (Ics=100%Icu) 4 Nos. 32 A, TP MCB, 10 KA 2 Nos. 16A, TP MCB, 10 KA. 50 kVAr capacitor duty contactor with illuminated ON- OFF push buttons (LED type)- 3 Nos. 25 kVAr capacitor duty contactor with illuminated ON- OFF push buttons (LED type)-2 No. 10 kVAr capacitor duty contactor with illuminated ON- OFF push buttons (LED type)- 4 Nos. 5 kVAr capacitor duty contactor with illuminated ON- OFF push buttons (LED type)- 2 No. 2 Sets of Axial flow fans with thermostate. 1 Set of Rotary operating mechanism and terminal extension / spreaders for all the MCCBs. Complete in all respect including all interconnections from the bus bars to MCCB and MCCB to contactor and contactor to terminal blocks for Automatic Switching "ON" and "OFF" capacitor panel described as above | 2.00 | Job |  | 440048.00 | 880096.00 | 325001.00 | 650002.00 | 800000.00 | 1600000.00 | 650000.00 | 1300000.00 | 356165.00 | 712330.00 | 650002.00 | UNIQUE TRANSFORMER SERVICE INDUSTRIES
15.00 | Supplying of following size of 1.1 KV grade XLPE insulated PVC sheathed armoured power cable of aluminium conductor confirming to IS: 7098 Part - I-1988 with latest amendments etc. as required.
15.01 | 3.5 Core X 400 Sq. mm Cable | 200.00 | Mtr. |  | 1110.00 | 222000.00 | 1000.00 | 200000.00 | 980.00 | 196000.00 | 1100.00 | 220000.00 | 1049.00 | 209800.00 | 196000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
15.02 | 3.5 Core X 240 Sq. mm Cable | 150.00 | Mtr. |  | 774.00 | 116100.00 | 650.00 | 97500.00 | 629.00 | 94350.00 | 750.00 | 112500.00 | 676.00 | 101400.00 | 94350.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
15.03 | 3.5 Core X 185 Sq. mm Cable | 200.00 | Mtr. |  | 576.00 | 115200.00 | 500.00 | 100000.00 | 499.00 | 99800.00 | 610.00 | 122000.00 | 531.00 | 106200.00 | 99800.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
15.04 | 3.5 Core X 120 Sq. mm Cable | 100.00 | Mtr. |  | 408.00 | 40800.00 | 350.00 | 35000.00 | 338.00 | 33800.00 | 410.00 | 41000.00 | 350.00 | 35000.00 | 33800.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
15.05 | 3.5 Core X 70 Sq. mm Cable | 600.00 | Mtr. |  | 239.00 | 143400.00 | 225.00 | 135000.00 | 224.00 | 134400.00 | 290.00 | 174000.00 | 224.00 | 134400.00 | 134400.00 | AT AND T ENGINEERS PVT LTD, PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
15.06 | 3.5 Core X 50 Sq. mm Cable | 350.00 | Mtr. |  | 185.00 | 64750.00 | 165.00 | 57750.00 | 165.00 | 57750.00 | 210.00 | 73500.00 | 163.00 | 57050.00 | 57050.00 | AT AND T ENGINEERS PVT LTD
16.00 | Supplying and Making end terminations with brass compression gland and aluminium lugs for following size of PVC insulated and PVC SHEATHED/XLPE aluminium conductor cable of 1.1 KV grade as required.
16.01 | 3.5 Core X 400 Sq. mm Cable | 12.00 | Each |  | 2459.00 | 29508.00 | 1200.00 | 14400.00 | 550.00 | 6600.00 | 2500.00 | 30000.00 | 1376.00 | 16512.00 | 6600.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
16.02 | 3.5 Core X 240 Sq. mm Cable | 4.00 | Each |  | 1639.00 | 6556.00 | 800.00 | 3200.00 | 450.00 | 1800.00 | 1600.00 | 6400.00 | 1018.00 | 4072.00 | 1800.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
16.03 | 3.5 Core X185 Sq. mm Cable | 4.00 | Each |  | 1325.00 | 5300.00 | 600.00 | 2400.00 | 350.00 | 1400.00 | 1400.00 | 5600.00 | 1018.00 | 4072.00 | 1400.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
16.04 | 3.5 Core X 120 Sq. mm Cable | 12.00 | Each |  | 1110.00 | 13320.00 | 400.00 | 4800.00 | 350.00 | 4200.00 | 1100.00 | 13200.00 | 604.00 | 7248.00 | 4200.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
16.05 | 3.5 Core X 70 Sq. mm Cable | 12.00 | Each |  | 787.00 | 9444.00 | 400.00 | 4800.00 | 250.00 | 3000.00 | 900.00 | 10800.00 | 548.00 | 6576.00 | 3000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
16.06 | 3.5 Core X 50 Sq. mm Cable | 12.00 | Each |  | 641.00 | 7692.00 | 250.00 | 3000.00 | 250.00 | 3000.00 | 650.00 | 7800.00 | 548.00 | 6576.00 | 3000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION, UNIQUE TRANSFORMER SERVICE INDUSTRIES
17.00 | Supply and Making end terminations for the following size of 33 KV grade Aluminium conductor XLPE insulated cable with heat shrinkable jointing kits etc. Complete with all accessories as required.
17.01 | 3 core X 300 Sqmm. indoor end termination. | 8.00 | Each |  | 17562.00 | 140496.00 | 15000.00 | 120000.00 | 8000.00 | 64000.00 | 16000.00 | 128000.00 | 12761.00 | 102088.00 | 64000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
18.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
18.01 | 450 mm width X 50 mm depth X 2.0 mm thickness | 100.00 | Mtr. |  | 853.00 | 85300.00 | 1000.00 | 100000.00 | 600.00 | 60000.00 | 1800.00 | 180000.00 | 1066.00 | 106600.00 | 60000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
18.02 | 300 mm width X 50 mm depth X 1.6 mm thickness | 150.00 | Mtr. |  | 643.00 | 96450.00 | 900.00 | 135000.00 | 500.00 | 75000.00 | 1350.00 | 202500.00 | 671.00 | 100650.00 | 75000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
18.03 | 150 mm width X 50 mm depth X 1.6 mm thickness | 100.00 | Mtr. |  | 433.00 | 43300.00 | 450.00 | 45000.00 | 350.00 | 35000.00 | 900.00 | 90000.00 | 426.00 | 42600.00 | 35000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
19.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray “bends” (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
19.01 | 450 mm width X 50 mm depth X 2.0 mm thickness | 8.00 | Each |  | 2428.00 | 19424.00 | 2000.00 | 16000.00 | 500.00 | 4000.00 | 650.00 | 5200.00 | 2156.00 | 17248.00 | 4000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
19.02 | 300 mm width X 50 mm depth X 1.6 mm thickness | 12.00 | Each |  | 1892.00 | 22704.00 | 1500.00 | 18000.00 | 300.00 | 3600.00 | 500.00 | 6000.00 | 1306.00 | 15672.00 | 3600.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
19.03 | 150 mm width X 50 mm depth X 1.6 mm thickness | 8.00 | Each |  | 1703.00 | 13624.00 | 800.00 | 6400.00 | 250.00 | 2000.00 | 450.00 | 3600.00 | 823.00 | 6584.00 | 2000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
20.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray “Reducer” (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc.
20.01 | 450 mm width X 50 mm depth X 2.0 mm thickness | 2.00 | Each |  | 2428.00 | 4856.00 | 2000.00 | 4000.00 | 500.00 | 1000.00 | 650.00 | 1300.00 | 2394.00 | 4788.00 | 1000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
20.02 | 300 mm width X 50 mm depth X 1.6 mm thickness | 4.00 | Each |  | 1892.00 | 7568.00 | 1500.00 | 6000.00 | 300.00 | 1200.00 | 500.00 | 2000.00 | 1443.00 | 5772.00 | 1200.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
20.03 | 150 mm width X 50 mm depth X 1.6 mm thickness | 2.00 | Each |  | 1703.00 | 3406.00 | 800.00 | 1600.00 | 260.00 | 520.00 | 450.00 | 900.00 | 908.00 | 1816.00 | 520.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 95 sq. mm and upto 185 sq. mm size in the existing RCC/HUME/ METAL pipe as required. | 250.00 | Mtr. |  | 45.00 | 11250.00 | 100.00 | 25000.00 | 100.00 | 25000.00 | 150.00 | 37500.00 | 79.00 | 19750.00 | 11250.00 | Konstelec Engineers Pvt. Ltd.
22.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 185 sq. mm and upto 400 sq. mm size in the existing RCC/HUME/ METAL pipe as required. | 250.00 | Mtr. |  | 76.00 | 19000.00 | 150.00 | 37500.00 | 100.00 | 25000.00 | 270.00 | 67500.00 | 89.00 | 22250.00 | 19000.00 | Konstelec Engineers Pvt. Ltd.
23.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 35 sq. mm and upto 95 sq. mm size in the existing RCC/HUME/ METAL pipe as required. | 400.00 | Mtr. |  | 40.00 | 16000.00 | 75.00 | 30000.00 | 100.00 | 40000.00 | 100.00 | 40000.00 | 63.00 | 25200.00 | 16000.00 | Konstelec Engineers Pvt. Ltd.
24.00 | Laying of one number XLPE insulated and PVC sheathed power cable of 1.1 KV grade in the existing open duct as required.
24.01 | Above 35 Sq. mm upto 95 Sq. mm | 100.00 | Mtr. |  | 40.00 | 4000.00 | 100.00 | 10000.00 | 80.00 | 8000.00 | 80.00 | 8000.00 | 63.00 | 6300.00 | 4000.00 | Konstelec Engineers Pvt. Ltd.
24.02 | Above 95 Sq. mm upto 185 Sq. mm | 50.00 | Mtr. |  | 45.00 | 2250.00 | 150.00 | 7500.00 | 80.00 | 4000.00 | 120.00 | 6000.00 | 79.00 | 3950.00 | 2250.00 | Konstelec Engineers Pvt. Ltd.
24.03 | Above 185 Sq. mm upto 400 Sq. mm | 200.00 | Mtr. |  | 76.00 | 15200.00 | 75.00 | 15000.00 | 80.00 | 16000.00 | 150.00 | 30000.00 | 89.00 | 17800.00 | 15000.00 | UNIQUE TRANSFORMER SERVICE INDUSTRIES
25.00 | Laying of one number XLPE insulated and PVC sheathed aluminium conductor cable of 1.1KV grade of following size on surface/ cable tray as required.
25.01 | Above 35 sq. mm and upto 95 Sq. mm | 200.00 | Mtr. |  | 35.00 | 7000.00 | 150.00 | 30000.00 | 100.00 | 20000.00 | 100.00 | 20000.00 | 63.00 | 12600.00 | 7000.00 | Konstelec Engineers Pvt. Ltd.
25.02 | Above 95 sq. mm and upto 185 sq. mm | 150.00 | Mtr. |  | 40.00 | 6000.00 | 75.00 | 11250.00 | 100.00 | 15000.00 | 150.00 | 22500.00 | 79.00 | 11850.00 | 6000.00 | Konstelec Engineers Pvt. Ltd.
26.00 | Earthing with Copper earth plate 600 mm X 600 mm X 3 mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe 2.7 mtr. long etc. with charcoal and salt complete as required. | 8.00 | Set |  | 15103.00 | 120824.00 | 15500.00 | 124000.00 | 20000.00 | 160000.00 | 13000.00 | 104000.00 | 15563.00 | 124504.00 | 104000.00 | CANELA ENTERPRISES PVT LTD
27.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal and salt complete as required. | 12.00 | Set |  | 11323.00 | 135876.00 | 7500.00 | 90000.00 | 10000.00 | 120000.00 | 7000.00 | 84000.00 | 11400.00 | 136800.00 | 84000.00 | CANELA ENTERPRISES PVT LTD
28.00 | Providing and fixing 25 mm x 5 mm Copper strip in 40 mm dia G. I. pipe from earth electrode including connection with brass nut, bolts, spring, washer excavations and refilling etc. as required. | 48.00 | Mtr. |  | 686.00 | 32928.00 | 1100.00 | 52800.00 | 650.00 | 31200.00 | 1200.00 | 57600.00 | 1229.00 | 58992.00 | 31200.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
29.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in reces for connections etc. as required. | 64.00 | Mtr. |  | 625.00 | 40000.00 | 190.00 | 12160.00 | 350.00 | 22400.00 | 900.00 | 57600.00 | 670.00 | 42880.00 | 12160.00 | UNIQUE TRANSFORMER SERVICE INDUSTRIES
30.00 | Providing and fixing 25 mm x 5 mm G. I. strip in 40 mm dia G. I. pipe from earth electrode including connection with G.I. nut, bolts, spring, washer excavation and refilling etc. as required. | 72.00 | Mtr. |  | 158.00 | 11376.00 | 1120.00 | 80640.00 | 450.00 | 32400.00 | 550.00 | 39600.00 | 652.00 | 46944.00 | 11376.00 | Konstelec Engineers Pvt. Ltd.
31.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in reces for connections etc. as required. | 96.00 | Mtr. |  | 97.00 | 9312.00 | 190.00 | 18240.00 | 350.00 | 33600.00 | 250.00 | 24000.00 | 93.00 | 8928.00 | 8928.00 | AT AND T ENGINEERS PVT LTD
32.00 | Supplying and fixing in position 3 Nos. of 9 ltr.. Capacity G.I. fire buckets duly painted with red oxicle and red paint and text. "FIRE" in white mounted on suitable size MS angle frame including grouting in floor or wall and filling dry sand etc. as required. | 2.00 | Set |  | 2395.00 | 4790.00 | 3000.00 | 6000.00 | 7000.00 | 14000.00 | 5000.00 | 10000.00 | 8033.00 | 16066.00 | 4790.00 | Konstelec Engineers Pvt. Ltd.
33.00 | Supply, installation, testing and commissioning ISI maked (IS:15683) Fire Extinguisher, Carbon-di-oxide type capacity 4.5 kg. Flat base including valve, discharge hose of not less than 10mm dia, 1M long, and complete in all respects including initial fill with CO2 gas conforming to IS:307-1966 and wall suspension braket as required as per specification. | 10.00 | Each |  | 5230.00 | 52300.00 | 5000.00 | 50000.00 | 9000.00 | 90000.00 | 6000.00 | 60000.00 | 5730.00 | 57300.00 | 50000.00 | UNIQUE TRANSFORMER SERVICE INDUSTRIES
34.00 | Supply,installation,testing and commissioning of 6kg ABC (Powder Type) Fire Extinguisher,Mild Steel Cylinders ISI marked fitted with pressure indicating gauge,internal tube,squeeze lever type valve fully charged with ABC 90 Powder (Monoammonium phoshate) pressured by Nitrogen complete in all respects including wall suspension bracket and conforming to IS:15683 as required as per specification. | 10.00 | Each |  | 3813.00 | 38130.00 | 5000.00 | 50000.00 | 7000.00 | 70000.00 | 10000.00 | 100000.00 | 5730.00 | 57300.00 | 38130.00 | Konstelec Engineers Pvt. Ltd.
35.00 | Supply and fixing in position shock treatment charts written in "English" and "Hindi" duly mounted on wooden frame with glass covering / in fiber board etc. complete as required. | 2.00 | Each |  | 1147.00 | 2294.00 | 500.00 | 1000.00 | 3000.00 | 6000.00 | 2500.00 | 5000.00 | 8543.00 | 17086.00 | 1000.00 | UNIQUE TRANSFORMER SERVICE INDUSTRIES
36.00 | Supply and Fixing First Aid box made of MS with powder coating, front door transparent Made of Acrylic sheet of size 15"x11"x4" with two compartments, hinged cover with locking arrangement with necessary general medical grade tools and medicines. | 1.00 | Set |  | 1991.00 | 1991.00 | 2000.00 | 2000.00 | 4900.00 | 4900.00 | 5000.00 | 5000.00 | 8543.00 | 8543.00 | 1991.00 | Konstelec Engineers Pvt. Ltd.
37.00 | Providing and fixing H.T. danger notice plate of 250 mm X 200 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 2.00 | Each |  | 1147.00 | 2294.00 | 250.00 | 500.00 | 1000.00 | 2000.00 | 500.00 | 1000.00 | 334.00 | 668.00 | 500.00 | UNIQUE TRANSFORMER SERVICE INDUSTRIES
38.00 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 3.00 | Each |  | 1336.00 | 4008.00 | 250.00 | 750.00 | 800.00 | 2400.00 | 500.00 | 1500.00 | 334.00 | 1002.00 | 750.00 | UNIQUE TRANSFORMER SERVICE INDUSTRIES
39.00 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc. as required.
39.01 | 250 mm dia. | 150.00 | Mtr. |  | 829.00 | 124350.00 | 700.00 | 105000.00 | 1000.00 | 150000.00 | 1600.00 | 240000.00 | 608.00 | 91200.00 | 91200.00 | AT AND T ENGINEERS PVT LTD
40.00 | Supply & fixing of fire retardant / extinguishing Electrical Insulated synthetic mat of 3 mm thick + 10% conforming to IS 15652: 2006, & other applicable standards, suitable for all voltages upto 33 KV AC and having minimum width of 1000 mm +/- 20 mm and including fixing the same at site by using adhesive/compound as per site requirement. | 25.00 | Sq mtr. |  | 1198.00 | 29950.00 | 1400.00 | 35000.00 | 3000.00 | 75000.00 | 3000.00 | 75000.00 | 1793.00 | 44825.00 | 29950.00 | Konstelec Engineers Pvt. Ltd.
41.00 | Supply & fixing of fire retardant / extinguishing Electrical Insulated synthetic mat of 2 mm thick + 10% conforming to IS 15652: 2006, & other applicable standards, suitable for all voltages upto 3.3 KV AC and having minimum width of 1000 mm +/- 20 mm and including fixing the same at site by using adhesive/compound as per site requirement. | 40.00 | Sq mtr. |  | 1387.00 | 55480.00 | 1200.00 | 48000.00 | 2500.00 | 100000.00 | 1200.00 | 48000.00 | 1230.00 | 49200.00 | 48000.00 | CANELA ENTERPRISES PVT LTD, UNIQUE TRANSFORMER SERVICE INDUSTRIES
42.00 | Supply, Installation, Testing and Commissioning of 500 KVA (Minimum) Silent type D.G Set with DG set controller module mounted on DG set having AMF control, auto synchronizing, auto load sharing, auto load management, inbuilt metering & protection, communicable port (RS485) etc. and acoustic enclosure conforming to latest environment protection regulations for emmission and noise levels complete with Diesel Engine of suitable BHP (considering de-rating factor if any) at 1500 RPM, water cooled, (Radiator type), four stroke, electric start, turbo-charged & after cooled conforming to BS: 5514 with all standard accessories,coupled with Alternator of 500 KVA rating (minimum), brushless, self excited, self regulated and suitable for continuous operation , generating 415 V+/-5% Volts at 0.8 PF ( lag), 50Hz, 3 phase, 4 wire system generally conforming to BS: 2613 & IS: 4722. Both Engine and Alternator shall be mounted on common channel iron base frame, with fuel pipe line upto 10 meter ( to be concealed under floor), exhaust pipe line upto 15 meter ( to be erected with sufficient M.S supports and insulated, hood on top) , Antivibration mountings, residential type silencer, electric starter, batteries & battery charger, fuel tank of 990 ltrs. capacity with level indicator, other standard accessories etc complete as required. ( Refer Technical specification) | 2.00 | Set |  | 4146536.00 | 8293072.00 | 3800000.00 | 7600000.00 | 3500000.00 | 7000000.00 | 3300000.00 | 6600000.00 | 3094341.00 | 6188682.00 | 6188682.00 | AT AND T ENGINEERS PVT LTD
| Total in Figures |  |  |  |  | 36503501.00 |  | 36491112.00 |  | 33648874.00 |  | 41826100.00 |  | 33762131.00
Lowest Amount Quoted BY: PRAGYA ELECTRIC AND ELECTRONICS CORPORATION(33648874.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of Technical Block cum Control Tower at Gaya Airport, Gaya. SH Provision of D.G Sets and substation equipments Tender ID: 2020_AAI_43578_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION | 33648874.00 | L1
| 2 | AT AND T ENGINEERS PVT LTD | 33762131.00 | L2
| 3 | UNIQUE TRANSFORMER SERVICE INDUSTRIES | 36491112.00 | L3
| 4 | Konstelec Engineers Pvt. Ltd. | 36503501.00 | L4
| 5 | CANELA ENTERPRISES PVT LTD | 41826100.00 | L5