## BoQ1
Government eProcurement System Created By: RAJITH V Created Date/Time: 13-Mar-2020 04:35 PM Tender Title: ARMO Works of E and M Instalaltions at Madurai Airport for 2019 2020 SH Miscellaneous Electrical Repair Works at Madurai Airport Tender ID: 2020_AAI_44235_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work: ARMO Works of E&M Installations at Madurai Airport for 2019-20. SH: Miscellaneous Electrical Repair Works at Madurai Airport.
Contract No: AAI/MDU/E-E/MDU-271/NIT-15/2019-20
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DElite System Engineering (India) Pvt. Ltd. |  | Shantha ELectricals and Engineers Pvt Ltd
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation, testing & commissioning of TN 250D 8way prewired TPN SMDB of sheet steel for 415 volts on Surface/recess complete with bottom cabling box, Side Cabling box on both sides,top & bottom corner boxes, metering box, Comprising of Ammeter, Voltmeter, Selector Switch, RYB Indicating lamp terminal connectors for all incoming and out going circuits, duly prewired with suitable size aluminium bus bar, neutral link, earth bar, interconnections, Powder coated including earthing etc. as required with the following: (Make: L&T) a) Incomer - 1 no 3 pole 250A MCCB - Suitable for above Enclosure b) Outgoing - 3nos 3 Pole 32A MCCB, 3nos 3 pole 63A MCCB, 2 nos 3 pole 100A MCCB - Suitable for above Enclosure | 1.00 | Each |  | 105000.00 | 105000.00 | 72000.00 | 72000.00 | 72000.00 | Shantha ELectricals and Engineers Pvt Ltd
2.00 | Supply of XLPE insulated PVC sheathed, armoured Aluminium conductor power cable of 1.1 KV grade of following size etc as per IS 7098 part I 1988 with uptodate amendments etc. for complete as required. a)3.5C X 35 Sq.mm | 55.00 | Mtrs |  | 189.00 | 10395.00 | 160.00 | 8800.00 | 8800.00 | Shantha ELectricals and Engineers Pvt Ltd
3.00 | Supply of XLPE insulated PVC sheathed, armoured Aluminium conductor power cable of 1.1 KV grade of following size etc as per IS 7098 part I 1988 with uptodate amendments etc. for complete as required. b)4C X 25 Sq.mm | 90.00 | Mtrs |  | 169.00 | 15210.00 | 150.00 | 13500.00 | 13500.00 | Shantha ELectricals and Engineers Pvt Ltd
4.00 | Supply of XLPE insulated PVC sheathed, armoured Aluminium conductor power cable of 1.1 KV grade of following size etc as per IS 7098 part I 1988 with uptodate amendments etc. for complete as required. c)4C X 16 Sq.mm | 470.00 | Mtrs |  | 129.00 | 60630.00 | 120.00 | 56400.00 | 56400.00 | Shantha ELectricals and Engineers Pvt Ltd
5.00 | Supply of XLPE insulated PVC sheathed, armoured Aluminium conductor power cable of 1.1 KV grade of following size etc as per IS 7098 part I 1988 with uptodate amendments etc. for complete as required. d)3C X 6 Sq.mm | 160.00 | Mtrs |  | 99.00 | 15840.00 | 75.00 | 12000.00 | 12000.00 | Shantha ELectricals and Engineers Pvt Ltd
6.00 | Supply of 50mm dia DWC HDPE pipe conforming to IS: 14930- (part-II) with latest amentments complete with accessories like couplers, bends, "T" etc. as required. ( OD-50mm & ID 38 mm nominal) | 400.00 | Mtrs |  | 109.00 | 43600.00 | 80.00 | 32000.00 | 32000.00 | Shantha ELectricals and Engineers Pvt Ltd
7.00 | Supply of PE 80 HDPE pipe (PN-6) of 75 mm dia with all necessary accessories including testing of joints complete as required. | 50.00 | Mtrs |  | 190.00 | 9500.00 | 390.00 | 19500.00 | 9500.00 | DElite System Engineering (India) Pvt. Ltd.
8.00 | Laying of 50mm dia DWC HDPE pipe direct in ground (minimum 60 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. complete as required. | 445.00 | Mtrs |  | 120.00 | 53400.00 | 200.00 | 89000.00 | 53400.00 | DElite System Engineering (India) Pvt. Ltd.
9.00 | Laying of 75mm dia HDPE pipe direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. complete as required. | 50.00 | Mtrs |  | 150.00 | 7500.00 | 210.00 | 10500.00 | 7500.00 | DElite System Engineering (India) Pvt. Ltd.
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/METAL/GI/ HDPE/DWC pipe etc. complete as required. Up to 35 sq.mm | 520.00 | Mtrs |  | 50.00 | 26000.00 | 50.00 | 26000.00 | 26000.00 | Shantha ELectricals and Engineers Pvt Ltd, DElite System Engineering (India) Pvt. Ltd.
11.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/METAL/GI/ HDPE/DWC pipe etc. complete as required. Above 95 sq. mm and upto 185 sq. mm | 50.00 | Mtrs |  | 50.00 | 2500.00 | 75.00 | 3750.00 | 2500.00 | DElite System Engineering (India) Pvt. Ltd.
12.00 | Laying and fixing of one number PVC insulated and PVC sheathed I XLPE power cable of 1.1 kV grade of following size on wall surface as required. Up to 35 sq. mm (clamped with 1mm thick saddle) | 171.00 | Mtrs |  | 70.00 | 11970.00 | 85.00 | 14535.00 | 11970.00 | DElite System Engineering (India) Pvt. Ltd.
13.00 | Supply and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade etc. complete as required. A) 3.5C X 185 Sq.mm | 4.00 | Set |  | 900.00 | 3600.00 | 560.00 | 2240.00 | 2240.00 | Shantha ELectricals and Engineers Pvt Ltd
14.00 | Supply and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade etc. complete as required. B) 3.5C X 35 Sq.mm | 4.00 | Set |  | 750.00 | 3000.00 | 275.00 | 1100.00 | 1100.00 | Shantha ELectricals and Engineers Pvt Ltd
15.00 | Supply and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade etc. complete as required. C) 4C X 25 Sq.mm | 4.00 | Set |  | 750.00 | 3000.00 | 240.00 | 960.00 | 960.00 | Shantha ELectricals and Engineers Pvt Ltd
16.00 | Supply and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade etc. complete as required. D)4C X 16 Sq.mm | 108.00 | Set |  | 400.00 | 43200.00 | 250.00 | 27000.00 | 27000.00 | Shantha ELectricals and Engineers Pvt Ltd
17.00 | Supply and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade etc. complete as required. E)3C X 6 Sq.mm | 6.00 | Set |  | 500.00 | 3000.00 | 175.00 | 1050.00 | 1050.00 | Shantha ELectricals and Engineers Pvt Ltd
18.00 | Dismantling of existing pole mounted SMC box & Supply and fixing of New SMC box of size (L=250 X W=200 X D=105 mm) with suitable accessories including 63A connectors,DIN channel,supply, installation, testing & commissioning of 10A SP C seris MCB, excavation of existing cable present below ground surface near the pole and pulling the cable up,cutting off existing End termination and refilling the excavated portion etc. complete as required. (Make: Sintex) | 50.00 | Job |  | 2000.00 | 100000.00 | 2050.00 | 102500.00 | 100000.00 | DElite System Engineering (India) Pvt. Ltd.
19.00 | Supply and fixing PVC Synthetic elastomer electrically insulating mat with class A insulation conforming to IS :15652-2006 & CPRI tested having 2 mm thickness upto 3.3 KV,This scope also includes dismantling the existing insulation mats at areas wherever required. | 25.00 | Sq.mtr |  | 1000.00 | 25000.00 | 850.00 | 21250.00 | 21250.00 | Shantha ELectricals and Engineers Pvt Ltd
20.00 | Supply and fixing of nominal 2.5mm +/- 10% thick electric insulated synthetic Mat conforming to IS: 15652 : 2006 & CPRI tested suitable for class - C upto 33KV, 415V AC supply etc. Complete as required.This scope also includes dismantling the existing insulation mats at areas wherever required. | 40.00 | Sq.mtr |  | 1250.00 | 50000.00 | 950.00 | 38000.00 | 38000.00 | Shantha ELectricals and Engineers Pvt Ltd
21.00 | Painting of Transformers along with supporting structures at Madurai Airport with enamel paint of required colour (2 coats), approved brand as required. (Approximate 5.0 Sq.m) | 2.00 | Job |  | 15000.00 | 30000.00 | 1250.00 | 2500.00 | 2500.00 | Shantha ELectricals and Engineers Pvt Ltd
22.00 | Painting of Feeder pillars along with supporting structures at Madurai Airport with enamel paint of required colour (2 coats), approved brand as required. (Approximate 3.0 Sq.m) | 13.00 | Job |  | 3500.00 | 45500.00 | 780.00 | 10140.00 | 10140.00 | Shantha ELectricals and Engineers Pvt Ltd
23.00 | Painting of Junction Boxs along with supporting structures at Madurai Airport with enamel paint of required colour (2 coats), approved brand as required. (Approximate 1.50 sq.m) | 40.00 | Job |  | 2000.00 | 80000.00 | 400.00 | 16000.00 | 16000.00 | Shantha ELectricals and Engineers Pvt Ltd
24.00 | Pin pointing the fault of the cable like , earth fault , open circuit fault etc , by means of portable fault locator at Madurai Airport. | 3.00 | Nos |  | 45000.00 | 135000.00 | 15000.00 | 45000.00 | 45000.00 | Shantha ELectricals and Engineers Pvt Ltd
25.00 | Excavation of trenches in all kinds of soils for cables/ pipes upto 120 mm dia to a depth of 0.75m meter including refilling the trench and disposal of surplus soil etc as required. | 100.00 | Cum |  | 1200.00 | 120000.00 | 400.00 | 40000.00 | 40000.00 | Shantha ELectricals and Engineers Pvt Ltd
26.00 | Excavation of trenches in ordinary rock for cables/ pipes upto 120 mm dia up to a depth of 0.75 meter including refilling the trench and disposal of surplus soil etc as required. | 50.00 | Cum |  | 1000.00 | 50000.00 | 500.00 | 25000.00 | 25000.00 | Shantha ELectricals and Engineers Pvt Ltd
27.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (but with charcoal/ coke and salt ) as required. | 4.00 | sets |  | 13000.00 | 52000.00 | 7000.00 | 28000.00 | 28000.00 | Shantha ELectricals and Engineers Pvt Ltd
28.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling etc. as required | 150.00 | Mtrs |  | 200.00 | 30000.00 | 80.00 | 12000.00 | 12000.00 | Shantha ELectricals and Engineers Pvt Ltd
29.00 | Providing and laying 6 SWG G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 625.00 | Mtrs |  | 30.00 | 18750.00 | 50.00 | 31250.00 | 18750.00 | DElite System Engineering (India) Pvt. Ltd.
30.00 | Supply, Installation, testing and commissioning of three phase surge & transient protection (MOV, Plug in type capable of carrying nominal discharge of 100KA, 9 block MOV), 8/20 Micro Second surge rating provides protection suitable for main distribution panels and an extended operational life etc. as per required. | 1.00 | Each |  | 24000.00 | 24000.00 | 90000.00 | 90000.00 | 24000.00 | DElite System Engineering (India) Pvt. Ltd.
31.00 | SITC of 2HP single stage, high speed, horizontal centrifugal open well submersible pump monobloc with volute type delivery casing alongwith 10 meter flat submersible pump power cable through 25mm dia PVC pipe for operation on single phase 230V, 50HZ, AC Supply, Head range-8 to 16 mtr, Discharge range-11 LPS to 4 LPS, having Delivery opening 50mm dia etc. complete as required.Including Supply & Fixing of DOL Starter suitable for above Pump consisting of contactor, thermal overload relay ON-OFF Push button etc in sheet steel enclosure etc. | 1.00 | Job |  | 25000.00 | 25000.00 | 20000.00 | 20000.00 | 20000.00 | Shantha ELectricals and Engineers Pvt Ltd
32.00 | Supply of UL listed Intelligent addressable optical smoke detector with standard base, accessories like base, base box etc., to install under/above false ceilling, roof and concealed space etc. Complete as required as per Specification.(Honey Well,Model No: SD 355) | 2.00 | Each |  | 2500.00 | 5000.00 | 2800.00 | 5600.00 | 5000.00 | DElite System Engineering (India) Pvt. Ltd.
33.00 | Supply of strobs cum hooters (Specification: 110 cd light & 85 db with adjustable DB) at different locations complete with all fixing accessories etc., under false ceiling roof, wall etc., interconnecting to loop cable complete as required. (Honey Well,Model No: SYSHS) | 2.00 | Each |  | 3000.00 | 6000.00 | 7700.00 | 15400.00 | 6000.00 | DElite System Engineering (India) Pvt. Ltd.
34.00 | Supply of Intelligent addressable control module for activating hooters in loop complete etc., to be installed under/above false ceiling, roof and concealed space etc. as required. (Make: Honey Well,Model No:CMF-300) | 2.00 | Each |  | 3000.00 | 6000.00 | 3750.00 | 7500.00 | 6000.00 | DElite System Engineering (India) Pvt. Ltd.
35.00 | Supply of Microcontroller based Auto dialler, 12V or 24V DC Supply,On board key pad with 2 lines LCD Display, Triggering:normally open , Triggering inputs- 2, Voice Message length :25 sec each channel, Telephone landline communication, Response time 25 Milli Sec ,Storage Capacity : Maximum upto 20 Numbers etc. complete as required. (Model No: EBT-ADLL02) Make:Eborntech | 1.00 | Each |  | 7000.00 | 7000.00 | 12000.00 | 12000.00 | 7000.00 | DElite System Engineering (India) Pvt. Ltd.
36.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed XLPE aluminium conductor cable of 1.1 kV grade as required. A)3.5C X 185 Sq.mm | 2.00 | Set |  | 7500.00 | 15000.00 | 4850.00 | 9700.00 | 9700.00 | Shantha ELectricals and Engineers Pvt Ltd
37.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed XLPE aluminium conductor cable of 1.1 kV grade as required. B)3.5C X 95 Sq.mm | 2.00 | Set |  | 6500.00 | 13000.00 | 3350.00 | 6700.00 | 6700.00 | Shantha ELectricals and Engineers Pvt Ltd
38.00 | Dismantling of existing junction box and installation of thermoplastic poly carbonate junction box after excavating the soil up to a depth of 1m, preparation of foundation using 1:2:4 in position cement concrete with 20 mm stone aggrgate and concreting the surroundings for 1 sqmtr,nuts,bolts etc complete as per direction of EIC. | 2.00 | Job |  | 3000.00 | 6000.00 | 4000.00 | 8000.00 | 6000.00 | DElite System Engineering (India) Pvt. Ltd.
39.00 | Supply and fixing of SMC box of size (L=250 X W=200 X D=105 mm) with suitable accessories including 63A connectors,DIN channel,supply, installation, testing & commissioning of 10A SP C seris MCB, etc. complete as required. (Make: Sintex) | 3.00 | Each |  | 2500.00 | 7500.00 | 2800.00 | 8400.00 | 7500.00 | DElite System Engineering (India) Pvt. Ltd.
40.00 | Supply and fixing of SMC box of size (L=240 X W=140 X D=95 mm) with suitable accessories including 63A connectors,DIN channel,supply, installation, testing & commissioning of 10A SP C seris MCB, etc. complete as required. (Make: Sintex) | 4.00 | Each |  | 2300.00 | 9200.00 | 2150.00 | 8600.00 | 8600.00 | Shantha ELectricals and Engineers Pvt Ltd
41.00 | Dismantling of Existing cross arm, Supply & installation of new single end cross arm of 1.5 metr length on existing pole & installation of 90W LED fitting with suitable adaptors for fixing street lights, suitable wiring complete from SMC box to lighting etc. complete as required. | 14.00 | Each |  | 3200.00 | 44800.00 | 1500.00 | 21000.00 | 21000.00 | Shantha ELectricals and Engineers Pvt Ltd
42.00 | Painting of 9 mtr octogonal pole along with single end cross arm, SMC box supporting structures at Madurai Airport with enamel paint of required colour (2 coats), approved brand as required. | 14.00 | Job |  | 2200.00 | 30800.00 | 900.00 | 12600.00 | 12600.00 | Shantha ELectricals and Engineers Pvt Ltd
43.00 | Supply of high effiency LED street light fittings of 90W or better as per technical specification enclosed in Annexure - I for New VIP Gate Approach road light fitting compound wall etc. as required. | 14.00 | Each |  | 5999.00 | 83986.00 | 4500.00 | 63000.00 | 63000.00 | Shantha ELectricals and Engineers Pvt Ltd
| Total in Figures |  |  |  |  | 1436881.00 |  | 1050475.00
Lowest Amount Quoted BY: Shantha ELectricals and Engineers Pvt Ltd(1050475.00)

## BOQ Summary
BOQ Summary Details Tender Title: ARMO Works of E and M Instalaltions at Madurai Airport for 2019 2020 SH Miscellaneous Electrical Repair Works at Madurai Airport Tender ID: 2020_AAI_44235_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Shantha ELectricals and Engineers Pvt Ltd | 1050475.00 | L1
| 2 | DElite System Engineering (India) Pvt. Ltd. | 1436881.00 | L2