## BoQ1
Government eProcurement System Created By: MANTRIMAYUM CHINGLENSANA SINGH Created Date/Time: 01-May-2020 01:24 PM Tender Title: Provision of power supply from ASR and MSSR substation to LLZ DVOR and perimeter lighting at Imphal Airport Tender ID: 2020_AAI_44608_1
Tender Inviting Authority: Asst GM Engg.(Electrical)-II, AAI,Imphal
Name of work:- Provision of power supply from ASR/MSSR substation to LLZ, DVOR and perimeter lighting, Imphal Airport.
Contract No: 2020_AAI_44608_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Nongpok Enterprises |  | Md Kheiruddin |  | KHARIBAM MAIMUSINGH
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of LT power cable of 1.1kV grade of following size aluminium conductor XLPE insulated PVC sheathed armoured cable conforming to IS 7098 Part-1 1988 with upto date amendments as required. 3.5 x 185 Sqmm. | 915.00 | Mtr. | 0.00 | 900.00 | 823500.00 | 700.00 | 640500.00 | 827.00 | 756705.00 | 640500.00 | Md Kheiruddin
2.00 | Supply of LT power cable of 1.1kV grade of following size aluminium conductor XLPE insulated PVC sheathed armoured cable conforming to IS 7098 Part-1 1988 with upto date amendments as required. 3.5 x 300 Sqmm. | 386.00 | Mtr. | 0.00 | 1250.00 | 482500.00 | 850.00 | 328100.00 | 1200.00 | 463200.00 | 328100.00 | Md Kheiruddin
3.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size above 185 sq. mm and upto 400 sq. mm in the existing masonry open duct as required. | 40.00 | Mtr. | 0.00 | 150.00 | 6000.00 | 82.00 | 3280.00 | 140.00 | 5600.00 | 3280.00 | Md Kheiruddin
4.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/DWC HDPE/ METAL pipe as required. Above 95 sq. mm and upto 185 sq. mm. | 835.00 | Mtr. | 0.00 | 40.00 | 33400.00 | 70.00 | 58450.00 | 40.00 | 33400.00 | 33400.00 | Nongpok Enterprises, KHARIBAM MAIMUSINGH
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/DWC HDPE/ METAL pipe as required. Above 185 sq. mm and upto 400 sq. mm. | 306.00 | Mtr. | 0.00 | 110.00 | 33660.00 | 94.00 | 28764.00 | 100.00 | 30600.00 | 28764.00 | Md Kheiruddin
6.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 20.00 | Nos. | 0.00 | 700.00 | 14000.00 | 710.00 | 14200.00 | 700.00 | 14000.00 | 14000.00 | Nongpok Enterprises, KHARIBAM MAIMUSINGH
7.00 | Supplying and making end termination with double compression brass gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 x 25 sq. mm (28mm). | 2.00 | Nos. | 0.00 | 390.00 | 780.00 | 320.00 | 640.00 | 320.00 | 640.00 | 640.00 | KHARIBAM MAIMUSINGH, Md Kheiruddin
8.00 | Supplying and making end termination with double compression brass gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ x 120 sq. mm (45mm). | 1.00 | No. | 0.00 | 405.00 | 405.00 | 470.00 | 470.00 | 350.00 | 350.00 | 350.00 | KHARIBAM MAIMUSINGH
9.00 | Supplying and making end termination with double compression brass gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ x 185 sq. mm (57mm). | 7.00 | Nos. | 0.00 | 532.00 | 3724.00 | 660.00 | 4620.00 | 500.00 | 3500.00 | 3500.00 | KHARIBAM MAIMUSINGH
10.00 | Supplying and making end termination with double compression brass gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ x 300 sq. mm (70mm). | 4.00 | Nos. | 0.00 | 799.00 | 3196.00 | 870.00 | 3480.00 | 750.00 | 3000.00 | 3000.00 | KHARIBAM MAIMUSINGH
11.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ x 185 sq. mm. | 2.00 | Nos. | 0.00 | 3000.00 | 6000.00 | 3600.00 | 7200.00 | 2800.00 | 5600.00 | 5600.00 | KHARIBAM MAIMUSINGH
12.00 | Supplying and laying of size 90 mm dia (OD-90 mm & ID-76 mm nominal) Type/Code 450 DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 16205, Part 24 complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 948.00 | Mtr. | 0.00 | 200.00 | 189600.00 | 250.00 | 237000.00 | 170.00 | 161160.00 | 161160.00 | KHARIBAM MAIMUSINGH
13.00 | Supplying and laying of size 90 mm dia (OD-90 mm & ID-76 mm nominal) Type/Code 450 DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 16205, Part 24 complete with fitting and cutting, jointing etc. in the existing trench, complete as required. | 193.00 | Mtr. | 0.00 | 242.00 | 46706.00 | 240.00 | 46320.00 | 210.00 | 40530.00 | 40530.00 | KHARIBAM MAIMUSINGH
14.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 6.00 | Nos. | 0.00 | 4502.00 | 27012.00 | 5500.00 | 33000.00 | 4370.00 | 26220.00 | 26220.00 | KHARIBAM MAIMUSINGH
15.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 21.00 | Mtr. | 0.00 | 425.00 | 8925.00 | 660.00 | 13860.00 | 395.00 | 8295.00 | 8295.00 | KHARIBAM MAIMUSINGH
16.00 | Constructing masonry Chamber 30x30x50 cm inside, in brick work in cement mortar 1:4 (1 cement :4 coarse sand) for stop cock, with C. I. surface box 100x100 x75 mm (inside) with hinged cover fixed in cement concrete slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), i/c necessary excavation, foundation concrete 1:5:10 ( 1 cement : 5 fine sand : 10 graded stone aggregate 40mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12mm thick, finished with a floating coat of neat cement complete as per standard design, With common burnt clay F.P.S. (non modular) bricks of class designation 7.5. | 2.00 | Nos. | 0.00 | 2000.00 | 4000.00 | 2000.00 | 4000.00 | 1900.00 | 3800.00 | 3800.00 | KHARIBAM MAIMUSINGH
17.00 | Excavation of the cable trenches in cement concrete platform not exceeding 1.5metres in width, and lift upto 1.5 metres, including getting outthe excavated soil and disposal of excavated soil as directedwithin a lead of 50 metres. | 10.50 | Cum. | 0.00 | 702.00 | 7371.00 | 880.00 | 9240.00 | 750.00 | 7875.00 | 7371.00 | Nongpok Enterprises
18.00 | Supply, Installation, Testing and Commissioning of cubicle type LT panel, as per IEC 61439-1 & IEC 61439-2, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, shall be mounted on cement concrete foundations over suitable height MS angle base frame i/c grouting the stand with concrete mortar (As per standard or directed by EIC) ................... as per specifications. Mechanical interlocking arrangement to be provided between incomers and bus-coupler. Incomer- 2 Nos.: 400A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c rotary magnetic handle, R,Y,B indication lamp- 1 Set, ON, OFF, TRIP indication lamp- Each 1 no., 2A SP 10kA control MCB, digital voltmeter, digital ammeter with suitable ratio CTs of class 1.0 accuracy. Buscoupler: 400A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c rotary magnetic handle, R,Y,B indication lamp- 1 Set, ON, OFF, TRIP indication lamp- Each 1 no. Outgoing-4 Nos.: 250A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c rotary magnetic handle, ON, OFF, TRIP indication lamp- Each 1 no. Busbar: TPN Aluminium alloy bus bars for high conductivity - 400A Rating. | 1.00 | No. | 0.00 | 328298.00 | 328298.00 | 400000.00 | 400000.00 | 320750.00 | 320750.00 | 320750.00 | KHARIBAM MAIMUSINGH
19.00 | Supply, Installation, Testing and Commissioning of cubicle type LT panel, as per IEC 61439-1 & IEC 61439-2, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, shall be mounted on cement concrete foundations over suitable height MS angle base frame i/c grouting the stand with concrete mortar(As per standard or directed by EIC) ............. cable alley with required size of AL conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, i/c providing following switchgears / accessories as per specifications. Mechanical interlocking arrangement to be provided between incomers. Incomer- 2 Nos.: 250A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c rotary magnetic handle, R,Y,B indication lamp- 1 Set, ON, OFF, TRIP indication lamp- Each 1 no., 2A SP 10kA control MCB, digital voltmeter, digital ammeter with suitable ratio CTs of class 1.0 accuracy. Outgoing-2 Nos.: 125A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c rotary magnetic handle, ON, OFF, TRIP indication lamp- Each 1 no. Outgoing-2 Nos.: 63A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c rotary magnetic handle, ON, OFF, TRIP indication lamp- Each 1 no. Busbar: TPN Aluminium alloy bus bars for high conductivity - 250A Rating . | 1.00 | No. | 0.00 | 228792.00 | 228792.00 | 300000.00 | 300000.00 | 217092.00 | 217092.00 | 217092.00 | KHARIBAM MAIMUSINGH
20.00 | Strutural steel work revited, bolted or welded in built up section, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 1350.00 | Kg. | 0.00 | 200.00 | 270000.00 | 180.00 | 243000.00 | 250.00 | 337500.00 | 243000.00 | Md Kheiruddin
21.00 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-charge) 0.50mm (+0.05%) total coated thickness with zinc coating 120 grams per sqm as per IS:277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimun to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5 * 55mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or cueved surfaces, excluding the cost of purlins, rathers and trusss and including cutting to sixe and shape wherever required. | 30.00 | Sqm | 0.00 | 700.00 | 21000.00 | 920.00 | 27600.00 | 645.00 | 19350.00 | 19350.00 | KHARIBAM MAIMUSINGH
22.00 | Providing and fixing precoated galvanised steel sheet roofing accessories 0.50mm(+0.05%) total coated thickness, zinc coating 120 grams per sqm as per IS:277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and poluester top coat 15-18 microns usiong self drilling/ self tapping screws complete: Ridges plain (500 - 600mm). | 8.00 | Mtr. | 0.00 | 627.00 | 5016.00 | 620.00 | 4960.00 | 690.00 | 5520.00 | 4960.00 | Md Kheiruddin
23.00 | Providing and laying in position cement concrete of specified grade excludingthe cost of centering and shuttering - All work up to plinth level 1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40mm nominal size. | 4.00 | Cum. | 0.00 | 7000.00 | 28000.00 | 8000.00 | 32000.00 | 7645.00 | 30580.00 | 28000.00 | Nongpok Enterprises
24.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more. | 320.00 | Kg. | 0.00 | 80.00 | 25600.00 | 160.00 | 51200.00 | 90.00 | 28800.00 | 25600.00 | Nongpok Enterprises
25.00 | Providing and fixing up to floor five level precast cement concrete string or lacing courses, copings, bed plates, anchor blocks, plain window sills, shelves, louvers, steps, stair cases, etc., including hoisting and setting in position with cement mortar 1:3 (1 Cement : 3 coarse sand), cost of required Centering complete. 1:1.5:3 (1 Cement : 1.5 coarse sand(zone-III) : 3 graded stone aggregate 20mm nominal size). | 5.00 | Cum. | 0.00 | 15209.00 | 76045.00 | 11000.00 | 55000.00 | 14990.00 | 74950.00 | 55000.00 | Md Kheiruddin
| Total in Figures |  |  |  |  | 2673530.00 |  | 2546884.00 |  | 2599017.00
Lowest Amount Quoted BY: Md Kheiruddin(2546884.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of power supply from ASR and MSSR substation to LLZ DVOR and perimeter lighting at Imphal Airport Tender ID: 2020_AAI_44608_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Md Kheiruddin | 2546884.00 | L1
| 2 | KHARIBAM MAIMUSINGH | 2599017.00 | L2
| 3 | Nongpok Enterprises | 2673530.00 | L3