## BoQ1
Government eProcurement System Created By: Yugal Kishor Created Date/Time: 03-Jul-2020 03:49 PM Tender Title: Provision of Cold Storage Room for Cargo Building at Jaipur Airport Tender ID: 2020_AAI_50207_1
Tender Inviting Authority: Asstt. General Manager (Engg-Electrical), Jaipur Airport.
Name of Work: Provision of Cold Storage Rooms for Cargo Building at Jaipur Airport.
Contract No: 2020_AAI_50207_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Airtech Cooling Process Pvt Ltd |  | Winchester Enterprises |  | Superior Aircon Pvt. Ltd. |  | ASVA COOL SOLUTIONS PVT LTD |  | CLIMATROL CORPORATION |  | Metro International
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, fabrication, supply, installation, testing and commissioning of Combo Cold Storage Room (L- 4.00 mtr x W- 4.00 mtr x H- 3.00 mtr) consisting of Chiller Room (L- 2.25 mtr x W- 4.00 mtr x H- 3.00 mtr) and Freezer Room (L- 1.75 mtr x W- 4.00 mtr x H- 3.00 mtr) as per actual site conditions. The Chiller Room should be suitable to maintain inside temperature range +2°C to +15°C on 48°C ambient temperature by providing one number air cooled chilling unit, 15000BTU/Hr (nominal) Scroll/ Rotary/ Reciprocating Compressor, green gas (R-404a, 407a, 134a etc.),evaporating (indoor) unit, individual control panel unit etc. complete as required. The Freezer Room should be maintain inside temperature range -25°C to +0°C on 48°C ambient temperature by providing one number air cooled 8000BTU/Hr (nominal) Scroll/ Rotary/ Reciprocating Compressor, green gas (R-404a, 407a, 134a etc.) evaporating (indoor) unit, individual control panel unit etc. complete as required. The Chiller Room is to be fabricated with 60 mm thickness of PUF panel covered with 0.51 mm (24 SWG) Stainless Steel (SS 304) on both sides and Freezer Room with 100 mm thickness of PUF panel covered with 0.51 mm (24 SWG), GI antiskid/ chequred plate flooring, suitable installation/ fixing arrangement for indoor & outdoor units, minor civil works, wiring, all other components/ accessories etc. suitable for operation on 415/230V, 50Hz etc. complete as required. | 2.00 | Each | 100.00 | 961000.00 | 1922000.00 | 729000.00 | 1458000.00 | 910000.00 | 1820000.00 | 964735.00 | 1929470.00 | 715849.26 | 1431698.52 | 880000.00 | 1760000.00 | 1431698.52 | CLIMATROL CORPORATION
2.00 | Design, fabrication, supply, installation, testing and commissioning of Combo Cold Storage Room (L- 5.00 mtr x W- 3.00 mtr x H- 3.00 mtr) consisting of Chiller Room (L- 3.00 mtr x W- 3.00 mtr x H- 3.00 mtr) and Freezer Room (L- 2.00 mtr x W- 3.00 mtr x H- 3.00 mtr) as per actual site conditions. The Chiller Room should be suitable to maintain inside temperature range +2°C to +15°C on 48°C ambient temperature by providing one number air cooled chilling unit, 15000BTU/Hr (nominal) Scroll/ Rotary/ Reciprocating Compressor, green gas (R-404a, 407a, 134a etc.),evaporating (indoor) unit, individual control panel unit etc. complete as required. The Freezer Room should be maintain inside temperature range -25°C to +0°C on 48°C ambient temperature by providing one number air cooled 8000BTU/Hr (nominal) Scroll/ Rotary/ Reciprocating Compressor, green gas (R-404a, 407a, 134a etc.) evaporating (indoor) unit, individual control panel unit etc. complete as required. The Chiller Room is to be fabricated with 60 mm thickness of PUF panel covered with 0.51 mm (24 SWG) Stainless Steel (SS 304) on both sides and Freezer Room with 100 mm thickness of PUF panel covered with 0.51 mm (24 SWG), GI antiskid/ chequred plate flooring, suitable installation/ fixing arrangement for indoor & outdoor units, minor civil works, wiring, all other components/ accessories etc. suitable for operation on 415/230V, 50Hz etc. complete as required. | 2.00 | Each | 10.00 | 940000.00 | 1880000.00 | 743000.00 | 1486000.00 | 910000.00 | 1820000.00 | 929735.00 | 1859470.00 | 725129.26 | 1450258.52 | 860000.00 | 1720000.00 | 1450258.52 | CLIMATROL CORPORATION
3.00 | Supply, installation, testing and commissioning of interconnecting copper refrigerant pipes of 12.7 mm (OD 1/2 Inch), 0.80 mm wall thickness & 9.50 mm (OD 3/8 inch), 0.80 mm wall thickness with 13mm insulation or OEM's standard along with 4C x 4.00 sqmm FRLS PVC copper conductor cables between freezer's indoor and outdoor units duly insulated with closed cell elastomeric nitrile rubber type tubular insulation of nominal thickness as per OEM's standard including fixing arrangements etc. as per site requirement. | 90.00 | Mtr | 10.00 | 1350.00 | 121500.00 | 460.00 | 41400.00 | 1500.00 | 135000.00 | 750.00 | 67500.00 | 1250.00 | 112500.00 | 950.00 | 85500.00 | 41400.00 | Winchester Enterprises
4.00 | Supply, installation, testing and commissioning of interconnecting copper refrigerant pipes of 15.9 mm (OD 5/8 inch), 1.00 mm wall thickness & 9.5 mm (OD 3/8 Inch), 0.80 mm wall thickness with 13mm insulation or OEM's standard along with 3C x 4.00 sqmm FRLS PVC copper conductor cables between chiller's indoor and outdoor units duly insulated with closed cell elastomeric nitrile rubber type tubular insulation of nominal thickness as per OEM's standard including fixing arrangements etc. as per site requirement. | 90.00 | Mtr | 10.00 | 1600.00 | 144000.00 | 545.00 | 49050.00 | 1600.00 | 144000.00 | 650.00 | 58500.00 | 1250.00 | 112500.00 | 1020.00 | 91800.00 | 49050.00 | Winchester Enterprises
5.00 | Supply, installation, testing and commissioning of 25 mm hard PVC drain piping complete with fittings, supports, valve and 6 mm thick closed nitrile rubber foam insulation complete as required. | 100.00 | Mtr | 10.00 | 193.00 | 19300.00 | 86.00 | 8600.00 | 90.00 | 9000.00 | 125.00 | 12500.00 | 20.00 | 2000.00 | 110.00 | 11000.00 | 2000.00 | CLIMATROL CORPORATION
| Total in Figures |  |  |  |  | 4086800.00 |  | 3043050.00 |  | 3928000.00 |  | 3927440.00 |  | 3108957.04 |  | 3668300.00
Lowest Amount Quoted BY: Winchester Enterprises(3043050.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Cold Storage Room for Cargo Building at Jaipur Airport Tender ID: 2020_AAI_50207_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Winchester Enterprises | 3043050.00 | L1
| 2 | CLIMATROL CORPORATION | 3108957.04 | L2
| 3 | Metro International | 3668300.00 | L3
| 4 | ASVA COOL SOLUTIONS PVT LTD | 3927440.00 | L4
| 5 | Superior Aircon Pvt. Ltd. | 3928000.00 | L5
| 6 | Airtech Cooling Process Pvt Ltd | 4086800.00 | L6