## BoQ1
Government eProcurement System Created By: MANTRIMAYUM CHINGLENSANA SINGH Created Date/Time: 14-Sep-2020 03:11 PM Tender Title: Installation, Replacement of ILS at Imphal International Airport. SH. Electrical Works Tender ID: 2020_AAI_50441_2
Tender Inviting Authority: AGM (E-E)-I
Name of Work: Installation (Replacement ) of ILS at Imphal International Airport. SH: Electrical Works
Contract No: 2020_AAI_50441_2
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SRI RAJARAJESHWARI ELECTRICALS(GSTN-29AINPB0160H2ZG)
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | A: MV panel
2.00 | Supply, Installation, Testing and Commissioning of cubicle type LT panel suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply system, IP 42 fabricated in modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, SMC bus bar supports, with short circuit withstand capacity of 35KA for 1 sec, bottom base channel of MS section not less than 400 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of size 50 mm x 6 mm at the rear with 2 Nos. earth stud, solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination in cable alley with required size of AL conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, i/c providing following switchgears / accessories as per specifications. Incomer: 100A, 25KA, 4P MCCB with Microprocessor based releases as incomer with R,Y,B,ON,OFF, Trip indication lamps, resin cast CT's with multifuction meter ( Schheider EM 6459 or Equivalent)-2 sets. Buscoupler: 100A, 25KA, 4P MCCB with Microprocessor based releases as buscoupler with R,Y,B, ON, OFF and three locks two key mechanical interlock- 1 set Outgoing: 63A, 36KA, 4P MCCB with microprocessor based releases with ON, OFF, Trip indication lamps as outgoing with digital ammeter and surge protection Device (class C, Type-2) - 4 sets. Spare compartment: suitable for providing 63 A 4P MCCB with all necessary arrangements etc complete as required - 2 Nos. Provision for feeding Mobile DG 25 KVA supply plug point for emergency purpose-1 No. Primary surge protection: Supply, installation, Testing & commissioning of Block MOV based surge Divertor (BMOVSD) 100 KA, 3 phase, 4 wire class-B, Qty-1 Secondary protection: Supply, Installation, Testing & commissioning of Block MOV based surge divertor 40KA, 3 phase, 4 wire class-B, Qty-1. h) With all necessary accessories including DSITC of suitable isolating switch gear of appropriate rating for surge protectors etc, complete as required. | 2.00 | Job |  | 275000.00 | 550000.00 | 550000.00 | SRI RAJARAJESHWARI ELECTRICALS
3.00 | B: AC & Water Dispensors
4.00 | SITC of 1.5 TR, 5 star rating, Inverter type split A/Cs, Units with R410a Gas. (Both indoor and outdoor units), complete with filters, cooling coils connected to condensing units, including remote control operation for temparature adjustment, indoor unit blower speed, swing adjustment, auto restart, sleep mode turbo mode, with LED display for temparature i/c standard length of copper refrigerant pipe, copper electrical cable & drain pipe first charge of refrigerant, providing raised platform / MS stand for outdoor units etc., complete as required. | 4.00 | Each |  | 55000.00 | 220000.00 | 220000.00 | SRI RAJARAJESHWARI ELECTRICALS
5.00 | Supply, fixing, testing and commisioning of wall mounting type automatic electricnic volatge stablizer suitable for 1.5 TR split Air conditioners having capacity 4 KVA single phase an auto volatge range of 180- 270 V with high/low voltage cut off on delay etc complete as required. (Make: V-Guard, Microtek, APC) | 4.00 | Each |  | 2000.00 | 8000.00 | 8000.00 | SRI RAJARAJESHWARI ELECTRICALS
6.00 | Supply, Installation, Testing and commissioning of water dispenser with RO + UV purification. Storage capacity (upto float level)- 15 ltr. for operation on 230 V, 50 Hz AC supply complete as per technical specification of reputed make.( Make: Kent / Aquaguard). | 2.00 | Each |  | 10000.00 | 20000.00 | 20000.00 | SRI RAJARAJESHWARI ELECTRICALS
7.00 | C: Fire Alarm System
8.00 | Supply, installation, testing and commissioning of UL listed conventional type Photo Elecrtic Smoke Detector with mounting based LED with Electronic Addressing Feature to programme the detectors. Complete as required to be installed under/above false ceiling, roof and concealed space, etc. interconnecting to loop cable complete as required.(UL 9th Edition Approved and NFPA). | 8.00 | Each |  | 2100.00 | 16800.00 | 16800.00 | SRI RAJARAJESHWARI ELECTRICALS
9.00 | Supply, installation, testing and commissioning of UL listed conventional type Manual Call Point (break glass type) complete with Input Module, push button, enclosed in box with provision for cable or conduit coupling, self adhesive sticker indicating loop number and address.The unit to be painted fire red outside, white inside and written 'In case of fire break glass.'(UL 9th Edition Approved and NFPA) | 4.00 | Each |  | 2700.00 | 10800.00 | 10800.00 | SRI RAJARAJESHWARI ELECTRICALS
10.00 | Supplying, installation, testing & commissioning of Response Indicator (METAL CLADE)which consists of steady glowing LED. This LED shall be mounted within a M.S. box and connected in parallel to the built in indicator of the detector as per specifications. The RI shall come "ON" as soon as the detector activates complete in all respects as per specification. | 4.00 | Each |  | 1000.00 | 4000.00 | 4000.00 | SRI RAJARAJESHWARI ELECTRICALS
11.00 | Supplying and drawing of 2 X 1.5 Sqmm FRLS insulated copper conductor single core cable in the existing surface/ recessed steel conduit/flexible conduit, including terminations etc complete as required. | 200.00 | Meter |  | 160.00 | 32000.00 | 32000.00 | SRI RAJARAJESHWARI ELECTRICALS
12.00 | Supply, installation, testing and commissioning of UL listed Hooter cum Strobe with control module interconnecting to loop cable complete as required. The strobes shall be synchronized for better evacuation as per specification complete as required. | 4.00 | Each |  | 8000.00 | 32000.00 | 32000.00 | SRI RAJARAJESHWARI ELECTRICALS
13.00 | Supply, installation, testing & commissioning of UL listed Fault Isolator Module as per specifications.(UL 9th edition Approved and NFPA) complete as required. | 2.00 | Each |  | 4200.00 | 8400.00 | 8400.00 | SRI RAJARAJESHWARI ELECTRICALS
14.00 | Supply, Installation, Testing & Commissioning of Conventional Type UL/FM listed Fire Alarm Control Panel, with LCD display for system status. The panel should have 2 zones to connect 32 conventional devices per zone for connecting smoke detectors, manual call points, Hooters etc suitable for operation on 220 Volts, 50 Hz AC power supply, LED indicators to indicate fire and normal operation & power supply status, push button for accept and Reset, maintenance free batteries sufficient for backup of 24 hour in standby and 30 minutes in alarm condition with automatic battery charger etc., shall be complete as required. Panel shall have necessary provision for connecting and functioning with auto dialer etc as required. | 2.00 | Each |  | 28000.00 | 56000.00 | 56000.00 | SRI RAJARAJESHWARI ELECTRICALS
15.00 | Supply, installation, testing and commissioning of auto dialer with all necessary accessories including connections, modules if any required for integrating with Addressable Fire Alarm Panels etc complete as required. | 2.00 | Each |  | 22000.00 | 44000.00 | 44000.00 | SRI RAJARAJESHWARI ELECTRICALS
16.00 | Supply of first aid box containing material as prescibed by Indian Red Cross complete as required. | 2.00 | Each |  | 7000.00 | 14000.00 | 14000.00 | SRI RAJARAJESHWARI ELECTRICALS
17.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface / recess including painting in case of surface conduit or cutting the wall and making good the same in case of recessed conduit as required.( Fire Alarm & Telephoine system ). 20mm. | 220.00 | Meter |  | 160.00 | 35200.00 | 35200.00 | SRI RAJARAJESHWARI ELECTRICALS
18.00 | Supply and laying of 25 mm dia. Flexible MS Spiral Steel Conduits with GI clamps, fittings/couplers and saddles for drawing detector control cables from surface to below false ceiling etc. | 20.00 | Meter |  | 120.00 | 2400.00 | 2400.00 | SRI RAJARAJESHWARI ELECTRICALS
19.00 | D: LT CABLE Supply Laying & End Termination
20.00 | Supply of following size of 1.1kv grade multicore aluminium conductor XLPE insulated and PVC sheathed armoured cable as per IS: 7098:1988 (Part - I) with upto date amendments. 3.5 core, 185 Sq.mm. | 120.00 | Meter |  | 1000.00 | 120000.00 | 120000.00 | SRI RAJARAJESHWARI ELECTRICALS
21.00 | Supply of following size of 1.1kv grade multicore aluminium conductor XLPE insulated and PVC sheathed armoured cable as per IS: 7098:1988 (Part - I) with upto date amendments. 3.5 core, 120 Sq.mm. | 70.00 | Meter |  | 675.00 | 47250.00 | 47250.00 | SRI RAJARAJESHWARI ELECTRICALS
22.00 | Supply of following size of 1.1kv grade multicore aluminium conductor XLPE insulated and PVC sheathed armoured cable as per IS: 7098:1988 (Part - I) with upto date amendments. 3.5 core, 95 Sq.mm. | 70.00 | Meter |  | 525.00 | 36750.00 | 36750.00 | SRI RAJARAJESHWARI ELECTRICALS
23.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing DWC HDPE pipe as required Above 95 sq. mm and upto 185 sq.mm. | 180.00 | Meter |  | 50.00 | 9000.00 | 9000.00 | SRI RAJARAJESHWARI ELECTRICALS
24.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 95 sq. mm and upto 185 sq.mm. | 80.00 | Meter |  | 30.00 | 2400.00 | 2400.00 | SRI RAJARAJESHWARI ELECTRICALS
25.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc.conforming to IS 16205 Part 24 complete with fitting(couplers and 'O' rings ) and cutting,jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 90 mm dia (OD-90 mm & ID-76 mm nominal). | 180.00 | Meter |  | 390.00 | 70200.00 | 70200.00 | SRI RAJARAJESHWARI ELECTRICALS
26.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 core, 185 Sq.mm. AL Cable. | 4.00 | Set |  | 500.00 | 2000.00 | 2000.00 | SRI RAJARAJESHWARI ELECTRICALS
27.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 core, 120 Sq.mm. AL Cable. | 2.00 | Set |  | 400.00 | 800.00 | 800.00 | SRI RAJARAJESHWARI ELECTRICALS
28.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 core, 95 Sq.mm. AL Cable. | 2.00 | Set |  | 350.00 | 700.00 | 700.00 | SRI RAJARAJESHWARI ELECTRICALS
29.00 | Supplying and fixing cable route marker with 10 cm x 10 cm x 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. | 9.00 | Each |  | 300.00 | 2700.00 | 2700.00 | SRI RAJARAJESHWARI ELECTRICALS
30.00 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 3.5 core, 185 Sq.mm. | 2.00 | Each |  | 5045.00 | 10090.00 | 10090.00 | SRI RAJARAJESHWARI ELECTRICALS
31.00 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 3.5 core, 120 Sq.mm. | 1.00 | Each |  | 4009.00 | 4009.00 | 4009.00 | SRI RAJARAJESHWARI ELECTRICALS
32.00 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 3.5 core, 95 Sq.mm. | 1.00 | Each |  | 3500.00 | 3500.00 | 3500.00 | SRI RAJARAJESHWARI ELECTRICALS
| Total in Figures |  |  |  |  | 1362999.00
Lowest Amount Quoted BY: SRI RAJARAJESHWARI ELECTRICALS(1362999.00)

## BOQ Summary
BOQ Summary Details Tender Title: Installation, Replacement of ILS at Imphal International Airport. SH. Electrical Works Tender ID: 2020_AAI_50441_2
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SRI RAJARAJESHWARI ELECTRICALS | 1362999.00 | L1