## BoQ1
Government eProcurement System Created By: Vinod Kumar Pandey Created Date/Time: 01-Oct-2020 05:20 PM Tender Title: Construction of Pre-Engineered Airport Terminal and Associated works at Muirpur Airport. S.H. Provision of Substation Equipments and Associated works etc. Tender ID: 2020_AAI_50655_1
Tender Inviting Authority: Sr. Manager (Engg.-E), LBSI Airport Varanasi.
Name of work: Construction of Pre-Engineered Airport Terminal and Associated works at Muirpur Airport. SH: Provision of Substation Equipments and Associated works etc.
Contract No: 2020_AAI_ 50655_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | m/s anil kumar singh(GSTN-09AVFPS4608C1ZL) |  | Naagar Infrastructure Pvt Ltd(GSTN-07AACCN7477R1ZJ) |  | Choubay And Co.(Agencies) Pvt.Ltd.(GSTN-09AAACC6073E1ZT) |  | TECHNISYS ENGINEERING PRIVATE LIMITED(GSTN-06AACCT8886E1ZZ)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | 11KV H.T. Panel in substation (1 incomer + 2 outgoings ) SITC of indoor cubicle type floor mounted metal clad 11KV VCB Panel Board with 11 KV, Minimum 18.3kA , 630A, HT VCB (One incomer & Two outgoing VCB),totally enclosed & fully interlocked, horizontal draw out, horizontal / vertical Isolation type breaker as per IEC 62271-100 for breaker & 62271-200 for panels and of capacity as mentioned below, single break, trip free mechanism, motor / manually charged and auto / manual closing breaker suitable for use on 11kV 3 phase 50 Hz AC supply complete with self contained, fully interlocked, rack in and rackout mechanism, air insulated encapsulated copper bus bars of 800 Amp capacity, Breaker featured with mechanical ON/OFF indication with hand trip device,DC power pack, spring released coil, shunt trip coil and auxiliary switches and equipped with switchgears mentioned below. Panel Board shall be provided with Earthing trolley for incoming side / Busbar / outgoing breakers earthing, Panel Board shall be fabricated, made out of 2 mm thick CRCA sheet steel, totally enclosed, IP 4X, free standing, floor mounting, dust and vermin proof ,indoor, compartmentalized, powder coated painting including internally wired / interconnected with suitable provision for end termination with heat shrinkable jointing material etc as required (Note cost of end termination not included in this item) VCBs shall be SCADA compatible & shall have feature for control & monitoring by SCADA system/ BMS in future.(Cost of SCADA system not included in this item) Incomer: (a) 630A,Minimum18.3kA, 11KV, 3 phase, 50 Hz Vacuum Circuit Breaker(VCB),Icu=Ics=Icw=100% and withstand capacity of 3 seconds. -1 No. (b) 3 phase 11 KV/110 V Volts PT, class 1.0 accuracy and 100 VA burden with 1 No Voltmeter (0-15 KV), Digital type, selector switch for voltmeter and protection fuses for HT metering upto 15 KV on incomer (Voltmeter shall have communication features for monitoring by BMS) - 1set (c ) 3 CTs 60/5+5A of 15 VA burden and accuracy class 1.0 for metering and class 5P10 for protection-1 set (d ) Multi function meter to display F, PF, kW, kVA, kVAR, kWh, kVAh, kVARh, THD, Phase angles, Power demand parameters, suitable for operation on 110V a.c supply, with RS-485 interface for integration to BMS- 1 No (e) Microprocessor based numerical relay for Over current and Earth fault protection -1 No (f) 0-100 Amps Ammeter, digital type with selector switch for ammeters. (ammeter shall have communication features for monitoring by BMS) -1 No (g) Phase indicating lamps with HRC fuses/MCB-1 Set (h) Indicating lamps to indicate OPEN, CLOSE, TRIP, SPRING CHARGED, TRIP CIRCUIT HEALTHY-1 set (i) 800 Amps TP Copper Busbar-1 set (j) Test terminal block-1 No (k) Copper bus bar of suitable size for earthing-1 set (l) Master trip relay & trip circuit healthy supervision relay.-1 set (m) Provision for padlocking the incomer VCBs in 'OFF' position.-1 No. Outgoing: (a) 630A,Minimum 18.3kA, 11KV, 3 phase, 50 Hz Vacuum Circuit Breaker(VCB),Icu=Ics=Icw=100% and withstand capacity of 3 seconds. -2 No. (b) 3 CTs 60/5+5A of 15 VA burden and accuracy class 1.0 for metering and class 5P10 for protection-2 set ( 1 set for each VCB) (c) Multi function meter to display F, PF, kW, kVA, kVAR, kWh, kVAh, kVARh, THD, Phase angles, Power demand parameters, suitable for operation on 110V a.c supply, with RS-485 interface for integration to BMS- 2 No (1 No for each VCB) (d) Microprocessor based numerical relay for O/C and E/F protection-2 No.(1 No for each VCB) (e) 0-100 Amp, digital type ammeter with selector switch (ammeter shall have communication features for monitoring by BMS)- 2 No.(1 No for each VCB) (f) indicating lamps to indicate OPEN, CLOSE, TRIP, SPRING CHARGED, TRIP CIRCUIT HEALTHY- 2 set (1 set for each VCB) (g) Master trip relay & trip circuit healthy supervision relay-2 set (1 Set for each VCB) (h) Protection arrangements with necessary auxiliary relays for connecting the WTI of Transformer- 2 set (1set for each transformer) (i) Annunciator (having minimum 8 windows) and alarm bell/ hooter - 2 No.( 1 No. for each VCB) NOTE:-All metering and protection devices, interconnections, necessary control wiring and all other accessories shall be provided as per SLD or as required as per specifications and technical particulars and as per instruction of E-I-C. | 1.00 | Each |  | 1610000.00 | 1610000.00 | 1090000.00 | 1090000.00 | 1051000.00 | 1051000.00 | 1150000.00 | 1150000.00 | 1061658.00 | 1061658.00 | 1051000.00 | Naagar Infrastructure Pvt Ltd
2.00 | SITC of 400 KVA, 11/0.433 KV, 3 Phase, 50 Hz, Dyn 11, indoor ONAN type, copper wound transformer with OFF load tap changing arrangement for tap range + 5% to -15% in steps of 2.5% on H.V. side , having cable end boxes on HV side suitable for 3x70.sqmm XLPE cable of 11 KV grade and 3X240 sqmm 1.1KV cable termination arrangement on LV side complete with all accessories i/c first filling of filtered dehydrated oil and confirming to IS 2026 (Part 1 to Part 5) & as per specification attached complete in all respects as required at site. The transformer losses shall be within the limits prescribed as per ECBC 2017 norms or lower. | 2.00 | Each |  | 1018000.00 | 2036000.00 | 550000.00 | 1100000.00 | 915000.00 | 1830000.00 | 1000000.00 | 2000000.00 | 858526.00 | 1717052.00 | 1100000.00 | m/s anil kumar singh
3.00 | APFC panel: SITC of floor mounted auto-manual power factor correction system panel of 150 KVAR capacity having 3 phase, Mixed Die Electric/ APP /utra heavy duty type (total power loss not exceeding 0.35 W/ KVAR) power capacitor in 10 steps and provided with Electronic Thyristor switching with 7 % detuned harmonics filter consisting of 7% Detuned Copper Reactors, 440V 50Hz for all capacitors to supress switching of inrush current and reducing harmonics to improve capcitor life. The panel shall be fabricated in compartmentalized design from CRCA sheet steel of 2mm thick for frame work and covers, having minimum 400 Amp capacity extensible type TPN Aluminium bus bars, entire panel shall have a common GI earth bar of size 50 mm x 6 mm with 2 Nos. earth stud, solid connections from main bus bar to switch gears/ accessories with required size of Al. bus bars and control wiring with 2.5 sq.mm. Single Core PVC insulated FRLS copper conductor , provided with exhaust fans and grills for proper ventilation, interconnections with suitable size conductor cables & lugs and accommodating the following swicthgears & accessories: Incomer:- 320 Amp,36kA, TP MCCB, Icu=Ics=100 %, with thermomagnetic based release having adjustable O/C, S/C setting- 1 No. Metering:- Digital Ammeter & Voltmeter of suitable range alongwith selector switch i/c suitable capacity CT & PT.-01 Set. Outgoing:- 100 A, 25KA, TP ,MCCB,Icu=Ics=100 %, with thermomagnetic based release having adjustable O/C,S/C setting - 1 Nos. 63 A, 10KA, TP ,MCB - 2 Nos 32 A, 10KA, TP ,MCB - 2 Nos 25 A, 10KA, TP ,MCB - 1 Nos 16 A, 10KA, TP ,MCB - 2 Nos Capaciors: 50 kVAr Capacitors feeder - 1 Set 25 kVAr Capacitors feeder - 2 set 15 kVAr Capacitor feeder - 2 set 10 kVAr Capacitor feeder- 1 set 5 kVAr Capacitor feeder- 2 set LED Indicating lamp for all steps (ON indication) and mains ON indication - 1 set One number automatic power factor sensing & correction relay (8 step) complete with its all accessories etc.as reqd. Auto manual selector switch with facility for manual control of capacitor bank in the event automatic operation not functioning. Suitable capacity fan for cooling of APFC panel of as per OEM recommendations. | 2.00 | Each |  | 455000.00 | 910000.00 | 208000.00 | 416000.00 | 340000.00 | 680000.00 | 590000.00 | 1180000.00 | 329224.00 | 658448.00 | 416000.00 | m/s anil kumar singh
4.00 | Supply of 11 KV grade (11 KV Earthed System) XLPE insulated , PVC sheathed, Aluminium Conductor,Armoured Power cable of size 3X70 sq mm, Conforming to IS: 7098 (Part - II) amended upto date. | 100.00 | Meter |  | 600.00 | 60000.00 | 500.00 | 50000.00 | 530.00 | 53000.00 | 500.00 | 50000.00 | 801.00 | 80100.00 | 50000.00 | m/s anil kumar singh, Choubay And Co.(Agencies) Pvt.Ltd.
5.00 | Supplying of 110 mm outer dia, PE80, HDPE pipe ISI marked to lay in underground as per IS:4984:2016 with latest ammendmants upto date duly ISI marked . Should withstand minimum pressure of 6 Kgf/cm2. | 650.00 | Meter |  | 450.00 | 292500.00 | 500.00 | 325000.00 | 390.00 | 253500.00 | 275.00 | 178750.00 | 303.00 | 196950.00 | 178750.00 | Choubay And Co.(Agencies) Pvt.Ltd.
6.00 | Laying of 110 mm outer dia HDPE along with all accessories like socket, bend, couplers etc.direct in ground (75 cm below ground level) including excavation and refilling the trench etc. , complete as required. | 600.00 | Meter |  | 70.00 | 42000.00 | 400.00 | 240000.00 | 110.00 | 66000.00 | 80.00 | 48000.00 | 240.00 | 144000.00 | 42000.00 | jaydeep agency corporation
7.00 | Laying of 110 mm outer dia HDPE along with all accessories like socket, bend, couplers etc.direct in ground (120 cm below ground level) including excavation and refilling the trench etc. , complete as required. | 50.00 | Meter |  | 90.00 | 4500.00 | 400.00 | 20000.00 | 150.00 | 7500.00 | 100.00 | 5000.00 | 521.00 | 26050.00 | 4500.00 | jaydeep agency corporation
8.00 | Laying of one number 3X70 sq mm PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing RCC/ HUME/ METAL /HDPE pipe as required. | 50.00 | Meter |  | 30.00 | 1500.00 | 500.00 | 25000.00 | 60.00 | 3000.00 | 30.00 | 1500.00 | 125.00 | 6250.00 | 1500.00 | jaydeep agency corporation, Choubay And Co.(Agencies) Pvt.Ltd.
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11KV grade of 3X70 sqmm in the existing masonry open duct as required. | 50.00 | Meter |  | 30.00 | 1500.00 | 500.00 | 25000.00 | 50.00 | 2500.00 | 20.00 | 1000.00 | 125.00 | 6250.00 | 1000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade Above 185 sq. mm and upto 400 sq. mm size in the existing RCC/ HUME/ METAL/HDPE pipe as required. | 600.00 | Meter |  | 35.00 | 21000.00 | 450.00 | 270000.00 | 90.00 | 54000.00 | 30.00 | 18000.00 | 146.00 | 87600.00 | 18000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
11.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 70 sq mm of 3 core, XLPE aluminium conductor cable of 11 KV grade as required | 5.00 | Each |  | 3500.00 | 17500.00 | 2756.00 | 13780.00 | 6800.00 | 34000.00 | 3000.00 | 15000.00 | 9140.00 | 45700.00 | 13780.00 | m/s anil kumar singh
12.00 | Cylinderless Clean Agent based ( Zero global warming potential ) Fire Suppression systems, suitable for extinguishing, electrical enclosed panel, fire by automatically triggering the thermo-activated micro capsules of aerosol forming soild compound ( minimum 100 gm aerosol for 1 cum panel space) or equivalent compound with cord minimum 3.5 Mtr for 1 cum panel space activated at 120-175 Degree C temperature(as per requirement of compartment of the panel),in each compartment of the panel conforming to relevant IS and CPWD norms.The system has to be Maintenance free and without any pressurized cylinder,tube, pressure gauge as required.Make and material of Fire Suppression systems required prior approval of EIC. | 20.00 | Cum |  | 5000.00 | 100000.00 | 24500.00 | 490000.00 | 33500.00 | 670000.00 | 6000.00 | 120000.00 | 27623.00 | 552460.00 | 100000.00 | jaydeep agency corporation
13.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt complete as required. | 6.00 | Each |  | 8900.00 | 53400.00 | 19500.00 | 117000.00 | 9500.00 | 57000.00 | 11000.00 | 66000.00 | 30818.00 | 184908.00 | 53400.00 | jaydeep agency corporation
14.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt complete as required. | 4.00 | Each |  | 6000.00 | 24000.00 | 18500.00 | 74000.00 | 5100.00 | 20400.00 | 4000.00 | 16000.00 | 15968.00 | 63872.00 | 16000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
15.00 | Providing and fixing 50 mm X 5 mm Copper strip on surface /recess/on existing GI pipe for connections etc. as required. | 66.00 | Meter |  | 1250.00 | 82500.00 | 650.00 | 42900.00 | 1700.00 | 112200.00 | 1300.00 | 85800.00 | 2644.00 | 174504.00 | 42900.00 | m/s anil kumar singh
16.00 | Providing and fixing 50 mm X 6 mm G.I. strip on surface /recess/on existing GI pipe for connections etc. as required. | 44.00 | Meter |  | 250.00 | 11000.00 | 70.00 | 3080.00 | 250.00 | 11000.00 | 200.00 | 8800.00 | 396.00 | 17424.00 | 3080.00 | m/s anil kumar singh
17.00 | Providing and laying of 65 mm dia GI pipe 'B' class below the ground (for laying earth strips in it) including road cutting & excavation upto a depth of 50 cm back filling & sealing of ends with bituminous resin and making good in an approved manner as required | 60.00 | Meter |  | 550.00 | 33000.00 | 1050.00 | 63000.00 | 850.00 | 51000.00 | 550.00 | 33000.00 | 1258.00 | 75480.00 | 33000.00 | jaydeep agency corporation, Choubay And Co.(Agencies) Pvt.Ltd.
18.00 | Providing and fixing testing joint, made of 50 mm X 5 mm thick Copper strip, 125 mm long, with 4 Nos. of brass bolts, nuts, chuck nuts and spring washers etc. complete as required. | 6.00 | Each |  | 1100.00 | 6600.00 | 18500.00 | 111000.00 | 900.00 | 5400.00 | 500.00 | 3000.00 | 1194.00 | 7164.00 | 3000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
19.00 | Providing and fixing testing joint, made of 50 mm X 6 mm thick G.I. strip, 125 mm long, with 4 Nos. of G.I. bolts, nuts, chuck nuts and spring washers etc. complete as required. | 4.00 | Each |  | 200.00 | 800.00 | 9500.00 | 38000.00 | 450.00 | 1800.00 | 200.00 | 800.00 | 805.00 | 3220.00 | 800.00 | jaydeep agency corporation, Choubay And Co.(Agencies) Pvt.Ltd.
20.00 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 2.00 | Each |  | 180.00 | 360.00 | 1000.00 | 2000.00 | 500.00 | 1000.00 | 200.00 | 400.00 | 345.00 | 690.00 | 360.00 | jaydeep agency corporation
21.00 | Providing and fixing H.T. danger notice plate of 250 mm X 200 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 2.00 | Each |  | 200.00 | 400.00 | 2000.00 | 4000.00 | 500.00 | 1000.00 | 200.00 | 400.00 | 345.00 | 690.00 | 400.00 | jaydeep agency corporation, Choubay And Co.(Agencies) Pvt.Ltd.
22.00 | Rubber gloves of 11KV grade as per IS 4770-68. | 2.00 | Pair |  | 450.00 | 900.00 | 1200.00 | 2400.00 | 1200.00 | 2400.00 | 500.00 | 1000.00 | 271.00 | 542.00 | 542.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
23.00 | Supply and fixing of high voltage synthetic insulating mat made of synthetic Elastomer suitable for upto 3.3 KV conforming to IS 15652:2006 with minimum width of 1 metre and thickness of 2.0 mm +/- 10 % (Class-A). Insulating mat should be flexible , anti skid, fire reatrdant, water and moisture proof with no adverse effect of acids,alkalies and transformer oil. Insulating mat should be fixed with suitable adhesive/chemibond , resin,water proofing compound and other sealing materials as per specifications. Insulating mats should be ISI marked alongwith CM/L nos at every meter. | 25.00 | Sq. Mtr |  | 1800.00 | 45000.00 | 525.00 | 13125.00 | 1350.00 | 33750.00 | 1600.00 | 40000.00 | 710.00 | 17750.00 | 13125.00 | m/s anil kumar singh
24.00 | Supply and fixing of high voltage synthetic insulating mat made of synthetic Elastomer suitable for upto 11 KV conforming to IS 15652:2006 with minimum width of 1 metre and thickness of 2.5 mm +/- 10 % (Class-B). Insulating mat should be flexible , anti skid, fire reatrdant, water and moisture proof with no adverse effect of acids,alkalies and transformer oil. Insulating mat should be fixed with suitable adhesive/chemibond , resin,water proofing compound and other sealing materials as per specifications. Insulating mats should be ISI marked alongwith CM/L nos at every meter. | 50.00 | Sq. Mtr |  | 1600.00 | 80000.00 | 625.00 | 31250.00 | 1950.00 | 97500.00 | 1800.00 | 90000.00 | 857.00 | 42850.00 | 31250.00 | m/s anil kumar singh
| Total in Figures |  |  |  |  | 5434460.00 |  | 4566535.00 |  | 5098950.00 |  | 5112450.00 |  | 5171612.00
Lowest Amount Quoted BY: m/s anil kumar singh(4566535.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of Pre-Engineered Airport Terminal and Associated works at Muirpur Airport. S.H. Provision of Substation Equipments and Associated works etc. Tender ID: 2020_AAI_50655_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | m/s anil kumar singh | 4566535.00 | L1
| 2 | Naagar Infrastructure Pvt Ltd | 5098950.00 | L2
| 3 | Choubay And Co.(Agencies) Pvt.Ltd. | 5112450.00 | L3
| 4 | TECHNISYS ENGINEERING PRIVATE LIMITED | 5171612.00 | L4
| 5 | jaydeep agency corporation | 5434460.00 | L5