## BoQ1
Government eProcurement System Created By: Moatemjen Pongen Created Date/Time: 13-Aug-2020 01:36 PM Tender Title: Electrical works for construction of new NDB building at Dimapur Airport Tender ID: 2020_AAI_50933_1
Tender Inviting Authority: AGM(E-E) AAI, Dimapur Airport.
Name of Work: Electrical works for construction of new NDB building at Dimapur Airport.
Contract No: (Tender ID: 2020_AAI_50933_1)
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RANJIT SALES CORPORATION(GSTN-NA) |  | K YHOME ENGINEERING AND CONSTRUCTION(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I : SITC OF DG SET & ACCESSORIES Supply, installation, testing and commissioning of 25 KVA Diesel Generator Set, trolley mounted, with acoustic enclosure confirming to latest enviromental protection regulations for emmission and noise levels complete with diesel engine along with required AVM pads, rated 1500 RPM , water cooled, electric start, turbo charged, after cooled confirming to the latest standard coupled with alternator of 400 KVA rating, brushless, self excited, self regulated,minimum Class H insulation and suitable for continuous operation at 1500 RPM, generating 415 +/- 5% volts at 0.8PF (lag) 50Hz, 3 phase, 4 wire system. Both engine and alternator shall be mounted on common channel iron fabricated base frame, with suitable accessories such as two nos of 12V,180 Ah, LEAD acid Batteries alongwith leads, battery stand, intregral fuel tank, fuel piping from fuel tank to engine, residential silencer with flexible coupling and exhaust pipe length as required as per site requirement, cable termination box suitable for termination of 2 runs 3.5 x 240/300 sq.mm armoured aluminium cables etc as required and as per specifications. | 1.00 | Job |  | 566170.00 | 566170.00 | 410000.00 | 410000.00 | 410000.00 | K YHOME ENGINEERING AND CONSTRUCTION
2.00 | Supply, Installation, Testing and Commissioning of Automatic Mains Failure Control Panel suitable for 400 KVA DG Set with By Pass arrangement, Power contactor of suitable capacity as per full load ampere rating of alternator for the mains and alternator supply, suitable size of copper/aluminium bus bars of rated capacity, control relays, battery charging circuit suitable for charging 2 nos.12V,180Ah lead acid batteries, meters, indicators etc including making interconnections as required. The set shall be capable to deliver and transfer full load within a switch over time of 5 to 15 seconds complete etc as required. | 1.00 | Job |  | 137762.00 | 137762.00 | 137000.00 | 137000.00 | 137000.00 | K YHOME ENGINEERING AND CONSTRUCTION
3.00 | SH-II : SUPPLY AND LAYING OF LT CABLES AND OTHER ASSOCIATED WORKS Supply of XLPE insulated,armoured 1.1 KV grade aluminium conductor cable as per IS 7098(Part 1) 1988 with upto date ammendments of following sizes: a) 4 Core, 120 Sq.mm | 1900.00 | Mtrs |  | 512.00 | 972800.00 | 415.00 | 788500.00 | 788500.00 | K YHOME ENGINEERING AND CONSTRUCTION
4.00 | b) 4 Core, 25 Sq.mm | 150.00 | Mtrs |  | 160.00 | 24000.00 | 160.00 | 24000.00 | 24000.00 | RANJIT SALES CORPORATION, K YHOME ENGINEERING AND CONSTRUCTION
5.00 | Supply of following sizes of XLPE insulated PVC sheathed, copper conductor armoured cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 with upto date amendments. 10 Core, 2.5 Sq.mm control cable | 50.00 | Mtrs |  | 249.00 | 12450.00 | 230.00 | 11500.00 | 11500.00 | K YHOME ENGINEERING AND CONSTRUCTION
6.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of XLPE armoured aluminium conductor cable of 1.1 KV grade as required. 4 Core, 120 Sq.mm | 4.00 | Set |  | 1065.00 | 4260.00 | 900.00 | 3600.00 | 3600.00 | K YHOME ENGINEERING AND CONSTRUCTION
7.00 | 4 Core, 25 Sq.mm | 4.00 | Set |  | 587.00 | 2348.00 | 600.00 | 2400.00 | 2348.00 | RANJIT SALES CORPORATION
8.00 | Laying and fixing of one number XLPE armoured power cable of 1.1 KV grade of following size on cable tray as required. above 95 sq mm. and upto 185 sq mm | 500.00 | Mtrs |  | 67.00 | 33500.00 | 75.00 | 37500.00 | 33500.00 | RANJIT SALES CORPORATION
9.00 | upto 35 sq mm | 50.00 | Mtrs |  | 24.00 | 1200.00 | 60.00 | 3000.00 | 1200.00 | RANJIT SALES CORPORATION
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required above 95 sq mm. and upto 185 sq mm | 50.00 | Mtrs |  | 43.00 | 2150.00 | 35.00 | 1750.00 | 1750.00 | K YHOME ENGINEERING AND CONSTRUCTION
11.00 | upto 35 sq mm | 20.00 | Mtrs |  | 20.00 | 400.00 | 20.00 | 400.00 | 400.00 | RANJIT SALES CORPORATION, K YHOME ENGINEERING AND CONSTRUCTION
12.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. above 95 sq mm. and upto 185 sq mm | 500.00 | Mtrs |  | 128.00 | 64000.00 | 60.00 | 30000.00 | 30000.00 | K YHOME ENGINEERING AND CONSTRUCTION
13.00 | upto 35 sq mm | 50.00 | Mtrs |  | 38.00 | 1900.00 | 40.00 | 2000.00 | 1900.00 | RANJIT SALES CORPORATION
14.00 | Laying of one number XLPE armoured power cable of 1.1 KV grade of following size in the existing masonary open duct as required. above 95 sq mm. and upto 185 sq mm | 100.00 | Mtrs |  | 35.00 | 3500.00 | 50.00 | 5000.00 | 3500.00 | RANJIT SALES CORPORATION
15.00 | upto 35 sq mm | 20.00 | Mtrs |  | 20.00 | 400.00 | 40.00 | 800.00 | 400.00 | RANJIT SALES CORPORATION
16.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. above 95 sq mm. and upto 185 sq mm | 300.00 | Mtrs |  | 302.00 | 90600.00 | 280.00 | 84000.00 | 84000.00 | K YHOME ENGINEERING AND CONSTRUCTION
17.00 | upto 35 sq mm | 60.00 | Mtrs |  | 284.00 | 17040.00 | 230.00 | 13800.00 | 13800.00 | K YHOME ENGINEERING AND CONSTRUCTION
18.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required. 50mm dia. | 20.00 | Mtrs |  | 505.00 | 10100.00 | 600.00 | 12000.00 | 10100.00 | RANJIT SALES CORPORATION
19.00 | 80mm dia. | 50.00 | Mtrs |  | 765.00 | 38250.00 | 900.00 | 45000.00 | 38250.00 | RANJIT SALES CORPORATION
20.00 | Supplying and installing following size of perforated pre painted M.S cable trays with perforation not more than 17.5 %, in convenient sections,joined with connectors and fixed on 25mmx25mmx3 mm angle supports duly grouted on the wall/floor with proper support etc complete as required. 300 mm width x 62.5 mm depth x 2.0 mm thickness | 500.00 | Mtrs |  | 408.00 | 204000.00 | 390.00 | 195000.00 | 195000.00 | K YHOME ENGINEERING AND CONSTRUCTION
21.00 | 100 mm width X 50 mm depth X 1.6 mm thickness | 50.00 | Mtrs |  | 343.00 | 17150.00 | 350.00 | 17500.00 | 17150.00 | RANJIT SALES CORPORATION
22.00 | SITC of modular TP+N Type 1+2 SPD , having 100KA 10/350 micro seconds neutral to earth, 50 KA 10/350 micro sec line to neutral, with limiting voltage less than 1.5 kV for installation on the mains power entry point at the incomers before UPS. | 4.00 | Each |  | 9000.00 | 36000.00 | 45000.00 | 180000.00 | 36000.00 | RANJIT SALES CORPORATION
23.00 | SITC of modular TP+N Type 2 SPD , having 100KA 10/350 micro seconds neutral to earth, 50 KA 10/350 micro sec line to neutral, with limiting voltage less than 1.5 kV to be provided at UPS output/Isolation Transformer output in each phase and neutral | 5.00 | Each |  | 4480.00 | 22400.00 | 55000.00 | 275000.00 | 22400.00 | RANJIT SALES CORPORATION
24.00 | SITC of modular 1P+N Type 2 SPD , having 100KA 10/350 micro seconds neutral to earth, 50 KA 10/350 micro sec line to neutral, with limiting voltage less than 1.5 kV to be provided at UPS output/Isolation Transformer output in each phase and neutral | 10.00 | Each |  | 2750.00 | 27500.00 | 12000.00 | 120000.00 | 27500.00 | RANJIT SALES CORPORATION
25.00 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 Core X 120 sq mm | 6.00 | Each |  | 4175.00 | 25050.00 | 5500.00 | 33000.00 | 25050.00 | RANJIT SALES CORPORATION
26.00 | Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. | 25.00 | Each |  | 325.00 | 8125.00 | 250.00 | 6250.00 | 6250.00 | K YHOME ENGINEERING AND CONSTRUCTION
27.00 | SH-III : SITC of Feeder Pillars,Cable Change Over Box, Distribution Board etc, SITC of outdoor cubicle type double door totally enclosed compartmentalized floor mounting type dust weather and vermin proof LT feeder piller panel of size 1200 mmX 600 mm X 600 mm suitable for 415V, 4 wire, 50Hz supply, fabricated from CRCA sheet of 2mm thick complete with bus bar, ammeter, voltmeter, Indication lamp(LED type) , interconnecting with suitable size of copper leads/ solid aluminium strip/ rod and having following incoming and outgoing MCCB/Switch gears with rotary mechanism as per latest IS Specifications, supported on suitable size of angle iron frame, making PCC foundation work etc complete as required. MCCB Description Incoming : 125 A, Ics = 100% of Icu, 50 kA, 4P MCCB = 01 no. Outgoing : 1) 63 A, Ics = 100% of Icu, 50 kA, 4P MCCB, Make Havells , F Frame , Category No. IHLFHT0063 = 02 nos. , 2) 40 A, Ics = 100% of Icu, 50 kA, 4P MCCB, Make Havells , F Frame , Category No. IHLFHF0040 = 02 nos. | 1.00 | Each |  | 117100.00 | 117100.00 | 80000.00 | 80000.00 | 80000.00 | K YHOME ENGINEERING AND CONSTRUCTION
28.00 | SITC of outdoor cubicle type double door totally enclosed compartmentalized floor mounting type dust weather and vermin proof Cable Change Over Box of size 1200 mmX 600 mm X 600 mm suitable for 415V, 4 wire, 50Hz supply, fabricated from CRCA sheet of 2mm thick complete with 01 no. Automatic Transfer Switch (ATS),Copper Bus Bar, interconnecting with suitable size of copper leads and capable for housing Loop-in & Loop Out of 2 X 240 sq mm Incoming and 04 X 120 sq mm Outgoing Cables, supported on suitable size of angle iron frame, making PCC foundation work etc complete as required. | 1.00 | Each |  | 48370.00 | 48370.00 | 70000.00 | 70000.00 | 48370.00 | RANJIT SALES CORPORATION
29.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB’s (but without MCB’s and incomer ) as required . 12 way (4 + 36), Double door | 3.00 | Each |  | 11325.00 | 33975.00 | 6500.00 | 19500.00 | 19500.00 | K YHOME ENGINEERING AND CONSTRUCTION
30.00 | Supplying and fixing of following rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 A | 4.00 | Each |  | 1378.00 | 5512.00 | 1500.00 | 6000.00 | 5512.00 | RANJIT SALES CORPORATION
31.00 | 5-32 A | 25.00 | Each |  | 1020.00 | 25500.00 | 1000.00 | 25000.00 | 25000.00 | K YHOME ENGINEERING AND CONSTRUCTION
32.00 | SH-IV : Internal Wiring Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size M.S. box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 48.00 | point |  | 890.00 | 42720.00 | 500.00 | 24000.00 | 24000.00 | K YHOME ENGINEERING AND CONSTRUCTION
33.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required. 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 168.00 | Mtrs |  | 195.00 | 32760.00 | 300.00 | 50400.00 | 32760.00 | RANJIT SALES CORPORATION
34.00 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 180.00 | Mtrs |  | 225.00 | 40500.00 | 380.00 | 68400.00 | 40500.00 | RANJIT SALES CORPORATION
35.00 | Supply & Installation of Surface and wall mounted LED batten, extruded aluminium housing provided for efficient heat dissipation with polycarbonate diffuser & integrated electronic driver with industrial grade heavy duty driverwith internal driver, | 23.00 | Each |  | 610.00 | 14030.00 | 2500.00 | 57500.00 | 14030.00 | RANJIT SALES CORPORATION
36.00 | Supply & Installation of indoor type Slim surface mounted Square LED,with internal driver, suited for installation in Ceiling Recess,Aesthetically designed 1x1, 2x2 & 4x1 LED flat panel which provides soft-light and glare free symmetrical illumination . | 20.00 | Each |  | 1475.00 | 29500.00 | 2000.00 | 40000.00 | 29500.00 | RANJIT SALES CORPORATION
37.00 | Supply & Installation of LED outdoor light made up of pressure die cast housing with toughned glass and individual high power LEDs,Screwed Type Pole Mouning Type, IP66 protection. | 4.00 | Each |  | 5845.00 | 23380.00 | 2100.00 | 8400.00 | 8400.00 | K YHOME ENGINEERING AND CONSTRUCTION
38.00 | Supply & Installation of Ceiling Fans, of Sweep: 1200mm , Power Rating : 50-55 Watt, RPM: 320-360 RPM, Air Delivery > 200 CMM, White Colour, Noise less, 5 Star/Availablke Maximum Star Rated by BEE. | 2.00 | Each |  | 2400.00 | 4800.00 | 2500.00 | 5000.00 | 4800.00 | RANJIT SALES CORPORATION
39.00 | Supply & Installation of Heavu Duty Exhaust Fans, of Sweep: 380 mm , Power Rating : 50-55 Watt, RPM: 900 RPM, White Colour, Noise less, 5 Star/Availablke Maximum Star Rated by BEE. | 5.00 | Each |  | 3658.00 | 18290.00 | 3500.00 | 17500.00 | 17500.00 | K YHOME ENGINEERING AND CONSTRUCTION
40.00 | SH-V : SITC of Energy Efficient Split Type Air Conditioner and Water Cooler Supply of Hi-wall single phase, 5 Star Inverter type split Air conditioners of nominal cooling capacity, with energy efficient rotary compressor filled with R410a GAS. Including remote control operation for temperature adjustment, indoor unit blower speed, swing adjustment, auto restart, sleep mode, turbo mode, with LED display for temperature i/c standard length of copper refrigerant pipe, copper electrical cable wire & drain pipe etc. complete as required. 1.5 ton HIGHWALL 5 Star Inverter type AC’s | 8.00 | Each |  | 42500.00 | 340000.00 | 48000.00 | 384000.00 | 340000.00 | RANJIT SALES CORPORATION
41.00 | Installation, testing, commissioning of hi-wall A/C units etc. and making of necessary hole on concrete/brick wall and making good the damages i/c providing suitable size PVC pipe for drawing the gas/drain pipe and wire etc through the concrete/brick wall as required.( 1.5 ton, 2.0 ton,3.0 Ton) | 8.00 | Each |  | 2000.00 | 16000.00 | 2500.00 | 20000.00 | 16000.00 | RANJIT SALES CORPORATION
42.00 | S/F of appropriate size of PVC drain pipes complete with fittings on wall or floor surface etc as required. | 48.00 | Mtrs |  | 225.00 | 10800.00 | 220.00 | 10560.00 | 10560.00 | K YHOME ENGINEERING AND CONSTRUCTION
43.00 | S/F of extra refrigerant pipe of suitable size and thickness complete with soldering, leakages testing and providing thermal insulation & white tape etc as required. | 16.00 | Mtrs |  | 1235.00 | 19760.00 | 220.00 | 3520.00 | 3520.00 | K YHOME ENGINEERING AND CONSTRUCTION
44.00 | Supply and fitting of Appropriate size and thickness of MS Stand / L-Chair for fixing outdoor unit or Condensing Units along with necessary anchor fastener/bolt & nuts etc on concrete/brick wall or floor etc. as required. | 8.00 | Each |  | 1275.00 | 10200.00 | 1000.00 | 8000.00 | 8000.00 | K YHOME ENGINEERING AND CONSTRUCTION
45.00 | Supply and laying of 3 core X 1.5 sq.mm PVC insulated flexible copper wire | 120.00 | Mtrs |  | 46.00 | 5520.00 | 80.00 | 9600.00 | 5520.00 | RANJIT SALES CORPORATION
46.00 | Supply and fixing of DBOXx Plug & Socket with Plastic Cover having modular type socket, DP-MCB of 20 amps rating, on surface or in recess testing and commissioning etc. as required. | 9.00 | Each |  | 887.00 | 7983.00 | 1000.00 | 9000.00 | 7983.00 | RANJIT SALES CORPORATION
47.00 | Supply and fixing of 105 mm X 50 mm DLP plastic trunking cover having single body with single / double compartments and for fixing on wall / floor surface for hiding the routing of refrigerant pipe, interconnection wires and drainage tube passing through room of the following sizes. DLP plastic trunking, 80 mmX 50 mm | 135.00 | Mtrs |  | 415.00 | 56025.00 | 400.00 | 54000.00 | 54000.00 | K YHOME ENGINEERING AND CONSTRUCTION
48.00 | Flexible cover 85 mm width | 125.00 | Mtrs |  | 250.00 | 31250.00 | 260.00 | 32500.00 | 31250.00 | RANJIT SALES CORPORATION
49.00 | Base joints | 20.00 | Mtrs |  | 53.00 | 1060.00 | 700.00 | 14000.00 | 1060.00 | RANJIT SALES CORPORATION
50.00 | End caps | 10.00 | Each |  | 105.00 | 1050.00 | 170.00 | 1700.00 | 1050.00 | RANJIT SALES CORPORATION
51.00 | Internal angles - adjustable from 80° - 100° | 15.00 | Each |  | 272.00 | 4080.00 | 390.00 | 5850.00 | 4080.00 | RANJIT SALES CORPORATION
52.00 | External angles - adjustable from 60° - 120° | 15.00 | Each |  | 266.00 | 3990.00 | 395.00 | 5925.00 | 3990.00 | RANJIT SALES CORPORATION
53.00 | Supply , Installation, Testing and Commissioning of Voltage Stabilizer suitable for 1.5 TR Air Conditioner, Current Rating 15 A, Operating Voltage Range 170 V - 270 V | 8.00 | Each |  | 3470.00 | 27760.00 | 4500.00 | 36000.00 | 27760.00 | RANJIT SALES CORPORATION
54.00 | Supply , Installation, Testing and Commissioning of Water Purifier cum Cooler with at least 80 ltrs inbuilt storage with inbuilt 3 stage high quality water purifier and temperature adjustable cooler. Separate taps for normal and cold water | 1.00 | Each |  | 75300.00 | 75300.00 | 40000.00 | 40000.00 | 40000.00 | K YHOME ENGINEERING AND CONSTRUCTION
55.00 | SH-VI : SITC of UPS Power conversion Efficiency 95% or better at 50-100% varying load. Output Overload Rating : Normal Operation: 125% for 60 sec before transfer to By-pass Bypass operation: 120% continuous 1000% for >10 milliseconds UPS shall have I/O, O/P, Bypass static switches and shall operate automatically. (a). SITC of UPS Battery : 02 Sets . Minimum VAH : 5000 The UPS battery shall be of Advanced Glass Mat Valve Regulated Sealed Lead Acid Battery Construction (AGM or VRSLAB) in ABS Flame retardant (UL94V-O) grade (UL 2436) spill containment casing to meet UL 62368-1 / IEC 62133 or equivalent standards type.​with suitable rating battery circuit breakers interconnection between the batteries cabling glanding and termination by copper conductor between battary bank and UPS alongwith battary rack. (b). SITC of Trasient voltage surge supperssors of minimuim 100kA for high surge supressions. | 1.00 | Job |  | 230000.00 | 230000.00 | 600000.00 | 600000.00 | 230000.00 | RANJIT SALES CORPORATION
56.00 | SH-VII : EARTHING & Lightning Conductor Earthing with copper earth plate 600mm x 600mm x 3mm thick, including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc.with charcoal/ coke and salt as required. | 4.00 | Set |  | 9000.00 | 36000.00 | 9000.00 | 36000.00 | 36000.00 | RANJIT SALES CORPORATION, K YHOME ENGINEERING AND CONSTRUCTION
57.00 | Earthing with GI earth plate 600mm x 600mm x 6mm thick, including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2.00 | Set |  | 4600.00 | 9200.00 | 7500.00 | 15000.00 | 9200.00 | RANJIT SALES CORPORATION
58.00 | Supply & fixing of 50 mm x 6mm copper strip in 65mm dia B- Class GI pipe from earth electrode as required. | 20.00 | Mtrs |  | 1700.00 | 34000.00 | 3000.00 | 60000.00 | 34000.00 | RANJIT SALES CORPORATION
59.00 | Providing & fixing of 25 mm x 5mm GI strip in 40mm dia B- Class GI pipe from earth electrode including connection with G.Inut,bolt,spring washer,excavation and refilling etc as required. | 25.00 | Mtrs |  | 370.00 | 9250.00 | 700.00 | 17500.00 | 9250.00 | RANJIT SALES CORPORATION
60.00 | Providing & fixing of 25mm x 5mm GI strip on surface or recess for earth connection as required. | 50.00 | Mtrs |  | 150.00 | 7500.00 | 450.00 | 22500.00 | 7500.00 | RANJIT SALES CORPORATION
61.00 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, G.I. tube, having single prong at top, with 85 mm dia 6 mm thick G.I. base plate including holes etc. complete as required. | 4.00 | Each |  | 320.00 | 1280.00 | 2000.00 | 8000.00 | 1280.00 | RANJIT SALES CORPORATION
62.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 25.00 | Mtrs |  | 850.00 | 21250.00 | 400.00 | 10000.00 | 10000.00 | K YHOME ENGINEERING AND CONSTRUCTION
63.00 | SH-VIII: SITC of Fire Alarm and Fire Detection System Supply , Installation, Testing and Commissioning of Fire Alarm and Fire Detection system consisting of the following components: (1) Microprocessor based Fire Alarm Control Panel , 8 zone, built in 24 volt battery supply with battery charger, Mains Power Supply 230 VAC ±5%, 50Hz, with necessary external and internal indicators and external and internal control switches (2) 15 nos of Optical type smoke detectors , 12/24 V Smoke detectors, (3) Dual LED lamp type Fire Response Indicators for (installation inside false ceilings) (4) Auto Dialer unit with keypad having storage capacity of minimum 10 nos emergency phone nos. and one voice message ( at least 20 sec recording time) and interconnection with fire alarm control panel as per specification complete along with GSM wireless terminal feature through incorporation of GSM Slot for using GSM Simcard for making incoming and outgoing calls. (5) Hooter / Buzzer 65 dB +/- 5 dB , 01 no. | 1.00 | Job |  | 160000.00 | 160000.00 | 137000.00 | 137000.00 | 137000.00 | K YHOME ENGINEERING AND CONSTRUCTION
| Total in Figures |  |  |  |  | 3878750.00 |  | 4451355.00
Lowest Amount Quoted BY: RANJIT SALES CORPORATION(3878750.00)

## BOQ Summary
BOQ Summary Details Tender Title: Electrical works for construction of new NDB building at Dimapur Airport Tender ID: 2020_AAI_50933_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RANJIT SALES CORPORATION | 3878750.00 | L1
| 2 | K YHOME ENGINEERING AND CONSTRUCTION | 4451355.00 | L2