## BoQ1
Government eProcurement System Created By: ARUN KUMAR K Created Date/Time: 05-Aug-2020 04:01 PM Tender Title: Replacement of old LT panels, Feeder pillars and LT cables at LGBI Airport, Guwahati Tender ID: 2020_AAI_50987_1
Tender Inviting Authority: Senior Manager (Engg – Elect), AAI, LGBI Airport, Guwahati, Assam – 781 015
Name of Work: Replacement of old LT Panels, Feeder Pillars and LT Cables at LGBI Airport, Guwahati Airport
Contract No: AAI/ENGG/SM(E-E)/GHY/NIT-01/2020-21
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | BR Power Control and Automation Services |  | Incotech Engineers Pvt Ltd |  | North Eastern Engineers |  | TECHNISYS ENGINEERING PRIVATE LIMITED |  | RIMA ELECTRICALS
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | FEEDER PILLAR Design, Fabrication, Supply, Installation, Testing & Commissioning of Outdoor type Feeder Pillar Panel (PTTA type construction) with enclosure protection class IP 54 of cubical construction, floor mounted, double door type with sloped roof, fabricated out of 2mm thick CRCA sheet, compartmentalised with hinged lockable doors, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, cable alley, interconnection of switchgears with suitable size solid aluminium strip / copper conductor cable, accessories of switchgear like rotary handles, spreader terminals, phase barriers, auxillary relays/contacts etc, terminal blocks/power connectors (nut bolt type), control wiring, protection MCBs, common G.I earth bar of size 25mm X 5 mm at the rear with 2 Nos. earth studs etc. complete in all respect and as per specification with following switchgears and components suitable for operation on 415V, 3 phase, 50Hz AC Supply etc including base channel and necessary PCC pedestal complete as required INCOMING (i) 200A, 36kA (Ics=100% Icu rating), TP MCCB with neutral link - 01 No. (ii) Three phase Digital VAF Meter with inbuilt selector switch, three nos of CTs of 200/5A, 15 VA, Class 1.0 etc. - 01 set. (iii) Set of LED type indicating lamps for R,Y,B, ON, OFF & TRIP - 01 set BUSBARS Set of Aluminium Bus Bar of 300A rating - 01 Set OUTGOINGS (i) 100A, 25kA (Ics=100% Icu rating), TP MCCB with neutral link - 01 No. (ii) 63A, 25kA (Ics=100% Icu rating), TP MCCB with neutral link - 03 No. (iii) Set of 40A TPN, 'C' Curve, 10kA MCB with 40A TP contractor (NO-NC), ON-OFF digital timer, Auto/Manual selector switch for auto/manual operation of following outgoing street lighting feeders through busbar/connector arrangement (a) 20A TPN, 'C' Curve, 10kA MCB - 03 No. (b) 16A DP, 'C' Curve, 10kA MCB - 02 Set. (iv) 40A TPN, 'C' Curve, 10kA MCB with 10 to 40Amp Three phase KWH meter (direct type) etc - 01 Set (v) 32A TPN, 'C' Curve, 10kA MCB - 02 No. | 1.00 | Set |  | 222798.00 | 222798.00 | 115815.00 | 115815.00 | 187640.00 | 187640.00 | 183562.00 | 183562.00 | 124000.00 | 124000.00 | 115815.00 | Incotech Engineers Pvt Ltd
2.00 | FEEDER PILLAR Design, Fabrication, Supply, Installation, Testing & Commissioning of Outdoor type Feeder Pillar Panel (PTTA type construction) with enclosure protection class IP 54 of cubical construction, floor mounted, double door type with sloped roof, fabricated out of 2mm thick CRCA sheet, compartmentalised with hinged lockable doors, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, cable alley, interconnection of switchgears with suitable size solid aluminium strip / copper conductor cable, accessories of switchgear like rotary handles, spreader terminals, phase barriers, auxillary relays/contacts etc, terminal blocks/power connectors (nut bolt type), control wiring, protection MCBs, common G.I earth bar of size 25mm X 5 mm at the rear with 2 Nos. earth studs etc. complete in all respect and as per specification with following switchgears and components suitable for operation on 415V, 3 phase, 50Hz AC Supply etc including base channel and necessary PCC pedestal complete as required INCOMING (i) 160A, 36kA (Ics=100% Icu rating), TP MCCB with neutral link etc - 02 No. (ii) Three phase Digital VAF Meter with inbuilt selector switch, three nos of CTs of 150/5A, 15 VA, Class 1.0 etc. - 02 set. (iii) Set of LED type indicating lamps for R,Y,B, ON, OFF & TRIP - 02 set (iv) Mechanical Interlocking arrangement between incomers with 2 lock and 1 key - 1 set BUSBARS Set of Aluminium Bus Bar of 200A rating - 01 Set OUTGOINGS (i) 100A, 25kA (Ics=100% Icu rating), TP MCCB with neutral link - 01 No. (ii) Set of 63A TPN, 'C' Curve, 10kA MCB with 60A TP contractor (NO-NC), ON-OFF digital timer, Auto/Manual selector switch for auto/manual operation of following outgoing street lighting feeders through busbar/connector arrangement (a) 40A TPN, 'C' Curve, 10kA MCB - 01 No. (b) 20A TPN, 'C' Curve, 10kA MCB - 03 No. (b) 16A DP, 'C' Curve, 10kA MCB - 02 No. (iii) 63A TPN, 'C' Curve, 10kA MCB - 01 set (iv) 40A TPN, 'C' Curve, 10kA MCB with 10 to 40Amp Three phase KWH meter (direct type) etc - 01 Set (v) 32A DP, 'C' Curve, 10kA MCB with 5 to 30Amp Single phase KWH meter (direct type) etc - 01 Set | 1.00 | Set |  | 179321.00 | 179321.00 | 121590.00 | 121590.00 | 165896.00 | 165896.00 | 184462.00 | 184462.00 | 129650.00 | 129650.00 | 121590.00 | Incotech Engineers Pvt Ltd
3.00 | FEEDER PILLAR Design, Fabrication, Supply, Installation, Testing & Commissioning of Outdoor type Feeder Pillar Panel (PTTA type construction) with enclosure protection class IP 54 of cubical construction, floor mounted, double door type with sloped roof, fabricated out of 2mm thick CRCA sheet, compartmentalised with hinged lockable doors, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, cable alley, interconnection of switchgears with suitable size solid aluminium strip / copper conductor cable, accessories of switchgear like rotary handles, spreader terminals, phase barriers, auxillary relays/contacts etc, terminal blocks/power connectors (nut bolt type), control wiring, protection MCBs, common G.I earth bar of size 25mm X 5 mm at the rear with 2 Nos. earth studs etc. complete in all respect and as per specification with following switchgears and components suitable for operation on 415V, 3 phase, 50Hz AC Supply etc including angle iron base with mounting legs (750mm height) and necessary PCC foundation complete as required INCOMING (i) 100A, 25kA (Ics=100% Icu rating), TP MCCB with neutral link - 01 No. (ii) Three phase Digital VAF Meter with inbuilt selector switch, three nos of CTs of 100/5A, 15 VA, Class 1.0 etc. - 01 set (iii) Set of LED type indicating lamps for R,Y,B, ON & OFF - 01 set BUSBARS Set of Aluminium Bus Bar of 200A rating - 01 Set OUTGOINGS (i) Set of 63A TPN, 'C' Curve, 10kA MCB with 60A TP contractor (NO-NC), ON-OFF digital timer, Auto/Manual selector switch for auto/manual operation of following outgoing street lighting feeders through busbar/connector arrangement (a) 32A TPN, 'C' Curve, 10kA MCB - 02 No. (b) 25A DP, 'C' Curve, 10kA MCB - 02 No. (ii) 32A TPN, 'C' Curve, 10kA MCB - 02 No. (iii) 25A DP, 'C' Curve, 10kA MCB - 02 No | 2.00 | Set |  | 120143.00 | 240286.00 | 65100.00 | 130200.00 | 100400.00 | 200800.00 | 137437.00 | 274874.00 | 72020.00 | 144040.00 | 130200.00 | Incotech Engineers Pvt Ltd
4.00 | FEEDER PILLAR Design, Fabrication, Supply, Installation, Testing & Commissioning of Outdoor type Feeder Pillar Panel (PTTA type construction) with enclosure protection class IP 54 of cubical construction, floor mounted, double door type with sloped roof, fabricated out of 2mm thick CRCA sheet, compartmentalised with hinged lockable doors, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, cable alley, interconnection of switchgears with suitable size solid aluminium strip / copper conductor cable, accessories of switchgear like rotary handles, spreader terminals, phase barriers, auxillary relays/contacts etc, terminal blocks/power connectors (nut bolt type), control wiring, protection MCBs, common G.I earth bar of size 25mm X 5 mm at the rear with 2 Nos. earth studs etc. complete in all respect and as per specification with following switchgears and components suitable for operation on 415V, 3 phase, 50Hz AC Supply etc including angle iron base with mounting legs (750mm height) and necessary PCC foundation complete as required INCOMING (i) 63A, 25kA (Ics=100% Icu rating), TP MCCB with neutral link - 01 No. (ii) Three phase Digital VAF Meter with inbuilt selector switch, three nos of CTs of 60/5A, 15 VA, Class 1.0 etc. - 01 set. (iii) Set of LED type indicating lamps for R,Y,B, ON & OFF - 01 set BUSBARS Set of Aluminium Bus Bar of 100A rating - 01 Set OUTGOINGS (i) 40A TPN, 'C' Curve, 10kA MCB with Star/Delta Starter consisting of suitable ratings of TP contractors (3 Nos), ON-OFF timer, O/L relay, Single Phasing Preventor, ON/OFF Pushbuttons, ON/OFF LED indication lamps etc suitable for operation of 12.5HP Pumpset - 02 set (ii) 32A TPN, 'C' Curve, 10kA MCB - 01 set (iii) 16A DP, 'C' Curve, 10kA MCB - 01 set | 2.00 | Set |  | 136001.00 | 272002.00 | 82425.00 | 164850.00 | 136050.00 | 272100.00 | 134687.00 | 269374.00 | 90100.00 | 180200.00 | 164850.00 | Incotech Engineers Pvt Ltd
5.00 | LT METERING PANEL Design, Fabrication, Supply, Installation, Testing and Commissioning of LT Metering Panel (PTTA type construction) indoor type with enclosure protection class IP 42 of cubical construction, wall mounted type (front accessable only), fabricated out of 2mm thick CRCA sheet, compartmentalised with hinged lockable doors with inspection glass window for energy meter compartment, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, cable alley, interconnection of switchgears with suitable size copper conductor cable, accessories of switchgear like rotary handles, spreader terminals, phase barriers, auxillary relays/contacts etc, terminal blocks/power connectors (nut bolt type), control wiring, protection MCBs, common G.I earth bar of size 25mm X 5 mm at the rear with 2 Nos. earth studs etc. complete in all respect and as per specification with following switchgears and components suitable for operation on 415V, 3 phase, 50Hz AC Supply etc complete as required INCOMING (i) 160A, 36kA (Ics=100% Icu rating), TP MCCB with neutral link - 01 No. (ii) Three phase Digital VAF Meter with inbuilt selector switch, three nos of CTs of 150/5A, 15 VA, Class 1.0 etc. - 01 set. (iii) Set of LED type indicating lamps for R,Y,B, ON & OFF - 01 set BUSBARS Set of Aluminium Bus Bar of 200A rating - 01 Set OUTGOINGS (i) 63A TPN, 'C' Curve, 10kA MCB with 10 to 60Amp Three phase, 4 wire KWH meter (direct type) - 01 Set (ii) 40A TPN, 'C' Curve, 10kA MCB with 10 to 40Amp Three phase, 4 wire KWH meter (direct type) - 01 Set (iii) 25A TPN, 'C' Curve, 10kA MCB with 5 to 20Amp Three phase, 4 wire KWH meter (direct type) - 02 Set (iV) 32A DP, 'C' Curve, 10kA MCB with 5 to 30Amp Single phase KWH meter (direct type) - 05 Set (V) 40A TPN, 'C' Curve, 10kA MCB - 01 No. (vi) 32A DP, 'C' Curve, 10kA MCB - 01 No. | 1.00 | Set |  | 201702.00 | 201702.00 | 78750.00 | 78750.00 | 158935.00 | 158935.00 | 128037.00 | 128037.00 | 112700.00 | 112700.00 | 78750.00 | Incotech Engineers Pvt Ltd
6.00 | STARTER PANEL Design, Fabrication, Supply, Installation, Testing and Commissioning of D.O.L Starter Panel indoor type with enclosure protection class IP 42, wall mounting type, fabricated out of 2mm thick CRCA sheet, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, interconnection of switchgears with suitable size copper conductor cable, auxillary relays/contacts, terminal blocks/power connectors (nut bolt type), control wiring, protection MCBs etc. complete in all respect and as per specification with following switchgears and components suitable for operation on 415V, 3 phase, 50Hz AC Supply etc complete as required INCOMING (i) 63A TPN, 'C' Curve, 10kA MCB - 01 No. (ii) LED type indicating lamps for R,Y,B - 01 set OUTGOING (i) 32A TPN, 'C' Curve, 10kA MCB with DOL Starter consisting of suitable rating TP contractor, O/L relay, Single Phasing Preventor, ON/OFF Pushbuttons, ON/OFF LED indication lamps etc suitable for 7.5HP Pumpset - 02 set | 1.00 | Set |  | 73862.00 | 73862.00 | 40740.00 | 40740.00 | 57100.00 | 57100.00 | 38825.00 | 38825.00 | 41510.00 | 41510.00 | 38825.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
7.00 | Supply of following sizes LT power cables of 1.1 KV grade aluminium conductor XLPE insulated and PVC sheathed armoured cable confirming to IS 7098 Part I-1988 with upto date amendment as required.
7.01 | 3.5C x 95 sq. mm. | 490.00 | Meter |  | 328.00 | 160720.00 | 323.40 | 158466.00 | 324.00 | 158760.00 | 289.00 | 141610.00 | 632.00 | 309680.00 | 141610.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
7.02 | 3.5C x 50 sq. mm. | 100.00 | Meter |  | 200.00 | 20000.00 | 196.35 | 19635.00 | 204.00 | 20400.00 | 176.00 | 17600.00 | 405.00 | 40500.00 | 17600.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
7.03 | 3.5C x 35 sq. mm. | 225.00 | Meter |  | 154.00 | 34650.00 | 161.70 | 36382.50 | 156.00 | 35100.00 | 136.00 | 30600.00 | 324.00 | 72900.00 | 30600.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
7.04 | 3.5C x 25 sq. mm. | 215.00 | Meter |  | 129.00 | 27735.00 | 127.05 | 27315.75 | 132.00 | 28380.00 | 114.00 | 24510.00 | 280.00 | 60200.00 | 24510.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
7.05 | 4C x 10 sq. mm. | 1245.00 | Meter |  | 90.00 | 112050.00 | 88.94 | 110730.30 | 90.00 | 112050.00 | 79.00 | 98355.00 | 185.00 | 230325.00 | 98355.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
8.00 | Supply of following sizes of HDPE (High Density Polyethylene) pipe of grade PE80, PN6 ISI marked conforming to IS 4984:1995, complete as required.
8.01 | 50mm (OD) | 1200.00 | Meter |  | 47.00 | 56400.00 | 94.25 | 113100.00 | 98.00 | 117600.00 | 62.50 | 75000.00 | 76.50 | 91800.00 | 56400.00 | BR Power Control and Automation Services
8.02 | 63mm (OD) | 235.00 | Meter |  | 59.00 | 13865.00 | 149.25 | 35073.75 | 165.00 | 38775.00 | 81.20 | 19082.00 | 109.00 | 25615.00 | 13865.00 | BR Power Control and Automation Services
9.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board (IP 43), 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing, finishing around the DB with cement plaster, putty, painting etc complete as required as per actual site requirements (But without MCB/RCCB/Isolator)
9.01 | 8 way, Double door | 5.00 | Set |  | 1207.00 | 6035.00 | 1372.00 | 6860.00 | 1232.00 | 6160.00 | 1020.00 | 5100.00 | 1322.00 | 6610.00 | 5100.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
9.02 | 12 way, Double door | 5.00 | Set |  | 1497.00 | 7485.00 | 1696.30 | 8481.50 | 1488.00 | 7440.00 | 1225.00 | 6125.00 | 1507.00 | 7535.00 | 6125.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
10.00 | Supplying and fixing Cable End Boxes (IP 43) suitable for following single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, including finishing around the end box with cement plaster, putty, painting etc complete as required as per actual site requirements.
10.01 | For 8 way, Double door SPN MCB DB | 4.00 | Each |  | 825.00 | 3300.00 | 562.40 | 2249.60 | 504.00 | 2016.00 | 446.00 | 1784.00 | 760.00 | 3040.00 | 1784.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
10.02 | For 12 way, Double door SPN MCB DB | 4.00 | Each |  | 909.00 | 3636.00 | 663.00 | 2652.00 | 564.00 | 2256.00 | 506.00 | 2024.00 | 807.00 | 3228.00 | 2024.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
11.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board (IP 43), 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing, finishing around the DB with cement plaster, putty, painting etc complete as required as per actual site requirements. (But without MCB/RCCB/Isolator)
11.01 | 4 way (4 + 12), Double door | 4.00 | Set |  | 2140.00 | 8560.00 | 2624.00 | 10496.00 | 2296.00 | 9184.00 | 1947.00 | 7788.00 | 2106.00 | 8424.00 | 7788.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
11.02 | 6 way (4 + 18), Double door | 1.00 | Set |  | 2596.00 | 2596.00 | 3220.00 | 3220.00 | 2832.00 | 2832.00 | 2340.00 | 2340.00 | 2516.00 | 2516.00 | 2340.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
11.03 | 8 way (4 + 24), Double door | 5.00 | Set |  | 3152.00 | 15760.00 | 3834.00 | 19170.00 | 3612.00 | 18060.00 | 2972.00 | 14860.00 | 3087.00 | 15435.00 | 14860.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
12.00 | Supplying and fixing Cable End Boxes (IP 43) suitable for following triple pole and neutral, sheet steel, MCB distribution board (Horizontal Type), 415 volts, on surface/ recess, including finishing around the end box with cement plaster, putty, painting etc complete as required as per actual site requirements.
12.01 | For 4 way, Double door TPN MCB DB | 3.00 | Each |  | 813.00 | 2439.00 | 774.00 | 2322.00 | 637.00 | 1911.00 | 683.00 | 2049.00 | 949.00 | 2847.00 | 1911.00 | North Eastern Engineers
12.02 | For 6 way, Double door TPN MCB DB | 1.00 | Each |  | 919.00 | 919.00 | 923.00 | 923.00 | 798.00 | 798.00 | 742.00 | 742.00 | 997.00 | 997.00 | 742.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
12.03 | For 8 way, Double door TPN MCB DB | 5.00 | Each |  | 1048.00 | 5240.00 | 1417.00 | 7085.00 | 1330.00 | 6650.00 | 1302.00 | 6510.00 | 1446.00 | 7230.00 | 5240.00 | BR Power Control and Automation Services
13.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel (IP 43), dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB’s (but without MCB’s and incomer ), finishing around the DB with cement plaster, putty, painting etc as required. as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
13.01 | 4 way (4 + 12), Double door | 4.00 | Set |  | 5625.00 | 22500.00 | 4960.00 | 19840.00 | 5744.00 | 22976.00 | 5197.00 | 20788.00 | 5098.00 | 20392.00 | 19840.00 | Incotech Engineers Pvt Ltd
13.02 | 8 way (4 + 24), Double door | 7.00 | Set |  | 7044.00 | 49308.00 | 6167.00 | 43169.00 | 7697.00 | 53879.00 | 6615.00 | 46305.00 | 6308.00 | 44156.00 | 43169.00 | Incotech Engineers Pvt Ltd
14.00 | Supplying and fixing Cable End Boxes (IP 43) suitable for tripple pole and neutral, sheet steel, 4/8 way Vertical MCB distribution board, 415 volts, on surface/ recess including finishing around the end box with cement plaster, putty, painting etc complete as required as per actual site requirements. | 7.00 | Each |  | 1231.00 | 8617.00 | 912.00 | 6384.00 | 567.00 | 3969.00 | 1833.00 | 12831.00 | 1874.00 | 13118.00 | 3969.00 | North Eastern Engineers
15.00 | Supplying and fixing 5 amps to 32 amps rating, single pole, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 358.00 | Each |  | 151.00 | 54058.00 | 143.00 | 51194.00 | 126.00 | 45108.00 | 130.00 | 46540.00 | 198.00 | 70884.00 | 45108.00 | North Eastern Engineers
16.00 | Supplying and fixing following rating, double pole, 240 volts, 'C' curve MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required.
16.01 | 40 amps | 7.00 | Each |  | 654.00 | 4578.00 | 681.00 | 4767.00 | 788.00 | 5516.00 | 667.00 | 4669.00 | 854.00 | 5978.00 | 4578.00 | BR Power Control and Automation Services
16.02 | 63 amps | 7.00 | Each |  | 738.00 | 5166.00 | 681.00 | 4767.00 | 788.00 | 5516.00 | 667.00 | 4669.00 | 854.00 | 5978.00 | 4669.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
17.00 | Supplying and fixing following rating, three pole, 240 volts, 'C' curve MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required.
17.01 | 40 amps | 33.00 | Each |  | 996.00 | 32868.00 | 1045.00 | 34485.00 | 980.00 | 32340.00 | 1035.00 | 34155.00 | 1186.00 | 39138.00 | 32340.00 | North Eastern Engineers
18.00 | Supplying and fixing following rating, four pole, 415 volts, 'C' curve MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required.
18.01 | 63 amps | 17.00 | Each |  | 1395.00 | 23715.00 | 1050.00 | 17850.00 | 1400.00 | 23800.00 | 1320.00 | 22440.00 | 1444.00 | 24548.00 | 17850.00 | Incotech Engineers Pvt Ltd
18.02 | 100 amps | 6.00 | Each |  | 6256.00 | 37536.00 | 5456.00 | 32736.00 | 6563.00 | 39378.00 | 5850.00 | 35100.00 | 6126.00 | 36756.00 | 32736.00 | Incotech Engineers Pvt Ltd
19.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 500.00 | Each |  | 28.00 | 14000.00 | 52.00 | 26000.00 | 9.00 | 4500.00 | 11.00 | 5500.00 | 16.00 | 8000.00 | 4500.00 | North Eastern Engineers
20.00 | Supplying and fixing 100A, 25kA (Ics=100% Icu rating), TP MCCB and terminal spreaders in sheet steel enclosure suitable for wall mounting including accessories like rotary handle, spreader links, neutral link etc including drilling holes in cubicle panel and to be mounted on wall etc. complete as required. | 1.00 | Each |  | 4082.00 | 4082.00 | 8058.00 | 8058.00 | 5353.00 | 5353.00 | 4241.00 | 4241.00 | 5806.00 | 5806.00 | 4082.00 | BR Power Control and Automation Services
21.00 | Fabrication, Supply and installation of 18 SWG MS sheet metal work for covering of open cable ducts / boxes etc as per actual site requirement including cutting, bending, drilling, fixing with screws etc complete with all accessories including painting as reqd. | 20.00 | Sq.m |  | 6118.00 | 122360.00 | 988.00 | 19760.00 | 900.00 | 18000.00 | 562.00 | 11240.00 | 552.00 | 11040.00 | 11040.00 | RIMA ELECTRICALS
22.00 | Supply and fixing of side hinged-door fixed with base SMC junction Box of size 250mmx200mmx100mm (Loop-in-Loop-out Box) on the GI pole with suitable size MS clamp including providing & fixing 63A, 4Pole connector for loop in & loop out to terminate 2Nos, 4 core 10/16/25 sq. mm. armoured aluminum cable, 6Amp SP MCB 'C' curve in din rail, Interconnection etc. as required. (Make: Sintex: model no. JS-JB-2520 or its equivalent) | 38.00 | Set |  | 1118.00 | 42484.00 | 2394.00 | 90972.00 | 630.00 | 23940.00 | 1096.00 | 41648.00 | 1656.00 | 62928.00 | 23940.00 | North Eastern Engineers
23.00 | Supply and fixing of side hinged-door fixed with base SMC junction Box of size 270mmx225mmx135mm (Loop-in-Loop-out Box) in ground including providing necessary angle iron legs (upto 750mm height) and concrete pedestal, providing & fixing 2 Nos of 63A, 4Pole connector for loop in & loop out to terminate 3Nos, 4 core 10/16/25 sq. mm. armoured aluminum cable, 6Amp SP MCB 'C' curve in din rail, Interconnection etc. as required. (Make: Sintex: model no. JS-JB-3126 or its equivalent) | 1.00 | Set |  | 1289.00 | 1289.00 | 4410.00 | 4410.00 | 1800.00 | 1800.00 | 1563.00 | 1563.00 | 2382.00 | 2382.00 | 1289.00 | BR Power Control and Automation Services
24.00 | Supply and fixing of 63A, 4Pole heavy duty power connector/stud (nut & bolt type) for loop in & loop out to terminate 2Nos, 4 core 10/16/25 sq. mm. armoured aluminum cable, 6Amp SP MCB 'C' curve in din rail, interconnection etc.in the existing octagonal pole | 52.00 | Set |  | 291.00 | 15132.00 | 3600.00 | 187200.00 | 950.00 | 49400.00 | 9625.00 | 500500.00 | 426.00 | 22152.00 | 15132.00 | BR Power Control and Automation Services
25.00 | Supply and fixing of following ratings of Three Pole Power contactor with auxillary contacts (min 1NO+1NC), 230V AC 50Hz coil etc on the existing APFC panel including interconnection between MCB, contactor & capacitor with required length of suitable size single core copper wire, termination with copper lugs etc complete as required
25.01 | 45A (AC3 rating at 415V), Three Pole Power Contactor (Make : Siemens 3TF4602-0A..ZA01) | 5.00 | Each |  | 3799.00 | 18995.00 | 4604.00 | 23020.00 | 5058.00 | 25290.00 | 15063.00 | 75315.00 | 5572.00 | 27860.00 | 18995.00 | BR Power Control and Automation Services
25.02 | 22A (AC3 rating at 415V), Three Pole Power Contactor (Make : Siemens 3TF3300-0A) | 2.00 | Each |  | 1022.00 | 2044.00 | 1087.00 | 2174.00 | 1116.00 | 2232.00 | 8560.00 | 17120.00 | 1956.00 | 3912.00 | 2044.00 | BR Power Control and Automation Services
25.03 | 12A (AC3 rating at 415V), Three Pole Power Contactor (Make : Siemens 3TF3110-0A) | 2.00 | Each |  | 797.00 | 1594.00 | 810.00 | 1620.00 | 810.00 | 1620.00 | 7377.00 | 14754.00 | 1560.00 | 3120.00 | 1594.00 | BR Power Control and Automation Services
26.00 | Supplying of 300 mm width X 50 mm depth X 1.6 mm thickness perforated Hot Dipped Galvanised Iron cable tray with perforation not more than 17.5% in convenient sections including accessories like bend etc complete as required. | 50.00 | Meter |  | 1273.00 | 63650.00 | 404.00 | 20200.00 | 475.00 | 23750.00 | 450.00 | 22500.00 | 915.00 | 45750.00 | 20200.00 | Incotech Engineers Pvt Ltd
27.00 | Installation of perforated Galvanised Iron cable tray of following sizes including providing connectors, M.S angles/threaded rod supports for fixing on wall/ceiling including G.I. bolts & nuts, anchor fastners, painting of supports etc as required. (Supply of cable tray is excluded)
27.01 | 450 mm width X 50 mm depth X 2.0 mm thickness | 15.00 | Meter |  | 117.00 | 1755.00 | 210.00 | 3150.00 | 430.00 | 6450.00 | 50.00 | 750.00 | 1210.00 | 18150.00 | 750.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
27.02 | 300 mm width X 50 mm depth X 1.6 mm thickness | 50.00 | Meter |  | 105.00 | 5250.00 | 168.00 | 8400.00 | 290.00 | 14500.00 | 45.00 | 2250.00 | 865.00 | 43250.00 | 2250.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
27.03 | 150 mm width X 50 mm depth X 1.6 mm thickness | 75.00 | Meter |  | 94.00 | 7050.00 | 126.00 | 9450.00 | 200.00 | 15000.00 | 35.00 | 2625.00 | 667.00 | 50025.00 | 2625.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
28.00 | Installation of departmentally supplied PVC Cable Management System upto 100mm width with base and lid along with accessories for fixing on surface / recess including cutting the wall and making good the damages in case of recessed installation as required. | 50.00 | Meter |  | 117.00 | 5850.00 | 63.00 | 3150.00 | 270.00 | 13500.00 | 450.00 | 22500.00 | 213.00 | 10650.00 | 3150.00 | Incotech Engineers Pvt Ltd
29.00 | Laying of DWC/HDPE (High Density Polyethylene) upto 110mm dia duct direct in ground up to a depth of 75 cm including cutting, providing accessories like couplers and adhesive/solvent for jointing, excavation and refilling the trench etc. complete as required. | 1125.00 | Meter |  | 140.00 | 157500.00 | 100.00 | 112500.00 | 36.00 | 40500.00 | 125.00 | 140625.00 | 142.00 | 159750.00 | 40500.00 | North Eastern Engineers
30.00 | Laying of DWC/HDPE (High Density Polyethylene) upto 110mm dia duct under hard/concrete/bituminous surface upto a depth of 45cm including cutting, providing accessories like couplers and adhesive/solvent for jointing, dismantling/breaking all types of surfaces, refilling the trench, repairing and finishing the top surface of excavated area with 6" thick cement concrete etc. complete as required. | 370.00 | Meter |  | 234.00 | 86580.00 | 42.00 | 15540.00 | 50.00 | 18500.00 | 125.00 | 46250.00 | 559.00 | 206830.00 | 15540.00 | Incotech Engineers Pvt Ltd
31.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC/ HUME/ METAL pipe/covered cable trench as required.
31.01 | Upto 35 sq.mm. | 1270.00 | Meter |  | 23.00 | 29210.00 | 23.00 | 29210.00 | 52.00 | 66040.00 | 50.00 | 63500.00 | 101.00 | 128270.00 | 29210.00 | BR Power Control and Automation Services, Incotech Engineers Pvt Ltd
31.02 | Above 35 sq. mm and upto 95 sq. mm | 350.00 | Meter |  | 23.00 | 8050.00 | 44.00 | 15400.00 | 75.00 | 26250.00 | 78.00 | 27300.00 | 101.00 | 35350.00 | 8050.00 | BR Power Control and Automation Services
31.03 | Above 185 sq. mm and upto 400 sq. mm | 75.00 | Meter |  | 70.00 | 5250.00 | 105.00 | 7875.00 | 135.00 | 10125.00 | 288.00 | 21600.00 | 101.00 | 7575.00 | 5250.00 | BR Power Control and Automation Services
32.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
32.01 | Upto 35 sq.mm. | 180.00 | Meter |  | 23.00 | 4140.00 | 26.00 | 4680.00 | 54.00 | 9720.00 | 50.00 | 9000.00 | 78.00 | 14040.00 | 4140.00 | BR Power Control and Automation Services
32.02 | Above 35 sq. mm and upto 95 sq. mm | 25.00 | Meter |  | 23.00 | 575.00 | 47.00 | 1175.00 | 60.00 | 1500.00 | 78.00 | 1950.00 | 78.00 | 1950.00 | 575.00 | BR Power Control and Automation Services
32.03 | Above 185 sq. mm and upto 400 sq. mm | 10.00 | Meter |  | 23.00 | 230.00 | 105.00 | 1050.00 | 8.00 | 80.00 | 288.00 | 2880.00 | 78.00 | 780.00 | 80.00 | North Eastern Engineers
33.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
33.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 135.00 | Meter |  | 82.00 | 11070.00 | 26.00 | 3510.00 | 54.00 | 7290.00 | 50.00 | 6750.00 | 113.50 | 15322.50 | 3510.00 | Incotech Engineers Pvt Ltd
33.02 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 185.00 | Meter |  | 175.00 | 32375.00 | 47.00 | 8695.00 | 60.00 | 11100.00 | 78.00 | 14430.00 | 118.50 | 21922.50 | 8695.00 | Incotech Engineers Pvt Ltd
33.03 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 165.00 | Meter |  | 292.00 | 48180.00 | 105.00 | 17325.00 | 80.00 | 13200.00 | 288.00 | 47520.00 | 157.00 | 25905.00 | 13200.00 | North Eastern Engineers
34.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
34.01 | 4 x 10/16 sq. mm. | 5.00 | Set |  | 1732.00 | 8660.00 | 1680.00 | 8400.00 | 3600.00 | 18000.00 | 521.00 | 2605.00 | 1836.00 | 9180.00 | 2605.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
35.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.
35.01 | 3.5 x 240 Sqmm. | 4.00 | Set |  | 1573.00 | 6292.00 | 1293.00 | 5172.00 | 630.00 | 2520.00 | 2970.00 | 11880.00 | 524.00 | 2096.00 | 2096.00 | RIMA ELECTRICALS
35.02 | 3.5 x 120 Sqmm. | 1.00 | Set |  | 1481.00 | 1481.00 | 727.00 | 727.00 | 540.00 | 540.00 | 1944.00 | 1944.00 | 276.00 | 276.00 | 276.00 | RIMA ELECTRICALS
35.03 | 3.5 x 95 Sqmm. | 6.00 | Set |  | 665.00 | 3990.00 | 656.00 | 3936.00 | 540.00 | 3240.00 | 1120.00 | 6720.00 | 230.00 | 1380.00 | 1380.00 | RIMA ELECTRICALS
35.04 | 3.5 x 50 Sqmm. | 5.00 | Set |  | 1154.00 | 5770.00 | 373.00 | 1865.00 | 460.00 | 2300.00 | 812.00 | 4060.00 | 128.00 | 640.00 | 640.00 | RIMA ELECTRICALS
35.05 | 3.5 x 35 sq. mm. | 14.00 | Set |  | 869.00 | 12166.00 | 361.00 | 5054.00 | 410.00 | 5740.00 | 729.00 | 10206.00 | 110.00 | 1540.00 | 1540.00 | RIMA ELECTRICALS
35.06 | 3.5 x 25 sq. mm. | 32.00 | Set |  | 565.00 | 18080.00 | 258.00 | 8256.00 | 400.00 | 12800.00 | 417.00 | 13344.00 | 99.00 | 3168.00 | 3168.00 | RIMA ELECTRICALS
35.07 | 4 x 16 sq. mm. | 22.00 | Set |  | 389.00 | 8558.00 | 248.00 | 5456.00 | 300.00 | 6600.00 | 417.00 | 9174.00 | 76.50 | 1683.00 | 1683.00 | RIMA ELECTRICALS
35.08 | 4 x 10 sq. mm. | 60.00 | Set |  | 288.00 | 17280.00 | 225.00 | 13500.00 | 300.00 | 18000.00 | 417.00 | 25020.00 | 76.50 | 4590.00 | 4590.00 | RIMA ELECTRICALS
35.09 | 2 X 35 sq. mm | 2.00 | Set |  | 621.00 | 1242.00 | 241.00 | 482.00 | 300.00 | 600.00 | 267.00 | 534.00 | 99.00 | 198.00 | 198.00 | RIMA ELECTRICALS
35.10 | 2 X 25 sq. mm | 2.00 | Set |  | 406.00 | 812.00 | 231.00 | 462.00 | 300.00 | 600.00 | 259.00 | 518.00 | 76.50 | 153.00 | 153.00 | RIMA ELECTRICALS
35.11 | 2 X 16 sq. mm | 7.00 | Set |  | 292.00 | 2044.00 | 166.00 | 1162.00 | 300.00 | 2100.00 | 236.00 | 1652.00 | 71.00 | 497.00 | 497.00 | RIMA ELECTRICALS
35.12 | 2 X 10 sq. mm | 3.00 | Set |  | 277.00 | 831.00 | 163.00 | 489.00 | 300.00 | 900.00 | 202.00 | 606.00 | 57.00 | 171.00 | 171.00 | RIMA ELECTRICALS
36.00 | Earthing with G.l. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/coke and salt as required. | 12.00 | Set |  | 6423.00 | 77076.00 | 5796.00 | 69552.00 | 7200.00 | 86400.00 | 6625.00 | 79500.00 | 8150.00 | 97800.00 | 69552.00 | Incotech Engineers Pvt Ltd
37.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 90.00 | Meter |  | 263.00 | 23670.00 | 483.00 | 43470.00 | 270.00 | 24300.00 | 540.00 | 48600.00 | 133.00 | 11970.00 | 11970.00 | RIMA ELECTRICALS
38.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 60.00 | Meter |  | 205.00 | 12300.00 | 133.00 | 7980.00 | 270.00 | 16200.00 | 131.00 | 7860.00 | 133.00 | 7980.00 | 7860.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
39.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 1830.00 | Meter |  | 32.00 | 58560.00 | 23.00 | 42090.00 | 10.00 | 18300.00 | 27.50 | 50325.00 | 17.00 | 31110.00 | 18300.00 | North Eastern Engineers
40.00 | Retrieving of one number PVC/XLPE insulated and PVC sheathed aluminium conductor armoured cable of grade not exceeding 1.1KV of cable size not exceeding 400 Sq.mm from the exising open duct / covered trench / RCC pipe / GI pipe, including removal of terminations, shifting and handing over of dismantled items to AAI store/dismantled store etc upto a distance not more than 250 mtrs. | 150.00 | Meter |  | 122.00 | 18300.00 | 42.00 | 6300.00 | 100.00 | 15000.00 | 80.00 | 12000.00 | 104.00 | 15600.00 | 6300.00 | Incotech Engineers Pvt Ltd
41.00 | Dismantling of existing Feeder Pillars of all types and sizes from its location i/c removal of cable termination, shifting and handing over to AAI store/dismantled yard upto a distance not more than 250 mtrs. | 4.00 | Job |  | 1836.00 | 7344.00 | 1050.00 | 4200.00 | 4900.00 | 19600.00 | 10000.00 | 40000.00 | 1065.00 | 4260.00 | 4200.00 | Incotech Engineers Pvt Ltd
42.00 | Dismantling of existing MCB Distribution boxes of all types (SPN/TPN Horizontal/vertical upto 12way) from its location i/c removal of loose wire box (if reqd), MCBs, cable termination, filling excess gaps with cement concrete and finishing the same with plastering, shifting and handing over of dismantled items to AAI store/dismantled store etc upto a distance not more than 250 mtrs. | 28.00 | Job |  | 184.00 | 5152.00 | 420.00 | 11760.00 | 200.00 | 5600.00 | 8000.00 | 224000.00 | 267.00 | 7476.00 | 5152.00 | BR Power Control and Automation Services
| Total in Figures |  |  |  |  | 2888010.00 |  | 2296136.40 |  | 2512305.00 |  | 3417569.00 |  | 3016418.00
Lowest Amount Quoted BY: Incotech Engineers Pvt Ltd(2296136.40)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of old LT panels, Feeder pillars and LT cables at LGBI Airport, Guwahati Tender ID: 2020_AAI_50987_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Incotech Engineers Pvt Ltd | 2296136.40 | L1
| 2 | North Eastern Engineers | 2512305.00 | L2
| 3 | BR Power Control and Automation Services | 2888010.00 | L3
| 4 | RIMA ELECTRICALS | 3016418.00 | L4
| 5 | TECHNISYS ENGINEERING PRIVATE LIMITED | 3417569.00 | L5