## BoQ1
Government eProcurement System Created By: K SANTHOSH KUMAR Created Date/Time: 14-Jul-2020 12:14 PM Tender Title: AMC Fire Hydrant with Sprinkler System Tender ID: 2020_AAI_51159_1
Tender Inviting Authority: Asstt. Gen. Mgr. (E-E), NATS Complex, IGI Airport, New Delhi
Name of Work : AMC of Fire Hydrant with Sprinkler System for 02 years at NATS Complex, IGI Airport, New Delhi (2020-22).
Contract No/Tender ID : 2020_AAI_51159_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals |  | Katyayni Engineering And Services
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | FIRE HYDRANT SYSTEM
2.00 | 1. Monthly site visit by experienced staff for the inspection of entire Fire fighting and sprinkler System including cleaning, oiling and greasing of Pumps, valves, etc. attending all complaints/breakdown during that Month and also carry out all the checks/preventive maintenance works as per enclosed schedule (Annexure-A) and submitting report of the entire Fire Hydrant with sprinkler System. | 24.00 | Nos. | 100.00 | 16000.00 | 384000.00 | 2500.00 | 60000.00 | 60000.00 | Katyayni Engineering And Services
3.00 | SPARES/ ACCESSORIES/ MAJOR REPAIRS(if any) (As and when required)
4.00 | 2. Supply and installation of following fire fighting component/spares including all accessories such as screwed/welded flanges etc. i/c dissmantling of the existing component along with accessories( if any )complete including painting, welding, jointing and neoprene gasket, nuts, bolts, washer etc. complete as required and as per relevant IS.
4.01 | (a) 200 mm dia flanged CI Foot Valve (As per IS 4038). Make : Kirloskar or any make as per Approved Make List. | 4.00 | Nos. | 100.00 | 2000.00 | 8000.00 | 13500.00 | 54000.00 | 8000.00 | Manish Electricals
4.02 | (b) 150 mm dia CI Non Return Valve (CIDF Swing Type, PN 1.0, IS 5312, Part I & II, Bronze to Rubber rings/ SS 410 Hinge Pin construction). Make : Kirloskar or any make as per Approved Make List. | 3.00 | Nos. | 10.00 | 9000.00 | 27000.00 | 16073.00 | 48219.00 | 27000.00 | Manish Electricals
4.03 | (c) 100 mm dia C I Spindle Sluice Valve (CIDF Non rising Type, PN 1.6, IS 14846, Part I & II, Bronze rings/SS 410 shaft). (ISI Marked). Make : Kirloskar or any make as per Approved Make List. | 2.00 | Nos. | 10.00 | 9000.00 | 18000.00 | 9500.00 | 19000.00 | 18000.00 | Manish Electricals
4.04 | (d) 50 mm dia C I Spindle Sluice Valve (CIDF Non rising Type, PN 1.6, IS 14846, Part I & II, Bronze rings/SS 410 shaft). (ISI Marked). Make : Kirloskar or any make as per Approved Make List. | 2.00 | Nos. | 10.00 | 3500.00 | 7000.00 | 4100.00 | 8200.00 | 7000.00 | Manish Electricals
4.05 | (e) 150 mm dia C I Spindle Sluice Valve (CIDF Non rising Type, PN 1.6, IS 14846, Part I&II, Bronze rings /SS 410 shaft). (ISI Marked). Make : Kirloskar or any make as per Approved Make List. | 2.00 | Nos. | 10.00 | 12000.00 | 24000.00 | 13500.00 | 27000.00 | 24000.00 | Manish Electricals
5.00 | 3. Supply and installation of the following fire fighting component/spares including all forged fittings and accessories such as screwed/welded flanges, tees, reducers etc. (if any) i/c dissmantling of the existing component along with accessories( if any), complete including painting, welding, jointing and Providing of neoprene gaskets, nuts, bolts ,washer etc., if required and as per direction of Engineer In Charge, and making good the same complete as required.
5.01 | (a) Gun metal ball Valve(25 mm dia). Make -ZOLOTO or any make as per Approved Make List. | 15.00 | Nos. | 100.00 | 500.00 | 7500.00 | 650.00 | 9750.00 | 7500.00 | Manish Electricals
5.02 | (b) Gun metal Single hydrant Valve ( ISI marked, IS 5290). Make -New age/Guards or any make as per Approved Make List. | 8.00 | Nos. | 10.00 | 1200.00 | 9600.00 | 6800.00 | 54400.00 | 9600.00 | Manish Electricals
5.03 | (c) Gun Metal lugs for Hydrant valves. Make -New age/Guards or any make as per Approved Make List. | 10.00 | Nos. | 10.00 | 1500.00 | 15000.00 | 650.00 | 6500.00 | 6500.00 | Katyayni Engineering And Services
6.00 | 4. Supply and Installation of First Aid rubber Hose reel tube, 30 Mtr. Length, ISI mark including dismantling the existing tube Make - New age/Guards or any make as per Approved Make List. | 2.00 | Nos. | 100.00 | 9000.00 | 18000.00 | 5000.00 | 10000.00 | 10000.00 | Katyayni Engineering And Services
7.00 | 5. Rewinding of motor of 15 KW, 2900 RPM of jockey pump including overhauling/ servicing, varnishing, baking, applying moisture proof varnish, assembling, testing, decoupling and coupling, loading / unloading and transportation to and from the site complete. ( Old defective winding shall be retained by Agency). | 2.00 | Job | 10.00 | 15000.00 | 30000.00 | 25000.00 | 50000.00 | 30000.00 | Manish Electricals
8.00 | 6. Providing and fixing of Gun metal female delivery hoss coupling, 63 mm ISI as per IS : 903 i/c dismantling of existing coupling (if any). Make - New age/Guards or any make as per Approved Make List. | 5.00 | Nos. | 10.00 | 2000.00 | 10000.00 | 2000.00 | 10000.00 | 10000.00 | Katyayni Engineering And Services, Manish Electricals
9.00 | 7. Providing and fixing of First Aid Hose Reel PVC Nozzle 20 mm i/c dismantling of existing nozzle(if any) .Make -as per Approved Make List. | 10.00 | Nos. | 10.00 | 800.00 | 8000.00 | 350.00 | 3500.00 | 3500.00 | Katyayni Engineering And Services
10.00 | 8. Repair of jockey pump motor of flow rate of 3 litre / second, 105 meter head including supply and replacement of bearing of suitable size shaft repair, impeller repair, stud and threading, coupling, oiling, greasing & glandory, including labour charges, loading / unloading, transportaion to & from the site etc. complete. | 2.00 | Job | 100.00 | 3000.00 | 6000.00 | 30000.00 | 60000.00 | 6000.00 | Manish Electricals
11.00 | 9. Painting of existing fire hydrant pipelines inside & outside at NATS Complex with (one or more coats on old work) synthetic enamel paint of approved brand and manufacture of required colour to give an even shade. | 100.00 | Sqm | 10.00 | 210.00 | 21000.00 | 50.00 | 5000.00 | 5000.00 | Katyayni Engineering And Services
12.00 | 10. Providing and fixing glazing in internal & external fire hydrant boxes with EPDM rubber/ neoprene gasket etc. complete as per the architectural drawings and the directions of Engineer-In-Charge. With float glass panes of 5.50 mm thickness. | 30.00 | Sqm | 10.00 | 400.00 | 12000.00 | 580.00 | 17400.00 | 12000.00 | Manish Electricals
13.00 | 11. Painting of existing external fire hydrants hose pipe cabinet (external site only ) and adjacent hydrant post of 80 -100 mm dia. Upto 01 meter and valve etc. including supporting structure with 02 coat of red oxide primer and 01 coat of enamel paint including scrapping, cleaning etc. complete as required as per site condition. | 10.00 | Job | 10.00 | 400.00 | 4000.00 | 50.00 | 500.00 | 500.00 | Katyayni Engineering And Services
14.00 | 12. Painting of existing internal fire hydrants hose pipe cabinet (external site only ) and adjacent hydrant pipe of 50 -100 mm dia. Upto 01 meter and valve etc. including supporting structure with 02 coat of red oxide primer and 01 coat of enamel paint including scrapping, cleaning etc. complete as required as per site condition. | 30.00 | Job | 10.00 | 500.00 | 15000.00 | 50.00 | 1500.00 | 1500.00 | Katyayni Engineering And Services
15.00 | 13. Supply and fixing of new gland plate, housing nut bolt with gland dori, gland nut bolt set, bearings of jockey pump (make: kirloskars brothers, type: CPHM 32/26 i/c dismantling, loading and unloading, transportation of pump to and from the site, Servicing of pump, allignment with Engine on common base plate, installation, testing & commisioning complete as required. | 2.00 | Job | 10.00 | 3000.00 | 6000.00 | 9000.00 | 18000.00 | 6000.00 | Manish Electricals
16.00 | 14. Providing and fixing of MS Pipe including all fittings and accessories such as screwed/welded flanges, tees, reducers etc. complete including painting(with one coat of primer & two coats of post office red enamel paint), welding, jointing and neoprene gaskets, nuts, bolts etc. as required i/c dismantling of the existing pipes with accessories (if any) of the following pipes fixed in ceiling, walls, coloumns for all heights with hangers, supports and fasteners all as per direction of Engineer In Charge, including chasing of walls/columns/ceilings etc. and making good the same complete as and when required.
16.01 | (a) 200 mm dia (Heavy class 6 mm thick) ( IS : 3589) | 10.00 | Mtr. | 100.00 | 1500.00 | 15000.00 | 15000.00 | 150000.00 | 15000.00 | Manish Electricals
16.02 | (b) 150 mm dia (Medium Class, IS 1239) | 10.00 | Mtr. | 10.00 | 1200.00 | 12000.00 | 1250.00 | 12500.00 | 12000.00 | Manish Electricals
16.03 | (c) 100 mm dia (Medium Class, IS 1239) | 10.00 | Mtr. | 10.00 | 1200.00 | 12000.00 | 1000.00 | 10000.00 | 10000.00 | Katyayni Engineering And Services
16.04 | (d) 80 mm dia (Medium Class, IS 1239) | 10.00 | Mtr. | 100.00 | 1000.00 | 10000.00 | 800.00 | 8000.00 | 8000.00 | Katyayni Engineering And Services
16.05 | (e) 50 mm dia (Medium Class, IS 1239) | 10.00 | Mtr. | 10.00 | 650.00 | 6500.00 | 550.00 | 5500.00 | 5500.00 | Katyayni Engineering And Services
| Total in Figures |  |  |  |  | 685600.00 |  | 648969.00
Lowest Amount Quoted BY: Katyayni Engineering And Services(648969.00)

## BOQ Summary
BOQ Summary Details Tender Title: AMC Fire Hydrant with Sprinkler System Tender ID: 2020_AAI_51159_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Katyayni Engineering And Services | 648969.00 | L1
| 2 | Manish Electricals | 685600.00 | L2