## BoQ1
Government eProcurement System Created By: Ravindra singh Mehrok Created Date/Time: 25-Aug-2020 11:49 AM Tender Title: Provision of UPS for GLF system at Vadodara Airport. Tender ID: 2020_AAI_51965_1
Tender Inviting Authority: Asst .Gen. Manager(E-E), AAI, CA, Vadodara
Name of Work: Provision of UPS for GLF System at Vadodara Airport.
Contract No: AAI/BO/EE/NIT-01/UPS FOR GLF/2020-21
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RS Power Systems Pvt. Ltd.(GSTN-NA) |  | ECS ENGINEERING PVT LTD(GSTN-NA) |  | GAYATRI ELECTRICAL(GSTN-NA) |  | Riello Power India Pvt Ltd.(GSTN-NA) |  | Awasthi Electric Works(GSTN-NA) |  | Gayatri Dimensions(GSTN-NA) |  | Consul Neowatt Power Solutions Pvt Ltd(GSTN-NA) |  | INDIAN ELECTRIC CORPORATION(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning (SITC) of 2x125KVA online UPS, 3 Phase input, 3 Phase output PWM IGBT based online double conversion type with inbuilt isolation transformer suitable to drive constant current regulators (CCR) with 100% unbalanced load at output at full load condition with standard features like 100% rated static bypass, maintenance bypass facilities active input power factor correction, phase sequence corrector, pure sinewave output, compatibility of generator supply, user friendly LCD display and run in load sharing mode, battery management features integrated with main UPS controller, operating condition 400V ±15%, 3 phase 50 Hz AC supply, IP 20 capable of running at 100% load delivering 2 phase/single phase load with 3 phase of output and as per the enclosed technical specification along with the following complete as required: (a) Supply, Installation, Testing & Commissioning (SITC) of two battery bank Sets (for 2 UPS) 12 V & minimum 124800 VAH per UPS for 30 minute backup from each UPS i/c suitable rating battery circuit breakers, interconnection between the batteries cabling by copper conductor between battery bank and UPS, glanding & termination along with battery rack.There should be provision for common battery bank. | 1.00 | Job |  | 3515000.00 | 3515000.00 | 2980000.00 | 2980000.00 | 1555000.00 | 1555000.00 | 3090000.00 | 3090000.00 | 3249000.00 | 3249000.00 | 3410000.00 | 3410000.00 | 2400000.00 | 2400000.00 | 3209406.00 | 3209406.00 | 1555000.00 | GAYATRI ELECTRICAL
2.00 | SITC of Dust & vermin proof Indoor type double door Floor Mounted panel of suitable size on angel iron frame/ flate iron frame work and to withstand rough usage. The panel shall be fabricated as per IEC 61439 with 14 SWG MS sheet complete with all accessories suitable angle/ channels frame, gland plates, painting etc. including supplying and fixing of following accessories and making inter connection, earth connection, neutral link, etc.as per the drawing and site requirement. [ UPS Incomer Panel ] Incomer : - 630A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 01 Nos. > Multi function meter (Shows Voltage, Current & Frequency) with 3 line LCD Display of size 96 x 96 mm. - 01 Nos. > Indication Lamp R, Y & B (LED Type) -01 set Outgoing : - 400A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 02 Nos. > Indication Lamp R & G (LED type) - 02 Set Other : - 800A Aluminium busbar, 3 Phase & Neutral >Necessary CT & Control wiring arrangement >Power terminal and other accessories >Three Phase Surge Protection Device (SPD) having nominal dischage current (L-N/N-PE) =25 /100 kA (8/20 us) Lightning impulse current (L1 + L2 + L 3 + N -PE=100kA (10/350 us) & (L-N / N-PE = 25/100 kA) with voltage protection level <=1.5 kV (L-N/N-PE) including all accessories for installing on the mains power entry point at the busbar shall be of modular type. [Make:-DEHN Model No. DV M TT 255 FM (951 315) or equivalent appproved make ] - 01 No. | 1.00 | Each |  | 180000.00 | 180000.00 | 135000.00 | 135000.00 | 248400.00 | 248400.00 | 250000.00 | 250000.00 | 310000.00 | 310000.00 | 252950.00 | 252950.00 | 160000.00 | 160000.00 | 267850.00 | 267850.00 | 135000.00 | ECS ENGINEERING PVT LTD
3.00 | SITC of Dust & vermin proof Indoor type double door Floor Mounted panel of suitable size on angel iron frame/ flate iron frame work and to withstand rough usage. The panel shall be fabricated as per IEC 61439 with 14 SWG MS sheet complete with all accessories suitable angle/ channels frame, gland plates, painting etc. including supplying and fixing of following accessories and making inter connection, earth connection, neutral link, etc.as per the drawing and site requirement. [ UPS Outgoing Panel ] Incomer : > 400A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 02 Nos. > Multi function meter (Shows Voltage, Current & Frequency) with 3 line LCD Display of size 96 x 96 mm. - 02 Nos. > Indication Lamp R, Y & B (LED Type) -02 set Outgoing : > 400A, MCCB, 4P, 35 KA (Icu= 100% Ics) with extended rotary handle - 01 Nos. >Indication Lamp R & G (LED type) - 01 Set Other : > 600A Aluminium busbar, 3 Phase & Neutral > Necessary CT & Control wiring arrangement > Power terminal and other accessories | 1.00 | Each |  | 180000.00 | 180000.00 | 120000.00 | 120000.00 | 226200.00 | 226200.00 | 175000.00 | 175000.00 | 210000.00 | 210000.00 | 175790.00 | 175790.00 | 145000.00 | 145000.00 | 226600.00 | 226600.00 | 120000.00 | ECS ENGINEERING PVT LTD
4.00 | SITC of Dust & vermin proof Indoor type double door Floor Mounted panel of suitable size on angel iron frame/ flate iron frame work and to withstand rough usage. The panel shall be fabricated as per IEC 61439 with 14 SWG MS sheet complete with all accessories suitable angle/ channels frame, gland plates, painting etc. including supplying and fixing of following accessories and making inter connection, earth connection, neutral link, etc.as per the drawing and site requirement. [ [ CCR Panel ] Incomer : > 400A, MCCB, 4P, 35-37 KA (Icu= 100% Ics) with extended rotary handle and spreaders - 02 Nos. > Multi function meter (Shows Voltage, Current & Frequency) with 3 line LCD Display of size 96 x 96 mm. - 02 Nos. > Indication Lamp R, Y & B (LED Type) -02 set > Mechanical key lock (2 Lock + 1 Key) Outgoing : > 125A, MCCB, 4P, 35 KA (Icu= 100% Ics) with extended rotary handle - 03 Nos. >100A, MCCB, 4P, 35 KA (Icu= 100% Ics) with extended rotary handle - 09 Nos. > 63A, MCCB, 4P, 35 KA (Icu= 100% Ics) with extended rotary handle - 07 Nos. > Indication Lamp R & G (LED type) - 19 Set Other : > 600A Aluminium busbar, 3 Phase & Neutral > Necessary CT & Control wiring arrangement > Power terminal and other accessories | 1.00 | Each |  | 240000.00 | 240000.00 | 385000.00 | 385000.00 | 573000.00 | 573000.00 | 520000.00 | 520000.00 | 630000.00 | 630000.00 | 400810.00 | 400810.00 | 425000.00 | 425000.00 | 647900.00 | 647900.00 | 240000.00 | RS Power Systems Pvt. Ltd.
5.00 | Supply of following sizes of 1.1 KV grade, XLPE insulated, PVC sheathed, armoured, aluminium conductor power cable confirms to IS 7098:1988 (Part -1) with up to date amendments etc complete as required a)4 x 25 sqmm | 250.00 | Mtrs. |  | 116.38 | 29095.00 | 135.00 | 33750.00 | 230.00 | 57500.00 | 174.00 | 43500.00 | 130.00 | 32500.00 | 140.00 | 35000.00 | 135.00 | 33750.00 | 114.00 | 28500.00 | 28500.00 | INDIAN ELECTRIC CORPORATION
6.00 | Supply of following sizes of 1.1 KV grade, PVC insulated, Unsheathed, Un-armoured, Copper conductor power cable confirms to IS 694:1990 with up to date amendments etc complete as required a) 1 core 95 Sq.mm | 200.00 | Mtrs. |  | 667.00 | 133400.00 | 642.00 | 128400.00 | 730.00 | 146000.00 | 828.00 | 165600.00 | 710.00 | 142000.00 | 682.00 | 136400.00 | 600.00 | 120000.00 | 562.00 | 112400.00 | 112400.00 | INDIAN ELECTRIC CORPORATION
7.00 | Supply of PVC/XLPE insulated and PVC sheathed Copper conductor armoured control cable of 1.1 KV grade conforming to IS : 7098 :1988 (Par : -I) with upto date amendments etc.,as required.of following sizes : a) 7 core 2.5 Sqmm | 250.00 | Mtrs. |  | 164.45 | 41112.50 | 170.00 | 42500.00 | 245.00 | 61250.00 | 195.00 | 48750.00 | 155.00 | 38750.00 | 168.00 | 42000.00 | 160.00 | 40000.00 | 146.00 | 36500.00 | 36500.00 | INDIAN ELECTRIC CORPORATION
8.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in masonary open duct/ Cable Tray etc. as required. a) Above 185 Sq. mm and up to 400 Sq. mm | 50.00 | Mtrs. |  | 276.00 | 13800.00 | 80.00 | 4000.00 | 80.00 | 4000.00 | 225.00 | 11250.00 | 50.00 | 2500.00 | 120.00 | 6000.00 | 100.00 | 5000.00 | 70.00 | 3500.00 | 2500.00 | Awasthi Electric Works
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in masonary open duct/ Cable Tray etc. as required. b) Above 35 sq. mm and upto 95 sq. mm | 60.00 | Mtrs. |  | 184.00 | 11040.00 | 60.00 | 3600.00 | 40.00 | 2400.00 | 110.00 | 6600.00 | 50.00 | 3000.00 | 70.00 | 4200.00 | 65.00 | 3900.00 | 45.00 | 2700.00 | 2400.00 | GAYATRI ELECTRICAL
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in masonary open duct/ Cable Tray etc. as required. c) Upto 35 sqmm | 395.00 | Mtrs. |  | 92.00 | 36340.00 | 40.00 | 15800.00 | 55.00 | 21725.00 | 75.00 | 29625.00 | 30.00 | 11850.00 | 50.00 | 19750.00 | 55.00 | 21725.00 | 30.00 | 11850.00 | 11850.00 | INDIAN ELECTRIC CORPORATION, Awasthi Electric Works
11.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. a)3.5 x 240 sqmm | 6.00 | Each |  | 531.30 | 3187.80 | 2275.00 | 13650.00 | 1450.00 | 8700.00 | 2070.00 | 12420.00 | 800.00 | 4800.00 | 2100.00 | 12600.00 | 2000.00 | 12000.00 | 700.00 | 4200.00 | 3187.80 | RS Power Systems Pvt. Ltd.
12.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. b)3.5 x 95 sqmm | 6.00 | Each |  | 209.30 | 1255.80 | 915.00 | 5490.00 | 900.00 | 5400.00 | 1092.00 | 6552.00 | 400.00 | 2400.00 | 1050.00 | 6300.00 | 1700.00 | 10200.00 | 450.00 | 2700.00 | 1255.80 | RS Power Systems Pvt. Ltd.
13.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. c)4 x 25 sqmm | 20.00 | Each |  | 110.40 | 2208.00 | 516.00 | 10320.00 | 350.00 | 7000.00 | 632.00 | 12640.00 | 250.00 | 5000.00 | 550.00 | 11000.00 | 1200.00 | 24000.00 | 325.00 | 6500.00 | 2208.00 | RS Power Systems Pvt. Ltd.
14.00 | Supplying and making end termination with brass compression gland and copper lugs with number ferruling etc. for following size of PVC insulated and PVC sheathed / XLPE copper control cable of 1 KV grade as required. a)7 core 2.5 Sqmm | 26.00 | Set |  | 54.62 | 1420.12 | 150.00 | 3900.00 | 325.00 | 8450.00 | 747.00 | 19422.00 | 175.00 | 4550.00 | 350.00 | 9100.00 | 1000.00 | 26000.00 | 250.00 | 6500.00 | 1420.12 | RS Power Systems Pvt. Ltd.
15.00 | Supplying and making end termination with PVC gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required. b) 1 core 95 Sq.mm | 32.00 | Set |  | 82.80 | 2649.60 | 100.00 | 3200.00 | 325.00 | 10400.00 | 287.00 | 9184.00 | 280.00 | 8960.00 | 900.00 | 28800.00 | 1400.00 | 44800.00 | 100.00 | 3200.00 | 2649.60 | RS Power Systems Pvt. Ltd.
16.00 | Supply & fixing of 1Mtr wide & 2MM Thick, ISI marked Electrical Insulating Mats Confirming to IS: 15652 / 2006, Working voltage upto 3.3 KV. | 30.00 | Sqm |  | 1437.50 | 43125.00 | 800.00 | 24000.00 | 1400.00 | 42000.00 | 5692.00 | 170760.00 | 850.00 | 25500.00 | 1000.00 | 30000.00 | 1200.00 | 36000.00 | 535.00 | 16050.00 | 16050.00 | INDIAN ELECTRIC CORPORATION
17.00 | SITC of control box with foldable door of stainless steel ( SS304) of size 2 mtr x 1.0 mtr x depth minimum 200mm with steel din rail and din rail mounted Control cable connector -13 Nos of 6 core of mail/ female type ( Make Phoenix PN3040300 or equivalent) . [ Job included termination of 60 core control cable, number ferruling , dressing and terminating the cores with suitable length in male / female connector ] . | 1.00 | Job |  | 25000.00 | 25000.00 | 36000.00 | 36000.00 | 275000.00 | 275000.00 | 75000.00 | 75000.00 | 19500.00 | 19500.00 | 73500.00 | 73500.00 | 17000.00 | 17000.00 | 10500.00 | 10500.00 | 10500.00 | INDIAN ELECTRIC CORPORATION
18.00 | Shifting of CCR from CCR Room to near HT Room with stand, cables and accessories by disconnecting and reconnecting , termination of cables etc. as per site requirement. | 6.00 | Job |  | 8000.00 | 48000.00 | 5000.00 | 30000.00 | 20000.00 | 120000.00 | 15000.00 | 90000.00 | 3500.00 | 21000.00 | 10000.00 | 60000.00 | 10000.00 | 60000.00 | 3000.00 | 18000.00 | 18000.00 | INDIAN ELECTRIC CORPORATION
19.00 | Modification of existing CCR MS stand by cutting, welding, painting with primer and two coats synthetic enamel, arrangement of nut bolt and making frame size upto 750mm x750mm from existing frame size 750mm x 1000mm etc. as per site requirement. | 2.00 | Job |  | 8625.00 | 17250.00 | 5000.00 | 10000.00 | 25000.00 | 50000.00 | 10000.00 | 20000.00 | 2500.00 | 5000.00 | 5000.00 | 10000.00 | 18000.00 | 36000.00 | 2500.00 | 5000.00 | 5000.00 | INDIAN ELECTRIC CORPORATION, Awasthi Electric Works
20.00 | Elevation of CCR MS stand by increasing the height of MS stand with new frame having size 750mm x 750mm by angle iron of size 50mm x 50mm x 5mm up to 1 feet by cutting, welding, painting with primer and two coats synthetic enamel, in CCR Room etc. as per site requirement. | 3.00 | Job |  | 3450.00 | 10350.00 | 4000.00 | 12000.00 | 18000.00 | 54000.00 | 10000.00 | 30000.00 | 3000.00 | 9000.00 | 3000.00 | 9000.00 | 15000.00 | 45000.00 | 2500.00 | 7500.00 | 7500.00 | INDIAN ELECTRIC CORPORATION
21.00 | Elevation of LT Panels MS Stand by increasing the height of MS stand with new frame having size 260mm x 1180mm and 270mm x 1210mm by angle iron of size 50mm x 50mm x 5mm up to 1 feet in ATC Tower Switch Room by cutting, welding, painting etc. as per site requirement. | 1.00 | Job |  | 5750.00 | 5750.00 | 8000.00 | 8000.00 | 28000.00 | 28000.00 | 25000.00 | 25000.00 | 10000.00 | 10000.00 | 3500.00 | 3500.00 | 15000.00 | 15000.00 | 3000.00 | 3000.00 | 3000.00 | INDIAN ELECTRIC CORPORATION
22.00 | Supplying and installing of 300 mm width x 50 mm depth x 1.6 mm thickness size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 60.00 | Mtrs. |  | 902.75 | 54165.00 | 540.00 | 32400.00 | 750.00 | 45000.00 | 747.00 | 44820.00 | 525.00 | 31500.00 | 680.00 | 40800.00 | 800.00 | 48000.00 | 758.00 | 45480.00 | 31500.00 | Awasthi Electric Works
23.00 | Supplying and installing of 150 mm width x 50 mm depth x 1.6 mm thickness size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 50.00 | Mtrs. |  | 730.25 | 36512.50 | 385.00 | 19250.00 | 950.00 | 47500.00 | 517.00 | 25850.00 | 425.00 | 21250.00 | 450.00 | 22500.00 | 650.00 | 32500.00 | 480.00 | 24000.00 | 19250.00 | ECS ENGINEERING PVT LTD
| Total in Figures |  |  |  |  | 4630661.32 |  | 4056260.00 |  | 3596925.00 |  | 4881973.00 |  | 4798060.00 |  | 4800000.00 |  | 3760875.00 |  | 4699836.00
Lowest Amount Quoted BY: GAYATRI ELECTRICAL(3596925.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of UPS for GLF system at Vadodara Airport. Tender ID: 2020_AAI_51965_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | GAYATRI ELECTRICAL | 3596925.00 | L1
| 2 | Consul Neowatt Power Solutions Pvt Ltd | 3760875.00 | L2
| 3 | ECS ENGINEERING PVT LTD | 4056260.00 | L3
| 4 | RS Power Systems Pvt. Ltd. | 4630661.32 | L4
| 5 | INDIAN ELECTRIC CORPORATION | 4699836.00 | L5
| 6 | Awasthi Electric Works | 4798060.00 | L6
| 7 | Gayatri Dimensions | 4800000.00 | L7
| 8 | Riello Power India Pvt Ltd. | 4881973.00 | L8