## BoQ1
Government eProcurement System Created By: Madan Mohan Agrawal Created Date/Time: 10-Sep-2020 01:52 PM Tender Title: Establishment of Civil Enclave at Adampur Airport, Jalandhar. SH- SITC of Apron High Mast and Associated Electrical Works at Civil Airport, Adampur, Jalandhar Tender ID: 2020_AAI_54535_1
Tender Inviting Authority: Sr. Manager (Engg.-Elect)
Name of Work: “ Establishment of Civil Enclave at Adampur Airport, Jalandhar. SH:- SITC of Apron High Mast and Associated Electrical Works at Civil Airport, Adampur, Jalandhar.”.
Contract No: Tender ID 2020_AAI_54535_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | BR Power Control and Automation Services(GSTN-06AREPS4024K1ZP) |  | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED(GSTN-03AACCJ6494J1ZC) |  | R S ELECTRICALS(GSTN-09AALFR7080G1ZS) |  | GREWAL ELECTRIC CORPORATION(GSTN-03ABNPG6269P1Z2) |  | M J ELECTRICALS AND ELECTRONICS(GSTN-07AAFPD8772P1Z3)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Installation, Testing & Commissioning of 20 Mtr High Mast system with its accessories. Mast shaft shall be in Two sections, hot dip galvanised and suitable for wind velocity as per IS:875. It shall also include accessories for high mast including head frame, steel wire rope 6 mm dia (SS) with raising lowering system comprising, luminaries carriage suitable to install required nos of LED Light fixtures with its accissories in Asymmetrical arrangement, double drum winch, trailing cable, connector, junction box, lightening finial etc. The mast shall have an integral power tool motor, manual handle installed inside the base compartment for its operation. Work includes the supply and fixing of required MCB in base compartment and following accessories etc. as required as per the enclosed specifications complete as required;. a) Providing & fixing of Counter weight for LED light fixtures (as per requirement) b) Providing & fixing of foundation bolts manufactured from special steel along with nuts, washers, anchor plate and common template (as per OEM standard). c) Construction of shallow foundation with M25 grade concrete for the highmast considering the safe soil bearing capacity at site as 10 T/sqmtr at 2.0 metre depth with all materials and labour as per approved design etc complete as per Technical specification of Tender Document. This item also covers the charges towards vetting of the foundation design (as submitted by OEM) from any Govt.Engg.Institute/lab.. d) Providing and fixing of LED type aviation obstruction light-02 nos | 2.00 | Job |  | 348500.00 | 697000.00 | 400000.00 | 800000.00 | 320000.00 | 640000.00 | 341000.00 | 682000.00 | 210000.00 | 420000.00 | 420000.00 | M J ELECTRICALS AND ELECTRONICS
2.00 | Supply of Flood light LED fitting with minimum output of 38500 lumens and wattage not more than 350 W, for 230V Single Phase AC supply, 50Hz, PF>0.95, CRI>70, CCT - 5700K, Life of fitting not less than 50000 hrs complete as required. Luminaire should have high pressure die cast Alminium/standard alloy housing with surge protection system > 4KV. Luminaire should have proper thermal management. Min IP protection should be IP65. The fixtures shall be suitable for lantern carrier of high mast vetted by OEM of Hi Masts and as per specifications etc. as required. It shall meet as per technical specifications enclosed with tender complete in all respect as required as per direction and satisfaction of Engineer‐Incharge. | 24.00 | Each |  | 20313.00 | 487512.00 | 16000.00 | 384000.00 | 19000.00 | 456000.00 | 14900.00 | 357600.00 | 20000.00 | 480000.00 | 357600.00 | GREWAL ELECTRIC CORPORATION
3.00 | Installation. Testing & Commsisioning of flood light fixtures (as per Item No.2 above) on the lantern carrier of high mast including connection, testing, commissioning etc. as required. | 20.00 | Each |  | 620.00 | 12400.00 | 200.00 | 4000.00 | 200.00 | 4000.00 | 1800.00 | 36000.00 | 100.00 | 2000.00 | 2000.00 | M J ELECTRICALS AND ELECTRONICS
4.00 | Design, manufacture, supply, installation, testing and commissioning of outdoor totally enclosed double door feeder pillar panel confirming to IP 65, made of 14 SWG CRCA sheet steel, totally enclosed, standing on a MS Angle frame suitably fixed on floor foundation, dust and vermin proof, powder coated painting, suitable for operation on 3 phase and neutral, 415 V, 50 Hz AC system with busbars, connection and interconnections including supply & installation of following items and as per specifications : (Control panel suitable for Item no 1 Poles for apron High mast) Incomers : 02 Nos. 63 Amp., 4 Pole, MCCB (Ics=100%Icu, 25 KA), spreader links and extendable ON/OFF rotary handle. CT's of ratio 63/5 Amps.-2 Set (1 Set of 3 Nos.) (0-63 A) Digital Ammeter with selector switch - 2 Set (0-500 V) Digital Voltmeter with selector switch - 2 Set Indication lamp R/Y/B with backup MCB - 2 Set of Three Terminal Block din rail mounted 10 A Almac suitable for 6 core 2.5 sqmm - 1 No for remote control operation Bus-Bars : 4-Pole Aluminium Bus bar of 100 A rating of high conductivity with heat shrinkable, coloured sleeves, required intervals complete for cross section, size supports and their spacing etc as per specification. Outgoings : (1) 40 A, 4 Pole C curve MCB-04 Nos.(2 ) 6-32 A, DP C curve MCB-02 Nos. (3) Suitable Capacity DOL starter / Contactor with Push Button for operating raising -lowering circuit. (4) All day timer along with contactor for switching on and off to Aviation obstruction light during night time with one No. toggle switch as a option for by passing the timer. (5) Compartment to accomodate 1 KV UPS with batteries with control wiring for providing 2 nos. 350 W LED fixture on UPS power back up. Note : Suitable arrangement is to be made for auto changing over from one incomer to another in case of failure of main incomer. (All required hard ware i.e. contactor, relays, control wiring etc are included in this item.) | 2.00 | Job |  | 116554.00 | 233108.00 | 75000.00 | 150000.00 | 125000.00 | 250000.00 | 98000.00 | 196000.00 | 100000.00 | 200000.00 | 150000.00 | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
5.00 | Design, manufacture, supply, installation, testing and commissioning of outdoor totally enclosed double door feeder pillar panel confirming to IP 65, made of 14 SWG CRCA sheet steel, totally enclosed, standing on a MS Angle frame suitably fixed on floor foundation, dust and vermin proof, powder coated painting, suitable for operation on 3 phase and neutral, 415 V, 50 Hz AC system with busbars, connection and interconnections including supply & installation of following items and as per specifications :(Main feeder piller ) Incoming : 02 Nos. 125 Amp., 4 Pole, MCCB (Ics=100%Icu, 35 kA),with Thermal Magnetic release spreader links and extendable ON/OFF rotary handle. CT's of ratio 125/5 Amps.-2 Set (1 Set of 3 Nos.) Digital Ammeter with selector switch - 2 set Digital Voltmeter with selector switch- 2 set 6 Nos. Phase indication LED Lamps with 2 Amp. MCBs 2 Nos. red ON indication LED Lamps with 2 Amp.MCBs 2 Nos. green OFF indication LED Lamps with 2 Amp. MCBs Bus coupler : 01 No. 125 Amp., 4 Pole, MCCB having (Ics=100%Icu, 35 kA), spreader links and extendable ON/OFF rotary handle. 1 Nos. red ON indication LED Lamps with 2 Amp.MCBs 1 Nos. green OFF indication LED Lamps with 2 Amp. MCBs Bus-Bars : 4-Pole Aluminium bus bars of minimum of 250 Amps. Capacity with heat shrinkable coloured sleeves & i/c. DMC /SMC bus bars supports at required intervals complete for cross section, size supports and their spacing etc. Outgoings : 10 Nos. 63 Amp., 4 Pole, MCCB having (Ics=100%Icu, 25 kA), spreader links and extendable ON/OFF rotary handle. Note : 2 Incomers & bus couplers are to be interlocked electrically & mechanically in a way so that only 2 (out of 3) can be Switched ON at a time. (All required hard ware i.e. Relays, control wiring etc are included in this item.) | 1.00 | Job |  | 194283.00 | 194283.00 | 200000.00 | 200000.00 | 265000.00 | 265000.00 | 235000.00 | 235000.00 | 250000.00 | 250000.00 | 194283.00 | BR Power Control and Automation Services
6.00 | Supply of following size XLPE insulated PVC Sheathed, armoured Aluminium conductor cable of 1.1KV grade confirming to IS:7098 with up to date amendments etc. as required.
6.10 | 4 X 10 sq.mm | 200.00 | Meter |  | 335.00 | 67000.00 | 100.00 | 20000.00 | 90.00 | 18000.00 | 92.00 | 18400.00 | 120.00 | 24000.00 | 18000.00 | R S ELECTRICALS
6.20 | 3½ X 95 sq.mm | 500.00 | Meter |  | 92.00 | 46000.00 | 300.00 | 150000.00 | 335.00 | 167500.00 | 346.00 | 173000.00 | 340.00 | 170000.00 | 46000.00 | BR Power Control and Automation Services
7.00 | Laying and Fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
7.10 | Upto 35 sq. mm size (Clamped with 1mm thick saddle) | 20.00 | Meter |  | 86.00 | 1720.00 | 100.00 | 2000.00 | 50.00 | 1000.00 | 20.00 | 400.00 | 30.00 | 600.00 | 400.00 | GREWAL ELECTRIC CORPORATION
7.20 | Above 35 Sqmm and upto 95 sq. mm size (Clamped with 25x3 mm MS flat clamp) | 250.00 | Meter |  | 185.00 | 46250.00 | 100.00 | 25000.00 | 70.00 | 17500.00 | 30.00 | 7500.00 | 70.00 | 17500.00 | 7500.00 | GREWAL ELECTRIC CORPORATION
8.00 | Laying of one number PVC insulated & PVC sheathed /XLPE power cable 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required.
8.10 | Upto 35 sq. mm size | 100.00 | Meter |  | 26.00 | 2600.00 | 20.00 | 2000.00 | 40.00 | 4000.00 | 15.00 | 1500.00 | 10.00 | 1000.00 | 1000.00 | M J ELECTRICALS AND ELECTRONICS
8.20 | Above 35 Sqmm and upto 95 sq. mm size | 100.00 | Meter |  | 32.00 | 3200.00 | 25.00 | 2500.00 | 50.00 | 5000.00 | 15.00 | 1500.00 | 20.00 | 2000.00 | 1500.00 | GREWAL ELECTRIC CORPORATION
9.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall / surface as required.
9.10 | Upto 35 sq. mm size | 30.00 | Meter |  | 86.00 | 2580.00 | 20.00 | 600.00 | 60.00 | 1800.00 | 25.00 | 750.00 | 40.00 | 1200.00 | 600.00 | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
9.20 | Above 35 Sqmm and upto 95 sq. mm size | 20.00 | Meter |  | 185.00 | 3700.00 | 25.00 | 500.00 | 80.00 | 1600.00 | 30.00 | 600.00 | 70.00 | 1400.00 | 500.00 | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
10.10 | Upto 35 sq. mm size | 30.00 | Meter |  | 25.00 | 750.00 | 20.00 | 600.00 | 40.00 | 1200.00 | 15.00 | 450.00 | 10.00 | 300.00 | 300.00 | M J ELECTRICALS AND ELECTRONICS
10.20 | Above 35 Sqmm and upto 95 sq. mm size | 30.00 | Meter |  | 31.00 | 930.00 | 25.00 | 750.00 | 50.00 | 1500.00 | 15.00 | 450.00 | 10.00 | 300.00 | 300.00 | M J ELECTRICALS AND ELECTRONICS
11.00 | Supply and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 KV grade as required.
11.10 | 4 x 16 sq mm size (28 mm) | 12.00 | Set |  | 693.00 | 8316.00 | 500.00 | 6000.00 | 150.00 | 1800.00 | 300.00 | 3600.00 | 50.00 | 600.00 | 600.00 | M J ELECTRICALS AND ELECTRONICS
11.20 | 3.5 x 95 sq mm size (45mm) | 4.00 | Set |  | 405.00 | 1620.00 | 1000.00 | 4000.00 | 300.00 | 1200.00 | 500.00 | 2000.00 | 90.00 | 360.00 | 360.00 | M J ELECTRICALS AND ELECTRONICS
12.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 4.00 | Set |  | 9531.00 | 38124.00 | 6000.00 | 24000.00 | 6000.00 | 24000.00 | 10000.00 | 40000.00 | 5000.00 | 20000.00 | 20000.00 | M J ELECTRICALS AND ELECTRONICS
13.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required | 30.00 | Meter |  | 275.00 | 8250.00 | 500.00 | 15000.00 | 450.00 | 13500.00 | 475.00 | 14250.00 | 450.00 | 13500.00 | 8250.00 | BR Power Control and Automation Services
14.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 30.00 | Meter |  | 215.00 | 6450.00 | 100.00 | 3000.00 | 140.00 | 4200.00 | 200.00 | 6000.00 | 200.00 | 6000.00 | 3000.00 | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED
15.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing suface/ recessed conduit/ submain wiring/ cable as required | 30.00 | Meter |  | 35.00 | 1050.00 | 25.00 | 750.00 | 40.00 | 1200.00 | 50.00 | 1500.00 | 18.00 | 540.00 | 540.00 | M J ELECTRICALS AND ELECTRONICS
16.00 | Supplying and laying of 63 mm dia (OD-63 mm & ID-51 mm nominal) size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. | 70.00 | Meter |  | 208.00 | 14560.00 | 200.00 | 14000.00 | 250.00 | 17500.00 | 275.00 | 19250.00 | 160.00 | 11200.00 | 11200.00 | M J ELECTRICALS AND ELECTRONICS
17.00 | Supplying and installing 300 mm width X 50 mm depth X 1.6 mm thickness size of perforated Hot Dipped Galvanised Iron cable tray (galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. | 80.00 | Meter |  | 1856.00 | 148480.00 | 1000.00 | 80000.00 | 800.00 | 64000.00 | 1500.00 | 120000.00 | 575.00 | 46000.00 | 46000.00 | M J ELECTRICALS AND ELECTRONICS
18.00 | Making brick wall (Minumum 10" width) Manhole for cable on a base of 4 inch of PCC of 1:2:4 (1cement :2 Sand: 4 aggregate stone of 20mm) including excavation of soil of all types with neat cement finish for base and plastering of inside wall and making necessary provision for entry of RCC/Metal/Plastic pipe etc. complete as required of following sizes (Inside Dimension) 900mm(length) x900mm (Width) x 1200mmDepth | 2.00 | Job |  | 1233.00 | 2466.00 | 10000.00 | 20000.00 | 9000.00 | 18000.00 | 6000.00 | 12000.00 | 9000.00 | 18000.00 | 2466.00 | BR Power Control and Automation Services
19.00 | Supply, Design, fabrication and installation of iron cover with heavy duty hinges for outdoor application and suitable lifting collapsible handle at AAI site made of MS chequered Plate and frame made of angle/channel/flat of various sizes and shape and other accessories suitable for covering Manholes, cable duct with necessary iron anchoring and grouting on existing wall/concrete or welding with existing iron structure etc complete as required as directed by Engineer incharge. The cover shall be openable upto 180 degree and all iron parts shall be painted with red oxide and final layer with two coats of synthetic enamelled paint of required colour as directed by Enginner incharge to give even and smooth finish. | 100.00 | Kg |  | 190.00 | 19000.00 | 150.00 | 15000.00 | 100.00 | 10000.00 | 95.00 | 9500.00 | 90.00 | 9000.00 | 9000.00 | M J ELECTRICALS AND ELECTRONICS
20.00 | Supply, Design & fabrication of iron structure at AAI site consisting of MS C Channel/ I section/ angle & MS flat iron of various sizes suitable for fencing of Outdoor Electrical panel/ manhole with necessary anchoring for grouting etc complete as required as directed by Engineer incharge. All iron parts shall be painted with red oxide and final layer with two coats of synthetic enamelled paint of required colour as directed by Enginner incharge to give even and smooth finish. | 300.00 | Kg |  | 125.00 | 37500.00 | 120.00 | 36000.00 | 100.00 | 30000.00 | 110.00 | 33000.00 | 120.00 | 36000.00 | 30000.00 | R S ELECTRICALS
21.00 | Fixing of Iron structure made of various sizes and shape in the ground of hard pavement with 1:1.5:3 PCC (1 Cement: 1.5 Sand: 3 Aggregate stone 20mm) including excavation of hard pavement upto depth of 450mm etc complete as required. | 12.00 | Each Column |  | 1849.00 | 22188.00 | 2000.00 | 24000.00 | 3000.00 | 36000.00 | 500.00 | 6000.00 | 700.00 | 8400.00 | 6000.00 | GREWAL ELECTRIC CORPORATION
22.00 | Making good the damages of Paved/Bituminous surface with 1:4:8 (1cement : 4 sand : 8 aggregate stone of 20mm) Concrete and Finishing the top surface with cement plaster etc. complete as required. | 6.00 | Cum |  | 2468.00 | 14808.00 | 6000.00 | 36000.00 | 3000.00 | 18000.00 | 7000.00 | 42000.00 | 3000.00 | 18000.00 | 14808.00 | BR Power Control and Automation Services
23.00 | Making good the damages of Paved/Bituminous surface with 1:2:4 (1cement : 2 sand : 4 aggregate stone of 20mm )Concrete and Finishing the top surface with cement plaster etc. complete as required. | 2.00 | Cum |  | 2466.00 | 4932.00 | 7000.00 | 14000.00 | 3000.00 | 6000.00 | 8000.00 | 16000.00 | 4000.00 | 8000.00 | 4932.00 | BR Power Control and Automation Services
24.00 | Providing and laying of 150mm Dia NP-4 pipe including excavation of trench upto 1mtr for road/drain crossings with accessories etc. complete as required. | 60.00 | Mtr |  | 470.00 | 28200.00 | 800.00 | 48000.00 | 700.00 | 42000.00 | 1000.00 | 60000.00 | 800.00 | 48000.00 | 28200.00 | BR Power Control and Automation Services
25.00 | Supply, installation,testing & commissioning of true online UPS of 1 KVA capacity, Input Voltage range 150-280 VAC, Output voltage range 220 VAC constant, High efficiency >90%, Short circuit over load, Over charge protection with internal batteries 9AH x 3 capable of min. 5 minute back up at nominal load 800 W as per relevent BIS specification with upto date amendments complete with all electrical parameters as required. | 2.00 | Job |  | 22511.00 | 45022.00 | 35000.00 | 70000.00 | 17000.00 | 34000.00 | 16000.00 | 32000.00 | 18000.00 | 36000.00 | 32000.00 | GREWAL ELECTRIC CORPORATION
| Total in Figures |  |  |  |  | 2199999.00 |  | 2151700.00 |  | 2155500.00 |  | 2128250.00 |  | 1849900.00
Lowest Amount Quoted BY: M J ELECTRICALS AND ELECTRONICS(1849900.00)

## BOQ Summary
BOQ Summary Details Tender Title: Establishment of Civil Enclave at Adampur Airport, Jalandhar. SH- SITC of Apron High Mast and Associated Electrical Works at Civil Airport, Adampur, Jalandhar Tender ID: 2020_AAI_54535_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M J ELECTRICALS AND ELECTRONICS | 1849900.00 | L1
| 2 | GREWAL ELECTRIC CORPORATION | 2128250.00 | L2
| 3 | JATINDER CONSTRUCTION COMPANY PRIVATE LIMITED | 2151700.00 | L3
| 4 | R S ELECTRICALS | 2155500.00 | L4
| 5 | BR Power Control and Automation Services | 2199999.00 | L5