## BoQ1
Government eProcurement System Created By: BANWARI LAL MEENA Created Date/Time: 31-Aug-2020 04:39 PM Tender Title: Construction Of Interim Terminal Building at Kushinagar Airport. SH- SITC of Sub Station Equipments and DG Sets Tender ID: 2020_AAI_54742_1
Tender Inviting Authority: AGM (Engg.-E), RHQ-NR
Name of Work: Construction Of Interim Terminal Building at Kushinagar Airport. SH: SITC of Sub Station Equipments and DG Sets.
Contract No: 2020_AAI_54742_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION(GSTN-09AOTPS2578C1ZC) |  | RASS CONTRACTOR AND ENGINEERS(GSTN-09AFIPR1600N1Z7) |  | TECHNISYS ENGINEERING PRIVATE LIMITED(GSTN-06AACCT8886E1ZZ)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | (SH: I) 11KV/0.433KV, 630 KVA DRY TYPE TRANSFORMER COMPACT SUB-STATION (OUTDOOR TYPE)
1.01 | Supply, Intallation, Testing and Commissioning of distribution network, 11KV, 630 KVA Dry Type Outdoor Compact Sub Station totally factory assembled (non walk in Type) consisting of 2 way RMU Type, 11KV/0.433KV, 630KVA Dry Type transformer - 01 No.; HT-LT PANELS, 200 KVAr APFC PANEL - 01 No. each as under including civil work for suitable Foundation for Compact Sub tation as per recommendation of OEM/OEA . Approved Makes of CSS-Siemens/Schneider/ABB/C&S/ L&T | 1.00 | Set |  | 1900000.00 | 1900000.00 | 2250000.00 | 2250000.00 | 2760096.00 | 2760096.00 | 1900000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
1.02 | MV COMPARTMENT- 11 KV, 630A, 25KA for 3 Second, Non-extensible,SF6 gas insulated Ring Main unit with sealed pressure system criterion in accordance with the IEC62271-200; 102,103,100.IAC of 21 kA for 1 sec for tank and cable box category IAC-AFL . The Switchgear includes the following MV cubicles- The indoor non -extensible SF6 insulated RMU manually operated consist of 1 No. Vacuum Circuit Breaker, 2 Nos. LBS with Numerical relay (3 OC +1 EF) for protection of treansformer with MFM for metering. Rated for Voltage 12kV, 630A, 21 KA for 3 sec. a.Rated voltage should be - 12 kV b.Rated power frequenecy voltage be - 28 kV (RMS) c.Rated lightening withstand voltage -75 KV d.Rated current for Ring main feeder -630 amps e.Rated current for VCB feeder -630amps f.Vacuum Circuit Breaker of RMU should clear minimum 40 Nos. of dead short circuit operations g.Rated short time cuirrent -21 KA for 3sec h.Rated short time making current -50 KA in Ambient temp (0 deg C to 42 deg C) j.Rated internal arc rating - 21 KA for 1 sec for tank and cable box category IAC-AFL k.The circuit breaker feeder shall be self powered & powered by external source type and shall be provided with 3 OC + 1 EF protection for transformer and shall have serial port for communication on modbus protocol. l.RMU should be certified from NABL accredited testing lab.
1.03 | Transformer (Dry Type) Three phase a.Standard: IS : 1180 Part 1 Level 2 b.Vector group : Dyn 11 c.Rating : 630 KVA d.Cooling System : AN e.Winding : Copper , Class of Insulation: F f.% impedance: 6.25% (IS Tol) g.High voltage :11KV - 50 Hz h.System highest voltage : 12kV at the HV side i.H.V. Impulse withstand voltage (KV peak ): 75 kVp j.Off load Tapping: +5% to -5% in steps of 2.5% in HV Side k.winding temperature rise as per IS 1180 Part 1 Makes of Transformer shall be as per AAI approved make list.
1.04 | LV COMPARTMENT The LV compartment with Degree of protection -IP54 designed shall be for a 50 degree C ambient temperature. The panel is modular, dead front, freestanding, floor mounted and comprises the following equipment a. 433V air insulated Alumimum busbar having capacity 1250A, 50Hz, 50KA withstand fault level capacity. b. Incomer - ACB, 1250 A, 4 Pole, 50KA EDO, MTX 1.5 G Fixed Manual Microprocessor based, fixed type ACB with S/C, O/C & earthfault release. The fault system of 50KA, Ics=Icu=Icw for 1 sec. c. Outgoings - 1250 Amp, 36 KA, FP MCCB - 01 No.; 630 Amp, 36 KA, FP MCCB - 02 Nos. Make-As per AAI approved make list
1.05 | 200 KVAR APFC panel (To be mounted inside the CSS) directly connected to the 1250 Amp main Bus bar. Incomer: a. 400 Amp, 35 KA, 3P MCCB with microprocessor base release; b. 14 Steps single phase APFC relay - 01 No.; c. CTs for APFC relay of suitable rating, Cl 1- 01 No.; d. Control MCB 6 A SP- As required; e. Metering and indication lamps; f. 630 Amp TPN aluminium busbar. Outgoing: a. Heavy duty contactor of suitable rating for 25 KVAr Capacitor - 06 Nos.; b. Heavy duty contactor of suitable rating for 10 KVAr Capacitor - 04 Nos.; c. Heavy duty contactor of suitable rating for 05 KVAr Capacitor - 02 Nos.; d. 25 KVAr / 440 V, MPP, normal duty capacitor - 06 Nos.; e. 10 KVAr / 440 V, MPP, normal duty capacitor - 04 Nos.; f. 05 KVAr / 440 V, MPP, normal duty capacitor - 02 Nos.; g. 125 A TP MCCB, 25 KA with thermal magnetic release - 6 Nos.; h. 63 A TP MCCB, 25 KA with thermal magnetic release - 6 Nos.
1.06 | Outdoor Enclosure:- The Enclosure shall be made of 2.0 mm thickness Galvanized Sheet Steel tropicalised to meet Indian weather conditions including all the partition sheets & doors. The base of the enclosure shall be made of 4.0 mm thickness Hot Dip Galvanized Sheet Steel to ensure rigidity for easy transport and installation. The entire package Substation shall be factory assembled & Factory fitted. The enclosure shall have IP54 degree of protection for HT&LT switchgear compartment & IP34 degree of protection for transformer compartment. The enclosure to be tested for Internal Arc Fault Test to the tune of atleast 21KA for 1 second adhering to as per latest IEC 62271-202.The temperature rise test on enclosure for K10 class.The enclosure exterior shall be powder coated and each compartment shall be provided with the door & locking arrangement. The compartment illumination lamp with door operated switch shall be provided for MV & LV compartment. RMU, Transformer and LT Panel of the same make preferred.
2.00 | (SH: II) SITC of LT PANELS
2.01 | L.T PANEL FOR NORMAL SUPPLY SUB-STATION Design, fabrication, assembling, supply, installation, testing and commissioning of Indoor type cubicle LT panels suitable for 415 V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2 mm thick for frame work IP 42 degree of protection and 3 mm thick for gland plates i/c cleaning and finishing complete with 7 tank process for powder coating in approved shade, having 1200 A capacity of TPN Aluminimum alloy busbar of high conductivity, DMC/SMC busbar supports, with bottom base channel of MS section not less than 100mm X 50 mm X 5 mm thick, entire panel shall have a common GI earthbar of size 50 mm X 5 mm at the rear with 2 Nos. earth studs, solid connection from main busbar to switchgears with require size of aluminium busbar & control wiring with 2.5 sqmm FRLS insulated copper conductor cable, cable alleys, cable gland plates and all MCCBs shall be thermal magnetic release having overload, short circuit adjustable setting & (Ics = Icu) i/c accessories as per specification and providing switchgears, metering instruments etc. complete as required. Incomer - 800 A 50KA (at 415Volts) Four Pole Air Circuit Breaker- 01 No. Aluminium TPN Bus Bar- 1200 A (1 Set) Outgoing - 630 A, 36KA (at 415Volts) Four Pole, MCCB - 02 Nos. Outgoing - 400 A, 36KA (at 415Volts) Four Pole, MCCB - 01 No. Outgoing - 250 A, 25KA (at 415Volts) Four Pole, MCCB - 01 No. Outgoing - 125 A, 25KA (at 415Volts) Four Pole, MCCB - 02 Nos. Outgoing - 63 A, 25KA (at 415Volts) Four Pole, MCCB - 02 Nos. | 1.00 | Job |  | 450000.00 | 450000.00 | 545000.00 | 545000.00 | 599372.00 | 599372.00 | 450000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
2.02 | L.T PANEL FOR ESSENTIAL SUPPLY SUB-STATION Design, fabrication, assembling, supply, installation, testing and commissioning of Indoor type cubicle LT panels suitable for 415 V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2 mm thick for frame work IP 42 degree of protection and 3 mm thick for gland plates i/c cleaning and finishing complete with 7 tank process for powder coating in approved shade, having 1000 A capacity of TPN Aluminimum alloy busbar of high conductivity, DMC/SMC busbar supports, with bottom base channel of MS section not less than 100mm X 50 mm X 5 mm thick, entire panel shall have a common GI earthbar of size 50mm X 5 mm at the rear with 2 Nos. earth studs, solid connection from main busbar to switchgears with require size of aluminium busbar & control wiring with 2.5 sqmm FRLS insulated copper conductor cable, cable alleys, cable gland plates and all MCCBs shall be thermal magnetic release having overload, short circuit adjustable setting & (Ics = Icu) i/c accessories as per specification and providing switchgears, metering instruments etc. complete as required. Incomer - 630 A, 36KA (at 415Volts),Four Pole, MCCB- 02 Nos. & having Electrical and Mechanical interlocking with both incomers and Bus Coupler. Bus Coupler- 630A, 36KA (at 415Volts) ,Four Pole, MCCB- 01 Aluminium TPN Bus Bar- 1000 A (1 Set) Outgoing - 400 A, 36KA, Four Pole, MCCB - 04 Nos. Outgoing - 250 A, 25KA, Four Pole, MCCB - 02 Nos. Outgoing - 125 A, 25KA, Four Pole, MCCB - 04 Nos. Outgoing - 63 A, 25KA, Four Pole, MCCB - 04 Nos. | 1.00 | Job |  | 500000.00 | 500000.00 | 635000.00 | 635000.00 | 684045.00 | 684045.00 | 500000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
2.03 | L.T PANEL - TERMINAL BUILDING- SWITCH ROOM Design, fabrication, assembling, supply, installation, testing and commissioning of Indoor type cubicle LT panels suitable for 415 V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized design from CRCA sheet steel of 2 mm thick for frame work IP 42 degree of protection and 3 mm thick for gland plates i/c cleaning and finishing complete with 7 tank process for powder coating in approved shade, having 600 A capacity of TPN Aluminimum alloy busbar of high conductivity, DMC/SMC busbar supports, with bottom base channel of MS section not less than 100mm X 50 mm X 5 mm thick, entire panel shall have a common GI earthbar of size 25mm X 5 mm at the rear with 2 Nos. earth studs, solid connection from main busbar to switchgears with require size of aluminium busbar & control wiring with 2.5 sqmm FRLS insulated copper conductor cable, cable alleys, cable gland plates and all MCCBs shall be thermal magnetic release having overload, short circuit adjustable setting & (Ics = Icu) i/c accessories as per specification and providing switchgears, metering instruments etc. complete as required. Incomer- 400A, 36KA (at 415Volts) ,Four Pole, MCCB- 02 Nos. & having Electrical and Mechanical interlocking with both incomers and Bus Coupler. Bus Coupler- 400A ,36KA (at 415Volts) ,Four Pole, MCCB- 01 Aluminium TPN Bus Bar- 600 Amps. (1 Set) Outgoing - 125 A, 25KA, Four Pole, MCCB - 02 Nos. Outgoing - 63 A, 25KA, Four Pole, MCCB - 16 Nos. | 1.00 | Job |  | 420000.00 | 420000.00 | 365000.00 | 365000.00 | 506927.00 | 506927.00 | 365000.00 | RASS CONTRACTOR AND ENGINEERS
2.04 | STREET LIGHT FEEDER PILLAR Design, fabrication, assembling, supply, installation, testing and commissioning of Suitable size dust & vermin proof, Outdoor type, floor mounted Feeder Pillar Panel inclusive of cement concrete foundation, fabricated with 14 SWG CRCA Sheet complete with detachable gland plate and front hinged door locking arrangment duly powder coated of approved shade, requied MCB/Contacters/auto manual switch/MCB LED indicater lamp/Busbar of capacity 100 A along with other accessories including all connections, inter connection, wiring with minimum 2.5 sqmm flexible copper wire & provision for earth connection etc complete as required: Incomer 63 Amps, Four Pole MCCB having adjustable Thermal ( 80% - 100% ) and adjustable Magnetic setting, breaking capacity Ics=100% of Icu at 415 V, 25 KA - 1 No. Set of indication lamps, LED type , R, Y, B with MCBs- 1 set Bus Bar 100 Amps Aluminium busbar for phase and neutral - 1 Set Outgoing 32 Amps, TPN MCB - 04 Nos. Control 4 Pole Contactor with a thermal rating of 63A - 1 no. Time Switch with Daily dial, suitable for operation on 230 Volt, Single phase, 50 Hz, AC Supply - 1 No. Auto-Manual Selector switch - 1 Nos. On/ Off Push Buttons-1 Nos with LED indication. | 1.00 | Job |  | 35000.00 | 35000.00 | 125000.00 | 125000.00 | 67809.00 | 67809.00 | 35000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
3.00 | (SH: III) SITC OF DG SET WITH AMF PANEL
3.01 | Providing, Installing, Testing and Commissioning of Silent Type Diesel Generating set alongwith having prime power rating of 500KVA, at 1500 RPM, 0.8 lagging power factor, 415 V suitable for 50 Hz., 3-Phase system and for 0.85 Load factor and consisting of the followings : The DG set should have Accoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine and alternator, extraction, discharging hot air into the atmosphere as per specifications. & CPCB norms | 2.00 | Set |  | 3000000.00 | 6000000.00 | 3000000.00 | 6000000.00 | 3529606.00 | 7059212.00 | 6000000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION, RASS CONTRACTOR AND ENGINEERS
3.02 | a) Diesel Engine : Diesel Engine 4 Stroke water cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 40 degree C, 50% RH & at 100 meter AMSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine should be fitted day service fuel tank as per OEM standarded & shall be complete with all the required accessories.
3.03 | b) Engine mounted Instrument Panel fitted with and having digital display for following : (i) Start-Sop switch with key (ii) Water temperature indication (iii) Lubrication oil pressure indication (iv) Lubrication oil temperature indication (v) Battery charging indication (vi) RPM indication (vii) Over speed indication (viii) Low Lubrication oil trip indication (ix) Engine Hourse indication.
3.04 | c) Alternator : Synchronous alternator having rated output 500 KVA, at 415 Volts, 1500 RPM, 3-Phase 50 Hz., AC Supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 100 Meter AMSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR conforming to IS: 4772/BS 2613 suitable for tropical conditions and with class-F/H insulation.
3.05 | d) Base Frame & Foundation : Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on suitable cement concrete foundation and vibration isolation arrangement as per recommendations of manufacturer.
3.06 | e) Exhaust System : Dry exhaust mainfold with residential exhaust silencer and catalytic convertor with structure for MS support for exhaust piping including rope wrapping insulation and aluminium clading as required..
3.07 | f) Starting System : 12V/24V DC starting system comprising of starter motors: Voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries (25 plates, 180 amp. Hour capacity lead acid type or as per the OEM standard) as required as per specifications.
3.08 | g) AMF PANEL: Design, fabrication, supply , installation, testing and commissioning of dust & vermin proof Automatic Mains Failure (AMF) panel made from 2 mm thick CRCA sheet steel with aluminium busbar of minimum capacity 1000A, consisting of 2 nos. 800A, 4Pole, 50 KA (Icu = 100% Ics) ACB, with microprocessor based release having short circuit, over current, earth fault protection , digital voltmeter, ammeter, energymeter and intellegent multifunction meter to read V, A, KVA, KW, KVAR, PF Hz etc with RS 485 port, LED indicating lamps R,Y,B & 'ON','OFF' lamps, CTs, PTs, controlling relays, contactors,other components/ accessories etc. for proper operation of AMF panel and capable to deliver/transfer with full load within and suitable for operation on auto/ manual/ test mode complete as per IEC 61439 and technical specifications, complete, as reqd.
3.09 | S.I.T.C. of calibrated HSD buffer/service tank, rectangular / square MS (IS:226) construction with 990 ltrs. capacity complete with flanged inlet & outlet, overflow, drain, vent, mechanical level indicator, 450mm dia access hole on top with cover, flame arrestor. Tank will be made out of 3mm MS sheet & will be provided with structural support to keep tank base at (1500mm) above FFL, painting etc. complete as required. | 2.00 | Each |  | 100000.00 | 200000.00 | 25000.00 | 50000.00 | 49261.00 | 98522.00 | 50000.00 | RASS CONTRACTOR AND ENGINEERS
3.10 | Providing & Fixing of 25 mm dia. "C" Class M.S.pipe confirming to IS: 1239 Part-I (2004) with up to date ammendments along with accessories in surface/recess including painting in case of surface pipe, or cutting the wall and making good the same in case of recessed pipe for making connection between HSD buffer tank & DG Set complete as required. | 25.00 | Mtr. |  | 500.00 | 12500.00 | 315.00 | 7875.00 | 1532.00 | 38300.00 | 7875.00 | RASS CONTRACTOR AND ENGINEERS
3.11 | Supply, installation, testing and commissioning of 200 mm dia MS exhaust piping, heavy duty class-C ( as per IS 3589) complete with all accessories such as bends flanges, flexible connections at a suitable distance etc. and insulated with 75 mm thick layer of LRB rock wool having 144 kg/m3 density, cladding with 0.63 mm aluminium sheet all-round the exhaust pipe complete as required at site, as per CPCB norm, including fixing of residential grade silencers, flexible bellows complete as per instruction of EIC . Exhaust pipe & silencer etc shall be sopported at least with MS angle size 50 mm x 50mm x 5 mm frame / structure with necessary civil work for foundation arrangements. etc The exhaust system including the silencer must be sized to ensure that back pressure on system does not exceed the back pressure recommended by engine manufacturer. Design calculation in support shall be submitted before execution of work & got approved from the engineer in charge. Silenscers and Horizontal pipe runs shall be supported with angle frame & fixed at foundation on ground. complete as required. | 20.00 | Mtr. |  | 1000.00 | 20000.00 | 6500.00 | 130000.00 | 50860.00 | 1017200.00 | 20000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
3.12 | Making PCC foundation complete with 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) for the above DG Set canopy of suitable size as per recommendation of OEM/OEA complete as required. | 25.00 | Cum |  | 500.00 | 12500.00 | 7000.00 | 175000.00 | 5500.00 | 137500.00 | 12500.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
4.00 | (SH: IV)SUPPLY & LAYING OF CABLES
4.01 | Supply of 3 Core, following sizes of XLPE insulated PVC sheathed aluminium conductor armoured Power cable of 11 KV grade (11 KV earthed system) conforming to IS: 7098 (part-II) amended up to date. i) 3C x 95 Sq mm | 600.00 | Mtr. |  | 623.00 | 373800.00 | 500.00 | 300000.00 | 451.00 | 270600.00 | 270600.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
4.02 | Supply of followin sixes of 1.1 KV grade XLPE insulated PVC sheathed, Alumimium Conductor armoured power cable confirming to IS 7098 (Part-I) 1988 amended upto date :
4.03 | 3.5C x 400 Sq mm | 50.00 | Mtr. |  | 1307.00 | 65350.00 | 1200.00 | 60000.00 | 940.00 | 47000.00 | 47000.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
4.04 | 3.5C x 300 Sq mm | 300.00 | Mtr. |  | 1026.00 | 307800.00 | 1000.00 | 300000.00 | 710.00 | 213000.00 | 213000.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
4.05 | 3.5C x 240 Sq mm | 500.00 | Mtr. |  | 837.90 | 418950.00 | 800.00 | 400000.00 | 588.00 | 294000.00 | 294000.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
4.06 | 3.5C x 185 Sq mm | 1000.00 | Mtr. |  | 665.00 | 665000.00 | 550.00 | 550000.00 | 478.00 | 478000.00 | 478000.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
4.07 | 3.5C x 150 Sq mm | 200.00 | Mtr. |  | 533.40 | 106680.00 | 472.00 | 94400.00 | 385.00 | 77000.00 | 77000.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
4.08 | 3.5C x 70 Sq mm | 250.00 | Mtr. |  | 297.00 | 74250.00 | 265.00 | 66250.00 | 209.00 | 52250.00 | 52250.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
4.09 | 3.5C x 25 Sq mm | 300.00 | Mtr. |  | 142.00 | 42600.00 | 165.00 | 49500.00 | 98.00 | 29400.00 | 29400.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
4.10 | 4C x 6 Sq mm | 400.00 | Mtr. |  | 79.00 | 31600.00 | 112.00 | 44800.00 | 58.00 | 23200.00 | 23200.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
4.11 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of size up to 95 Sq. mm. direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. | 500.00 | Mtr. |  | 150.00 | 75000.00 | 150.00 | 75000.00 | 280.00 | 140000.00 | 75000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION, RASS CONTRACTOR AND ENGINEERS
4.12 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of size up to 95 Sq. mm. in the existing RCC/HUME/ METAL pipe as required. | 100.00 | Mtr. |  | 100.00 | 10000.00 | 55.00 | 5500.00 | 130.00 | 13000.00 | 5500.00 | RASS CONTRACTOR AND ENGINEERS
4.13 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. a) 90 mm dia (OD-90 mm & ID-76 mm nominal) | 1000.00 | Mtr. |  | 450.00 | 450000.00 | 135.00 | 135000.00 | 344.00 | 344000.00 | 135000.00 | RASS CONTRACTOR AND ENGINEERS
4.14 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc. as required.
4.15 | Upto 35 sq. Mm | 500.00 | Mtr. |  | 100.00 | 50000.00 | 75.00 | 37500.00 | 210.00 | 105000.00 | 37500.00 | RASS CONTRACTOR AND ENGINEERS
4.16 | Above 35 sq. mm and upto 95 sq. Mm | 175.00 | Mtr. |  | 120.00 | 21000.00 | 125.00 | 21875.00 | 220.00 | 38500.00 | 21000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
4.17 | Above 95 sq. mm and upto 185 sq. Mm | 850.00 | Mtr. |  | 120.00 | 102000.00 | 155.00 | 131750.00 | 230.00 | 195500.00 | 102000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
4.18 | Above 185 sq. mm and upto 400 sq. Mm | 600.00 | Mtr. |  | 200.00 | 120000.00 | 175.00 | 105000.00 | 250.00 | 150000.00 | 105000.00 | RASS CONTRACTOR AND ENGINEERS
4.19 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required.
4.20 | Upto 35 sq. Mm | 200.00 | Mtr. |  | 50.00 | 10000.00 | 25.00 | 5000.00 | 110.00 | 22000.00 | 5000.00 | RASS CONTRACTOR AND ENGINEERS
4.21 | Above 35 sq. mm and upto 95 sq. Mm | 100.00 | Mtr. |  | 50.00 | 5000.00 | 35.00 | 3500.00 | 110.00 | 11000.00 | 3500.00 | RASS CONTRACTOR AND ENGINEERS
4.22 | Above 95 sq. mm and upto 185 sq. Mm | 350.00 | Mtr. |  | 100.00 | 35000.00 | 45.00 | 15750.00 | 120.00 | 42000.00 | 15750.00 | RASS CONTRACTOR AND ENGINEERS
4.23 | Above 185 sq. mm and upto 400 sq. Mm | 250.00 | Mtr. |  | 100.00 | 25000.00 | 55.00 | 13750.00 | 130.00 | 32500.00 | 13750.00 | RASS CONTRACTOR AND ENGINEERS
4.24 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
4.25 | 3.5C x 400 Sq mm | 4.00 | Each |  | 800.00 | 3200.00 | 1500.00 | 6000.00 | 2148.00 | 8592.00 | 3200.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
4.26 | 3.5C x 300 Sq mm | 24.00 | Each |  | 700.00 | 16800.00 | 1200.00 | 28800.00 | 1666.00 | 39984.00 | 16800.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
4.27 | 3.5C x 240 Sq mm | 4.00 | Each |  | 600.00 | 2400.00 | 1000.00 | 4000.00 | 1477.00 | 5908.00 | 2400.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
4.28 | 3.5C x 150 Sq mm | 12.00 | Each |  | 500.00 | 6000.00 | 850.00 | 10200.00 | 1427.00 | 17124.00 | 6000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
4.29 | 3.5C x 70 Sq mm | 10.00 | Each |  | 500.00 | 5000.00 | 500.00 | 5000.00 | 741.00 | 7410.00 | 5000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION, RASS CONTRACTOR AND ENGINEERS
4.30 | 3.5C x 25 Sq mm | 10.00 | Each |  | 300.00 | 3000.00 | 320.00 | 3200.00 | 495.00 | 4950.00 | 3000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
4.31 | 4C x 6 Sq mm | 120.00 | Each |  | 250.00 | 30000.00 | 200.00 | 24000.00 | 438.00 | 52560.00 | 24000.00 | RASS CONTRACTOR AND ENGINEERS
4.32 | Suppy and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 3 core X 95 sqmm XLPE aluminium conductor cable of 11 KV (UE) grade as required. | 4.00 | Set |  | 2000.00 | 8000.00 | 4500.00 | 18000.00 | 8271.00 | 33084.00 | 8000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
4.33 | Suppy and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 3 core X 95 sqmm XLPE aluminium conductor cable of 11 KV (UE) grade as required. | 4.00 | Set |  | 2000.00 | 8000.00 | 6500.00 | 26000.00 | 11819.00 | 47276.00 | 8000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
5.00 | (SH: V) EARTHING
5.01 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 6.00 | Set |  | 10000.00 | 60000.00 | 4500.00 | 27000.00 | 17227.00 | 103362.00 | 27000.00 | RASS CONTRACTOR AND ENGINEERS
5.02 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 6.00 | Set |  | 20000.00 | 120000.00 | 10500.00 | 63000.00 | 26634.00 | 159804.00 | 63000.00 | RASS CONTRACTOR AND ENGINEERS
5.03 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 14.00 | Set |  | 3000.00 | 42000.00 | 3500.00 | 49000.00 | 15854.00 | 221956.00 | 42000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
5.04 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 90.00 | Mtr. |  | 850.00 | 76500.00 | 750.00 | 67500.00 | 1367.00 | 123030.00 | 67500.00 | RASS CONTRACTOR AND ENGINEERS
5.05 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 140.00 | Mtr. |  | 350.00 | 49000.00 | 125.00 | 17500.00 | 284.00 | 39760.00 | 17500.00 | RASS CONTRACTOR AND ENGINEERS
5.06 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 60.00 | Mtr. |  | 650.00 | 39000.00 | 950.00 | 57000.00 | 1682.00 | 100920.00 | 39000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
5.07 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 140.00 | Mtr. |  | 250.00 | 35000.00 | 235.00 | 32900.00 | 720.00 | 100800.00 | 32900.00 | RASS CONTRACTOR AND ENGINEERS
5.08 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 140.00 | Mtr. |  | 10.00 | 1400.00 | 236.00 | 33040.00 | 318.00 | 44520.00 | 1400.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
5.09 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 30.00 | Mtr. |  | 650.00 | 19500.00 | 700.00 | 21000.00 | 1237.00 | 37110.00 | 19500.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
5.10 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | Mtr. |  | 250.00 | 12500.00 | 115.00 | 5750.00 | 154.00 | 7700.00 | 5750.00 | RASS CONTRACTOR AND ENGINEERS
5.11 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 3500.00 | Mtr. |  | 10.00 | 35000.00 | 15.00 | 52500.00 | 38.00 | 133000.00 | 35000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
6.00 | (SH: VI) HYDRO PNEUMATIC SYSTEM
6.01 | Supply, Installation, Testing and Commissioning of Hydro Pneumatic Pump System (01 Working + 01 Standby ) veritical in-line multi stage booster centrifugal SS-316 pump motor sets of size 1.5 HP (1.1KW) with Flow 9000 LPH at Head 25 Mtrs (Each Pump) sutiable for Operation on 415 V, 50 Hz, 3 Phase AC Supply with 100 Ltr. .Pneumatic balancing tank, mounting skid, foot valve, GI Suction & discharge pipes, fittings, cast brass/virigin brass valves, CI Strainers suction head, etc. each pump shall have TEFC 2900 RPM 3 Phase electric motor includes pressure switches, VFD based control panel with starters, protection relays, cable, interlocking with level and pressure switches, suction, delivery piping all connections etc. complete as required. | 1.00 | Set |  | 50000.00 | 50000.00 | 65000.00 | 65000.00 | 282050.00 | 282050.00 | 50000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
7.00 | (SH: VII) SITC OF HIGH MAST
7.01 | 1. SUPPLY PART i)Supply of high mast shaft 20M in two section suitable for 47 m/sec wind speed as per IS:875 part-III along with head frame, luminaires carriage suitable for 10-15 nos 350W LED floodlight luminaires in symmetrical arrangement with counter weights and other accessories manufactured in factory. -01 Nos ii) Supply of raising lowering system comprising double drum winch, 6 mm diameter SS wire rope, trailing cable, connector, integral power tool motor, manual handle, junction box, lightning finial. -01 set iii) Supply of foundation bolts manufactured from special steel along with nuts, washers, anchor plate and common template. -01 Set iv) Supply of LED floodlight type 350W LED(similar to BJFL).-08 Nos. v) Supply of LED type single dome aviation obstruction light.-02 Nos vi) Supply of outdoor, made of 14 SWG CRCA sheet, IP-55, stand mounted feeder pillar with 1 no. 32A TPN MCB incomer, single dial time switch, 32A TPN contactor for the automatic switching of luminaries, power tool control with 2 no 9A contactors and raise lower push button, Incoming 35 sq. mm and out going 16 & 2.5 sq. mm terminals i/c provision for manual to raising & lowering. | 2.00 | Job |  | 400000.00 | 800000.00 | 550000.00 | 1100000.00 | 317518.00 | 635036.00 | 635036.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
7.02 | 2. ERECTION PART i) Construction of shallow foundation with M-25 grade concrete for the highmast considering the safe soil bearing capacity at site as 10 T/sqmtr at 2 metre depth with all materials and labour. ii) Erection of the high mast with the help of suitable tools and plants, wiring of luminaires with all wiring materials like PVC insulated PVC sheathed flexible cable of suitable copper conductor cores of 1.5 sq. mm, lugs, MCB and all labour. iii) Provision of GI pipe earthing for High mast with 2.5 M long 40 mm dia GI Pipe including connection to High mast earth terminal with 25 x 3 mm GI flats with all materials and labour. (2 nos per mast required) iv) Installation, Testing & Commissioning of the High Mast mast feeder pillar by grouting the stand in cement concrete complete as required. | 2.00 | Job |  | 50000.00 | 100000.00 | 185000.00 | 370000.00 | 100000.00 | 200000.00 | 100000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
8.00 | (SH: VIII) MISC. ITEMS
8.01 | Dismanteling of metallic pole i/c bracket upto 10.0 metre height along with LED street ight fittings of 72 watt with all accesories from installed location of Kishangarh (Raj) and shifting Poles, bracket & LED fittings carefully up to storage location nearby power house or as directed by EIC at Kishangarh Airport complete as required. | 30.00 | Each |  | 7000.00 | 210000.00 | 1500.00 | 45000.00 | 4000.00 | 120000.00 | 45000.00 | RASS CONTRACTOR AND ENGINEERS
8.02 | Shifting of 60 Nos. metallic poles of 10 metre height with Brackets & LED Fittings i/c Packing, forwarding, Loading & Unloading, transportation charges etc. complete as required from Kishangarh Airport to Kushinagar Airport. | 1.00 | Job |  | 50000.00 | 50000.00 | 150000.00 | 150000.00 | 130000.00 | 130000.00 | 50000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
8.03 | Erection of metallic Octagonal pole of standard height of 10.0 metre with base plate & bracket, by making of suitable pedestral foundation of size (0.45 x 0.45 x 1.70) Mtr. with PCC foundation 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) i/c providing & fixing 04 Nos. G I foundation bolt, anchor plate, template, nut & washer by laying of 32 mm dia HDPE flexible pipe for loop in/out cable i/c excavation & refilling etc. complete as required. | 60.00 | Job |  | 5000.00 | 300000.00 | 6500.00 | 390000.00 | 11575.00 | 694500.00 | 300000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
8.04 | Installation, testing and commissioning of 72 Watt LED Luminarie with all accessories on existing street light pole of 10 mtr height, including pole bracket,supplying and drawing of 3 Nos x1.5 sq.mm. PVC insulated PVC sheathed flexible copper conductor cable from loop-in-loop-out termination upto the individual street light fitting(s), connection etc. complete as required. | 60.00 | Job |  | 500.00 | 30000.00 | 1000.00 | 60000.00 | 1425.00 | 85500.00 | 30000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
8.05 | Supplying of Rubber hand gloves suitable for 11kV grade . | 2.00 | Pair |  | 1000.00 | 2000.00 | 1500.00 | 3000.00 | 191.00 | 382.00 | 382.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
8.06 | Supplying and fixing of Shock treatment chart both in Hindi & English and framed with 5mm thick glass as required.(Frame A2 Size). | 2.00 | Each |  | 5000.00 | 10000.00 | 1500.00 | 3000.00 | 228.00 | 456.00 | 456.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
8.07 | Supplying and fixing single line diagram, schematic diagrams etc. of A1 size on suitable Aluminium sheet including lamination etc. ss required complete on wall. | 2.00 | Each |  | 3000.00 | 6000.00 | 150.00 | 300.00 | 738.00 | 1476.00 | 300.00 | RASS CONTRACTOR AND ENGINEERS
8.08 | Supplying and fixing of flame retardant electrical insulation mat having no adverse effect of mineral oil, high insulation resistance and water proof of nominal size: 2.5mm +/- 10% thick and 1000mm +/-20mm wide Antistatic Electric Insulated Synthetic Mat confirming to IS: 15652: 2006 with upto date amendments suitable for 11 KV installation alongwith adhesive/resin, sealing material and similar type of taping on sealing at all joints and corners as per recommendations etc as required .The Mat shall be ISI marked. Its leakage current at 11 KV shall not be more then 10 mA.The mat shall be welded by hot gas lending with filler martial method by making V grove cut at joints with suitable welding cord of insulation material of matching colour to provide a seamless jointed surface as per IS:8002 | 6.00 | Sq.Mtr |  | 2500.00 | 15000.00 | 2000.00 | 12000.00 | 1267.00 | 7602.00 | 7602.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
8.09 | Supplying and fixing of nominal 2.0 mm thick Electric Insulated Synthetic Mat of conforming to IS:15652:2006 and meeting the requirements of IS 5216, IS 8437, IEC-479 Pub-1, alongwith suitable adhesive /chemibound, pu-resin, water proofing compound and sealing material as per in service recommendations of Annexure-'A' 'Clause C' of IS:15652 and Suitable for Class - A upto 3.3 KV AC & 240 V DC without HT Trolley movement. | 10.00 | Each |  | 2200.00 | 22000.00 | 2000.00 | 20000.00 | 924.00 | 9240.00 | 9240.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
8.10 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 20.00 | Each |  | 500.00 | 10000.00 | 200.00 | 4000.00 | 355.00 | 7100.00 | 4000.00 | RASS CONTRACTOR AND ENGINEERS
8.11 | Providing and fixing H.T. danger notice plate of 250 mm X 200 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 10.00 | Each |  | 500.00 | 5000.00 | 200.00 | 2000.00 | 341.00 | 3410.00 | 2000.00 | RASS CONTRACTOR AND ENGINEERS
8.12 | Supply of First Aid Box with medicines, accessories as approved by St.John Ambulance Brigade/Indian Red Cross conforming to IS:2217-1963. | 1.00 | Set |  | 2000.00 | 2000.00 | 2500.00 | 2500.00 | 2557.00 | 2557.00 | 2000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
8.13 | Providing of set of 04 Nos. 9.5 Ltr. Capacity GI Bucket painted in post office red colour with prior coat of Red Oxide paint and written with white paint "FIRE" and mounted on MS Angle iron frame with bracket of appropriate size and capacity including fillings sand etc. complete as required. | 2.00 | Set |  | 9500.00 | 19000.00 | 15000.00 | 30000.00 | 3443.00 | 6886.00 | 6886.00 | TECHNISYS ENGINEERING PRIVATE LIMITED
8.14 | Supplying and fixing of Wall mounted wooden Key Board of Size 450 x 600 mmx 150 mm depth suitable with 70 key pins etc complete as required. | 1.00 | Each |  | 1500.00 | 1500.00 | 1500.00 | 1500.00 | 2413.00 | 2413.00 | 1500.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION, RASS CONTRACTOR AND ENGINEERS
| Total in Figures |  |  |  |  | 14743830.00 |  | 15507140.00 |  | 19024391.00
Lowest Amount Quoted BY: PRAGYA ELECTRIC AND ELECTRONICS CORPORATION(14743830.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction Of Interim Terminal Building at Kushinagar Airport. SH- SITC of Sub Station Equipments and DG Sets Tender ID: 2020_AAI_54742_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION | 14743830.00 | L1
| 2 | RASS CONTRACTOR AND ENGINEERS | 15507140.00 | L2
| 3 | TECHNISYS ENGINEERING PRIVATE LIMITED | 19024391.00 | L3