## BoQ1
Government eProcurement System Created By: Rahul S Mankar Created Date/Time: 03-Sep-2020 01:14 PM Tender Title: Construction of New DVOR at Nagpur Airport. SH- Electrical Works. Tender ID: 2020_AAI_54852_1
Tender Inviting Authority: Asstt. Gen. Manager (Engg-Elect), AAI, Nagpur
Name of Work :- Construction of New DVOR at Nagpur Airport. SH: Electrical Works.
Contract No: Ref:- AAI/NGP/E-E/2020-21/02/DVOR/NIT-01 Date: 11.08.2020
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | M/s LEESHA ELECTRICALS(GSTN-27ABAPW8550C1ZK) |  | M/s V.R. Associates(GSTN-NA) |  | M/s BHARAT ELECTRIC, NAGPUR(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH I :- Internal & External Electrification
1.01 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
1.01 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire. | 80.00 | Mtr. | 256.00 | 160.00 | 12800.00 | 230.00 | 18400.00 | 225.00 | 18000.00 | 200.00 | 16000.00 | 12800.00 | Manish Electricals
1.01 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire. | 300.00 | Mtr. | 291.00 | 240.00 | 72000.00 | 260.00 | 78000.00 | 255.00 | 76500.00 | 250.00 | 75000.00 | 72000.00 | Manish Electricals
1.01 | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire. | 100.00 | Mtr. | 455.00 | 320.00 | 32000.00 | 430.00 | 43000.00 | 360.00 | 36000.00 | 350.00 | 35000.00 | 32000.00 | Manish Electricals
1.02 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc. as required. | 26.00 | Point | 1297.00 | 800.00 | 20800.00 | 1100.00 | 28600.00 | 750.00 | 19500.00 | 700.00 | 18200.00 | 18200.00 | M/s BHARAT ELECTRIC, NAGPUR
1.03 | Supplying and fixing following modular switch / socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
1.03 | 5/6 A switch. | 6.00 | Each | 78.00 | 60.00 | 360.00 | 65.00 | 390.00 | 80.00 | 480.00 | 75.00 | 450.00 | 360.00 | Manish Electricals
1.03 | 3 pin 5/6 A socket outlet. | 6.00 | Each | 101.00 | 80.00 | 480.00 | 100.00 | 600.00 | 105.00 | 630.00 | 100.00 | 600.00 | 480.00 | Manish Electricals
1.04 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin, 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 17.00 | Each | 498.00 | 500.00 | 8500.00 | 410.00 | 6970.00 | 505.00 | 8585.00 | 500.00 | 8500.00 | 6970.00 | M/s LEESHA ELECTRICALS
1.05 | Supplying and fixing two module stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 3.00 | Each | 334.00 | 280.00 | 840.00 | 350.00 | 1050.00 | 310.00 | 930.00 | 300.00 | 900.00 | 840.00 | Manish Electricals
1.06 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
1.06 | For 4 way, Double door TPN MCBDB | 2.00 | Each | 3109.00 | 4000.00 | 8000.00 | 3000.00 | 6000.00 | 2550.00 | 5100.00 | 2500.00 | 5000.00 | 5000.00 | M/s BHARAT ELECTRIC, NAGPUR
1.06 | For 8 way, Double door TPN MCBDB | 1.00 | Each | 4546.00 | 6000.00 | 6000.00 | 4500.00 | 4500.00 | 3600.00 | 3600.00 | 3500.00 | 3500.00 | 3500.00 | M/s BHARAT ELECTRIC, NAGPUR
1.07 | Supplying and fixing following rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
1.07 | 6 A to 32 A ratings, SP MCB. | 24.00 | Each | 248.00 | 170.00 | 4080.00 | 210.00 | 5040.00 | 155.00 | 3720.00 | 150.00 | 3600.00 | 3600.00 | M/s BHARAT ELECTRIC, NAGPUR
1.07 | 6 A to 32 A ratings, DP MCB. | 11.00 | Each | 632.00 | 470.00 | 5170.00 | 700.00 | 7700.00 | 575.00 | 6325.00 | 550.00 | 6050.00 | 5170.00 | Manish Electricals
1.07 | 32 A ratings, FP MCB. | 1.00 | Each | 1312.00 | 1200.00 | 1200.00 | 1200.00 | 1200.00 | 1225.00 | 1225.00 | 1200.00 | 1200.00 | 1200.00 | M/s BHARAT ELECTRIC, NAGPUR, Manish Electricals, M/s LEESHA ELECTRICALS
1.07 | 63 A ratings, FP MCB. | 1.00 | Each | 1834.00 | 1500.00 | 1500.00 | 1700.00 | 1700.00 | 1525.00 | 1525.00 | 1500.00 | 1500.00 | 1500.00 | M/s BHARAT ELECTRIC, NAGPUR, Manish Electricals
1.08 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps “C” curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | 12.00 | Each | 1847.00 | 900.00 | 10800.00 | 1200.00 | 14400.00 | 1100.00 | 13200.00 | 1000.00 | 12000.00 | 10800.00 | Manish Electricals
1.09 | Supply of recess type LED lighting fixture suitable for 600 X 600 mm grid false ceiling, made of CRCA housing, with a nominal system lumen output of minimum 3100 lumens, with minimum 100 Lumens / watt efficacy, high efficiency diffuser, shall comply with IS 10322 requirements and technical specifications etc. as required. - (Wipro Elate Cat Ref.:CRCO10R038HP57GL1 / Crompton Polaris NIO-I Cat. Ref. LCTLRNE-36-FO-CDL or similar) | 12.00 | Each | 3666.00 | 2400.00 | 28800.00 | 2500.00 | 30000.00 | 1800.00 | 21600.00 | 1700.00 | 20400.00 | 20400.00 | M/s BHARAT ELECTRIC, NAGPUR
1.10 | Installation, testing and commissioning of pre-wired, LED fitting / fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 12.00 | Each | 177.00 | 200.00 | 2400.00 | 100.00 | 1200.00 | 100.00 | 1200.00 | 100.00 | 1200.00 | 1200.00 | M/s BHARAT ELECTRIC, NAGPUR, M/s LEESHA ELECTRICALS, M/s V.R. Associates
1.11 | Supply of high efficiency and low power consumption 25 watt LED street light luminaire having minimum 2750 lumens output with powder coated pressure die-cast aluminium housing and toughened glass / polycarbonate cover, IP 66 protection, weatherproof gasket for lamp and control gear accessories, integral electronics with in-built short circuit, over voltage, over load and 5 KV surge protection, suitable for mounting on existing bracket arm of 40 mm outer dia. pipe bracket, as per technical specifications etc. as required. (Wipro Cat. Ref. LR02291-XXX-57-XX / Crompton Cat. Ref. LSTS-25-CDL-M or similar). | 6.00 | Each | 1689.00 | 1500.00 | 9000.00 | 2500.00 | 15000.00 | 1300.00 | 7800.00 | 1250.00 | 7500.00 | 7500.00 | M/s BHARAT ELECTRIC, NAGPUR
1.12 | Supplying and fixing of 32 mm dia X 2.00 metres long G.I. pipe (medium class) bracket for mounting of LED/ fluorescent / HPMV / HPSV street light fitting on pole including bending the pipe to the required shape, 2 nos 40 mm X 3 mm flat iron clamps with nuts, bolts and washer, painting the flat iron with primer and finish paint etc. as required. | 6.00 | Each | 1015.00 | 600.00 | 3600.00 | 800.00 | 4800.00 | 600.00 | 3600.00 | 500.00 | 3000.00 | 3000.00 | M/s BHARAT ELECTRIC, NAGPUR
1.13 | Installation, Testing and Commissioning of 25 W LED fitting on existing pole bracket / wall bracket including providing 3C x 1.5 sqmm PVC insulated copper conductor flexible cable of suitable length, connections etc. complete as required. | 6.00 | Job | 214.00 | 200.00 | 1200.00 | 100.00 | 600.00 | 100.00 | 600.00 | 100.00 | 600.00 | 600.00 | M/s BHARAT ELECTRIC, NAGPUR, M/s LEESHA ELECTRICALS, M/s V.R. Associates
1.14 | Supply of size 48" (1200 mm) Ceiling fan suitable for operating on 230V AC etc. as required. (Make - Havells Model ES-50 or similar). | 3.00 | Each | 2006.00 | 1800.00 | 5400.00 | 1700.00 | 5100.00 | 1850.00 | 5550.00 | 1800.00 | 5400.00 | 5100.00 | M/s LEESHA ELECTRICALS
1.15 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (up to 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required. | 3.00 | Each | 182.00 | 100.00 | 300.00 | 100.00 | 300.00 | 100.00 | 300.00 | 100.00 | 300.00 | 300.00 | M/s BHARAT ELECTRIC, NAGPUR, Manish Electricals, M/s LEESHA ELECTRICALS, M/s V.R. Associates
1.16 | Supply of 380 mm, 1400 rpm Heavy Duty Exhaust Fan with suitable louvers / shutters complete with frame, suitable for operating on 230V AC etc. complete as required. (Make - Havells Model Turbo Force SP or similar) | 3.00 | Each | 3094.00 | 3500.00 | 10500.00 | 3000.00 | 9000.00 | 2550.00 | 7650.00 | 2500.00 | 7500.00 | 7500.00 | M/s BHARAT ELECTRIC, NAGPUR
1.17 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. (Up to 450 mm sweep). | 3.00 | Each | 558.00 | 100.00 | 300.00 | 300.00 | 900.00 | 100.00 | 300.00 | 100.00 | 300.00 | 300.00 | M/s BHARAT ELECTRIC, NAGPUR, Manish Electricals, M/s V.R. Associates
1.18 | Supply, installation, testing and commissioning of cubicle type, floor mounted, indoor type, IP-42 rating LT panel suitable for operation on 415V, 3 phase, 4 wire 50Hz AC supply system, fabricated in totally enclosed and compartmentalized design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick for segmented gland plates, powder coating in approved shade, with TPN Aluminium Alloy bus bars of high conductivity extensible type on both sides, rated for 200 Amps with short circuit withstand capacity of 35kA for 1 Sec., bottom base channel of MS frame of suitable size, common earth bus bar, connections from main bus bars to switch gears with required size of copper / aluminium conductors / bus bars, control wiring with 2.5 sqmm PVC insulated copper conductor flexible cable, i/c providing following switch gears etc. as per technical specifications as required. | 1.00 | Job | 230755.00 | 125000.00 | 125000.00 | 225000.00 | 225000.00 | 175000.00 | 175000.00 | 150000.00 | 150000.00 | 125000.00 | Manish Electricals
1.18 | INCOMER (a) 125 Amps, 4 pole MCCB (ICS = 100% ICU), Thermal release range of 100-125 A, 30 kA (L&T DU125H Cat. No. CM90679OOLO or similar) - 4 Nos. (b) C. T. 100/5 Amps, 5 VA, CL-1 - 9 Nos. (c) LED type indication lamps for RYB & ON/OFF indication for each MCCB with control MCB. - 02 sets. (d) Multifunction meter of Class accuracy 1.0 ( Schneider Conzerv 5.1 Hexa Series Product Code EM6436H / L&T MFM 4405 WL440511OOOO or similar) - 2 Nos. (e) 3 Phase 4 Wire kWh Meter, CT op base mounting, Class accuracy 0.5s (L&T ER 300P WR301BC3C00 or similar) - 1 No. (f) Automatic Transfer Switch with Controller (Open Execution), Four Pole, 50 Hz, 415 V with complete protection. (Havells - IHYFCDO125/ ABB or similar) - 1 No. (g) 125 Amps, 4 pole Change over Switch with operating handle (L&T Cat No. CO21250OOOO OR similar) - 1 No.
1.18 | OUTGOINGS (a) 63 Amps, 4 pole MCCB (ICS = 100% ICU), Thermal release range of 50-63 (A), 30 kA (L&T DU100H Cat. No. CM97933OOH2 or similar) - 5 Nos. (b) LED type indication lamps for ON/OFF indication for each MCCB with control MCBs. - 7 sets. NOTE: All MCCBs shall be provided with rotary operating handle and spreader terminals.
1.19 | Supply, installation, testing and commissioning outdoor feeder pillar box of minimum size 450 X 450 X 300 mm depth, suitable for operation on 415V, 3 phase, 4 wire 50Hz AC supply system, fabricated in totally enclosed, free standing, non-extensible, IP-65 rated design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates, complete with 35 kA rated 200 Amp current capacity Aluminium Bus-bars, hinged front & back door opening & locking arrangement, painted/powder coated with one coat of red oxide & two coats of enamel paint, suitable openings at the bottom for cable entries, earthing bolts etc. The box shall be mounted on MS angle stand to be grouted in 1:2:4 concrete of 100 X 100 X 300 mm depth, providing & laying in position cement concrete (PCC) of specified grade around the feeder panel boxes (PCC Size 1Mtr X 1 Mtr X 0.25 Mtr) (1:2:4) (1 cement: 2 coarse sand: 4 graded stone aggregate 40mm nominal size) with Suitable HDPE pipe for cable in & out to the boxes, etc. as per technical specifications as required. | 1.00 | Job | 7356.00 | 12000.00 | 12000.00 | 15000.00 | 15000.00 | 15000.00 | 15000.00 | 12000.00 | 12000.00 | 12000.00 | M/s BHARAT ELECTRIC, NAGPUR, Manish Electricals
1.20 | Supply, installation, testing and commissioning outdoor feeder pillar box of minimum size 450 X 450 X 300 mm depth, suitable for operation on 415V, 3 phase, 4 wire 50Hz AC supply system, fabricated in totally enclosed, free standing, non-extensible, IP 65 rated design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates, complete with 35 kA rated 200 Amp current capacity Aluminium Bus-bars, hinged front & back door opening & locking arrangement, painted/powder coated with one coat of red oxide & two coats of enamel paint, suitable openings at the bottom for cable entries, earthing bolts etc. The box shall be mounted on MS angle stand to be grouted in 1:2:4 concrete of 100 X 100 X 300 mm depth, providing & laying in position cement concrete (PCC) of specified grade around the feeder panel boxes (PCC Size 1Mtr X 1 Mtr X 0.25 Mtr) (1:2:4) (1 cement: 2 coarse sand: 4 graded stone aggregate 40mm nominal size) with Suitable HDPE pipe for cable in & out to the boxes, i/c providing following switch gears etc. as per technical specifications as required. (a) 125 Amps, 4 pole MCCB (ICS = 100% ICU), Thermal release range of 100-125 (A), 30 kA (L&T DU125H Cat. No. CM90679OOLO or similar) - 1 No. NOTE: All MCCBs shall be provided with rotary operating handle and spreader terminals. | 1.00 | Job | 12747.00 | 35000.00 | 35000.00 | 20000.00 | 20000.00 | 30000.00 | 30000.00 | 25000.00 | 25000.00 | 20000.00 | M/s LEESHA ELECTRICALS
1.21 | Supply, installation, testing and commissioning of Type 1+2 Three phase Surge Protection on existing panel on input side to eliminate the direct & indirect lightning surges and switching surges from electrical power supply system. The SPD shall be have combined varistor block with encapsulated spark gap (GDT) protection for L-N and encapsulated spark gap (GDT) protection for N-PE, no following current, with visual fault signalling, voltage protection level of 1.5 kV, according to IEC / EN 61643-11, suitable for DIN rail mounting along with 32A, FP C-Series MCB in an IP-42 polycarbonate enclosure with clear front cover including complete connection with copper flexible cable and shall be as per technical specifications etc. as required. (Make: Finder / 7P.04.8.260.1025 or similar) | 2.00 | Set | 89618.00 | 55000.00 | 110000.00 | 75000.00 | 150000.00 | 17000.00 | 34000.00 | 15000.00 | 30000.00 | 30000.00 | M/s BHARAT ELECTRIC, NAGPUR
1.22 | Supply of following size Aluminium conductor, XLPE insulated, PVC sheathed (FRLS), armoured power cable for working voltage 1.1 KV grade & as per IS: 7098 (Part- I) 1988 with up to date amendments of approved make & as per technical specifications etc. complete as required.
1.22 | 3.5 core X 185 sq.mm. | 60.00 | Mtr. | 624.00 | 540.00 | 32400.00 | 625.00 | 37500.00 | 700.00 | 42000.00 | 650.00 | 39000.00 | 32400.00 | Manish Electricals
1.22 | 3.5 core X 120 sq.mm. | 120.00 | Mtr. | 420.00 | 460.00 | 55200.00 | 425.00 | 51000.00 | 425.00 | 51000.00 | 400.00 | 48000.00 | 48000.00 | M/s BHARAT ELECTRIC, NAGPUR
1.22 | 3.5 core X 70 sq.mm. | 700.00 | Mtr. | 289.00 | 280.00 | 196000.00 | 280.00 | 196000.00 | 325.00 | 227500.00 | 300.00 | 210000.00 | 196000.00 | Manish Electricals, M/s LEESHA ELECTRICALS
1.23 | Providing, laying and fixing 100 mm dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep) and re-filling etc. as required. | 36.00 | Mtr. | 959.00 | 1500.00 | 54000.00 | 1000.00 | 36000.00 | 775.00 | 27900.00 | 750.00 | 27000.00 | 27000.00 | M/s BHARAT ELECTRIC, NAGPUR
1.24 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC pipe as required.
1.24 | Above 35 sq. mm and up to 95 sq. mm | 660.00 | Mtr. | 50.00 | 50.00 | 33000.00 | 50.00 | 33000.00 | 55.00 | 36300.00 | 50.00 | 33000.00 | 33000.00 | M/s BHARAT ELECTRIC, NAGPUR, Manish Electricals, M/s LEESHA ELECTRICALS
1.24 | Above 95 sq. mm and up to 185 sq. mm | 174.00 | Mtr. | 68.00 | 80.00 | 13920.00 | 50.00 | 8700.00 | 60.00 | 10440.00 | 50.00 | 8700.00 | 8700.00 | M/s BHARAT ELECTRIC, NAGPUR, M/s LEESHA ELECTRICALS
1.25 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers, end caps etc. conforming to IS 16205, Part 24 complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
1.25 | (i) 120 mm size (OD-120 mm & ID-103 mm nominal) | 798.00 | Mtr. | 294.00 | 280.00 | 223440.00 | 250.00 | 199500.00 | 255.00 | 203490.00 | 250.00 | 199500.00 | 199500.00 | M/s BHARAT ELECTRIC, NAGPUR, M/s LEESHA ELECTRICALS
1.26 | Extra for Excavation for cable trenches in hard rock/PCC/Bituminous not exceeding 1.5 meters in width and lift up to 1.5 meters, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 meters. | 5.00 | CuM | 728.00 | 500.00 | 2500.00 | 500.00 | 2500.00 | 550.00 | 2750.00 | 500.00 | 2500.00 | 2500.00 | M/s BHARAT ELECTRIC, NAGPUR, Manish Electricals, M/s LEESHA ELECTRICALS
1.27 | Supplying and making end termination with brass compression gland and Aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required.
1.27 | 3½ X 70 sq. mm (38 mm) | 5.00 | Set | 408.00 | 300.00 | 1500.00 | 350.00 | 1750.00 | 200.00 | 1000.00 | 150.00 | 750.00 | 750.00 | M/s BHARAT ELECTRIC, NAGPUR
1.27 | 3½ X 120 sq. mm (45 mm) | 4.00 | Set | 525.00 | 600.00 | 2400.00 | 500.00 | 2000.00 | 250.00 | 1000.00 | 200.00 | 800.00 | 800.00 | M/s BHARAT ELECTRIC, NAGPUR
1.27 | 3½ X 185 sq. mm (57mm) | 2.00 | Set | 775.00 | 900.00 | 1800.00 | 600.00 | 1200.00 | 300.00 | 600.00 | 250.00 | 500.00 | 500.00 | M/s BHARAT ELECTRIC, NAGPUR
1.28 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 6473.00 | 6000.00 | 12000.00 | 6000.00 | 12000.00 | 5500.00 | 11000.00 | 5000.00 | 10000.00 | 10000.00 | M/s BHARAT ELECTRIC, NAGPUR
1.29 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 12323.00 | 16000.00 | 32000.00 | 12000.00 | 24000.00 | 10500.00 | 21000.00 | 10000.00 | 20000.00 | 20000.00 | M/s BHARAT ELECTRIC, NAGPUR
1.30 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtr. | 1123.00 | 900.00 | 18000.00 | 1000.00 | 20000.00 | 800.00 | 16000.00 | 750.00 | 15000.00 | 15000.00 | M/s BHARAT ELECTRIC, NAGPUR
1.31 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtr. | 432.00 | 450.00 | 9000.00 | 600.00 | 12000.00 | 150.00 | 3000.00 | 150.00 | 3000.00 | 3000.00 | M/s BHARAT ELECTRIC, NAGPUR, M/s V.R. Associates
1.32 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 10.00 | Mtr. | 951.00 | 700.00 | 7000.00 | 800.00 | 8000.00 | 750.00 | 7500.00 | 750.00 | 7500.00 | 7000.00 | Manish Electricals
1.33 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 10.00 | Mtr. | 207.00 | 180.00 | 1800.00 | 200.00 | 2000.00 | 125.00 | 1250.00 | 150.00 | 1500.00 | 1250.00 | M/s V.R. Associates
1.34 | Providing and laying in position cement concrete of specified grade excluding the cost of centering, shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand(zone-III) : 4 graded stone aggregate 20 mm nominal size) | 1.28 | CuM | 6684.00 | 4000.00 | 5120.00 | 5000.00 | 6400.00 | 5250.00 | 6720.00 | 5000.00 | 6400.00 | 5120.00 | Manish Electricals
1.35 | Excavation for foundation in soft soil including dressing of sides and ramming of bottoms, lift up to 3 m including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 22.28 | CuM | 697.00 | 400.00 | 8912.00 | 500.00 | 11140.00 | 525.00 | 11697.00 | 500.00 | 11140.00 | 8912.00 | Manish Electricals
2.00 | SH: II - SITC of Split ACs
2.01 | Supply of Inverter type, 5 star rated 1.5 TR split air conditioner having inverter rotary / scroll type compressor, 100% copper condenser, with cordless remote control, refrigerant type R-32, suitable for operation on 230 V AC, 50 Hz, 1-Ph power supply, suitable for operation in ambient temperature of 52 Deg.C (minimum) etc. complete as per technical specifications as required. (Make/model: Bluestar/DBTX or Voltas/ 185V JZJ or similar). | 4.00 | Each | 31336.00 | 38000.00 | 152000.00 | 35000.00 | 140000.00 | 42000.00 | 168000.00 | 40000.00 | 160000.00 | 140000.00 | M/s LEESHA ELECTRICALS
2.02 | Supply of Inverter type, 5 star rated 2.0 TR split air conditioner having inverter dual / twin rotary / scroll type compressor, 100% copper condenser, with cordless remote control, refrigerant type R-32, suitable for operation on 230 V AC, 50 Hz, 1-Ph power supply, suitable for operation in ambient temperature of 52 Deg.C (minimum) etc. complete as per technical specifications as required. (Make/model: Bluestar/DATX or Voltas/ 245V ADZ or similar). | 4.00 | Each | 47833.00 | 55000.00 | 220000.00 | 48000.00 | 192000.00 | 55500.00 | 222000.00 | 55000.00 | 220000.00 | 192000.00 | M/s LEESHA ELECTRICALS
2.03 | Installation, testing & commissioning of inverter type 1.5/2 TR split air conditioner by fixing indoor unit on wall/ceiling/structure and outdoor unit on wall/stand including providing & fixing suitable size duly painted / powder coated M.S. / G.I. equal angle base frame (ODU Stand), providing and fixing suction/discharge refrigerant copper piping with elastomeric nitrile rubber insulation (Up to 4 Mtrs), control cabling (Up to 4 Mtrs) from indoor to outdoor unit, fasteners, charging of refrigerant gas i/c minor civil works and all accessories etc. complete as per technical specifications as required. | 8.00 | Job | 1646.00 | 2000.00 | 16000.00 | 2000.00 | 16000.00 | 3500.00 | 28000.00 | 3000.00 | 24000.00 | 16000.00 | Manish Electricals, M/s LEESHA ELECTRICALS
2.04 | Supply & fixing (Over and above 4 Mtrs included in Item No: 3) of suction/discharge refrigerant copper piping for 1.5/2 TR split AC with elastomeric nitrile rubber insulation between indoor and outdoor units with suitable size of clamp / MS hanger / MS support / MS angle as per site requirement and as per technical specifications as required. | 30.00 | Mtr. | 887.00 | 600.00 | 18000.00 | 800.00 | 24000.00 | 275.00 | 8250.00 | 250.00 | 7500.00 | 7500.00 | M/s BHARAT ELECTRIC, NAGPUR
2.05 | Supply & fixing 25 mm dia. UPVC drain pipe including cutting, jointing with approved solvent cement compound as per IS 14735, etc complete as required. | 30.00 | Mtr. | 209.00 | 90.00 | 2700.00 | 150.00 | 4500.00 | 110.00 | 3300.00 | 100.00 | 3000.00 | 2700.00 | Manish Electricals
2.06 | Supply and laying of 3 C x 4 Sq. mm PVC insulated, FRLS PVC sheathed, unarmoured, multi stranded copper cable as per IS : 694 along with refrigerant piping between indoor and outdoor unit of 1.5/2.0 TR Split type AC units etc as required. | 30.00 | Mtr. | 118.00 | 120.00 | 3600.00 | 120.00 | 3600.00 | 175.00 | 5250.00 | 150.00 | 4500.00 | 3600.00 | Manish Electricals, M/s LEESHA ELECTRICALS
2.07 | Supply, installation, testing and commissioning of AC timer suitable to control 2 No. 1.5 / 2.0 TR Split ACs, suitable for operation with 230 VAC +/- 15 %, 50Hz AC power supply, output contacts rating of 25 A at 230 V AC with heavy duty connectors rated for 25 Amps for both ACs, cycle time from 4 / 8 hours, with auto / manual mode, test mode etc. as per technical specifications as required. | 4.00 | Each | 3211.00 | 1800.00 | 7200.00 | 3500.00 | 14000.00 | 11000.00 | 44000.00 | 10000.00 | 40000.00 | 7200.00 | Manish Electricals
2.08 | Supply, installation, testing and commissioning of 4 KVA, 12 Amp, 170V-270V voltage stabilizer of wall mounting type with Instant Start and Intelligent time delay provisions complete etc. as required. (Make : V-Guard Model : VG400, Make : Everest Model: EW 400 or similar) | 4.00 | Each | 1514.00 | 3000.00 | 12000.00 | 2100.00 | 8400.00 | 2500.00 | 10000.00 | 2200.00 | 8800.00 | 8400.00 | M/s LEESHA ELECTRICALS
2.09 | Supply, installation, testing and commissioning of 5 KVA, 15 Amp, 170V-270V voltage stabilizer of wall mounting type with Instant Start and Intelligent time delay provisions complete etc.as required. (Make : V-Guard Model : VG500, Make : Everest Model: EW 500 or similar) | 4.00 | Each | 1724.00 | 5000.00 | 20000.00 | 2500.00 | 10000.00 | 4000.00 | 16000.00 | 3500.00 | 14000.00 | 10000.00 | M/s LEESHA ELECTRICALS
3.00 | SH: III - Fire Detection and Alarm System
3.01 | Supply, Installation, Testing & Commissioning of UL / EN listed (latest version) Modular Microprocessor based intelligent Addressable Type Fire Alarm Control Panel of one loop, with minimum 80-character graphics / back-lit LCD display with touch screen or other keypad including suitable mounting enclosure. The panel should be equipped with loop capacity to take minimum 64 intelligent addressable detectors/ devices (In any combination) in one loop. The panel shall have networking capability, RS 485 connectivity, two access levels, capable of taking Protocol Devices, sufficient numbers of programmable relay controls, built-in real time clock operation with provision of GSM Auto Dialler facilitation (Inbuilt or externally installed) and shall be capable to auto dial minimum 5 No. mobile / telephone nos. in case of any emergency /exigency, suitable for 230 volts, 50 Hz AC power supply, automatic battery charger, 12/24 volts sealed maintenance free lead acid batteries (Minimum 12 V, 7 Ah) sufficient for 24 hours normal working and capable of operating the system for 30 minutes during an emergency / fault conditions along with battery stand / enclosure etc. complete as per technical specifications as required. (Make: Edwards / IO-64 / Make: Honeywell - Morley IAS - DXc Series or similar) | 1.00 | Job | 73699.00 | 80000.00 | 80000.00 | 85000.00 | 85000.00 | 125000.00 | 125000.00 | 115000.00 | 115000.00 | 80000.00 | Manish Electricals
3.02 | Supply, installation, testing & commissioning of UL /EN listed (latest version) Repeater Panel having controls for system reset, accept, mute, silence alarms and self test; RS 485 communication capability; back-lit 80 character LCD display with touch screen or other keypad including suitable enclosure for panel mounting, providing all components & accessories for suitable DC power supply to the panel etc. complete as per technical specifications as required. (Make: Edwards / RLCD-C / Make: Honeywell - Morley IAS ZXr-A or similar) | 1.00 | Job | 46512.00 | 30000.00 | 30000.00 | 50000.00 | 50000.00 | 60000.00 | 60000.00 | 55000.00 | 55000.00 | 30000.00 | Manish Electricals
3.03 | Supply, installation, testing & commissioning of UL / EN listed (latest version) Addressable Intelligent multi-criteria detector (Smoke + Heat) with in-built fault isolator / isolator base, with optical sensing chamber, with visible multi-color LED Status indication, suitable for 2 wires loop connection, with all accessories like plug-in common base, base box, etc. to be installed below / above false ceiling, concealed space etc. complete with interconnections to loop cable as per technical specifications as required. (Make: Edwards / SIGA-PHD+IB / Make: Honeywell - Morley IAS - MI-PTSE-S2I or similar) | 8.00 | Each | 2380.00 | 5000.00 | 40000.00 | 2250.00 | 18000.00 | 3500.00 | 28000.00 | 3000.00 | 24000.00 | 18000.00 | M/s LEESHA ELECTRICALS
3.04 | Supply, installation, testing & commissioning of UL / EN listed (latest version) Addressable intelligent fixed temperature cum rate-of-rise type Heat Detector with in-built fault isolator / isolator base, with multi-color LED status indication complete with all accessories like plug-in common base, base box, etc. to be installed below / above false ceiling, concealed space etc. complete with interconnections to loop cable as per technical specifications as required. (Make: Edwards / SIGA-HRD+IB / Make: Honeywell - Morley IAS - MI-RHSE-S2I or similar) | 3.00 | Each | 2425.00 | 4800.00 | 14400.00 | 2250.00 | 6750.00 | 3200.00 | 9600.00 | 3000.00 | 9000.00 | 6750.00 | M/s LEESHA ELECTRICALS
3.05 | Supply, installation, testing & commissioning of UL / EN listed (latest version) intelligent addressable Manual Call Station / Manual Pull Station (Resettable pull / push type) with inbuilt fault isolator / isolator module, with LED for status indication, suitable for semi flush mounting and indoor use, with double gang outlet box, equipment for key operator test-reset lock, electronic or rotary switches for address setting etc. complete as per technical specifications as required. (Make: Edwards / SIGA-278 with Isolator / Make: Honeywell - Morley IAS - MI-MCP-Flex-I or similar) | 2.00 | Each | 3489.00 | 2500.00 | 5000.00 | 3350.00 | 6700.00 | 3200.00 | 6400.00 | 3000.00 | 6000.00 | 5000.00 | Manish Electricals
3.06 | Supply, installation, testing & commissioning of UL / EN listed (latest version) loop powered addressable sounder cum strobe with inbuilt fault isolator / isolator module complete with all fixing accessories, interconnections to loop cable etc. complete as per technical specifications as required. (Make: Edwards / G1RF-HDVM with Isolator / Make: Honeywell - Morley IAS - MI-WSS-PR-I or similar) | 2.00 | Each | 3388.00 | 2500.00 | 5000.00 | 3350.00 | 6700.00 | 6200.00 | 12400.00 | 6000.00 | 12000.00 | 5000.00 | Manish Electricals
3.07 | Supply, Installation, testing & commissioning of UL / EN listed (Latest Version) LED Remote Indicator for getting fire indications of detectors installed above false ceiling area complete including mounting boxes with all fixing accessories, interconnections to loop cable etc. complete as per technical specifications as required. (Make: Edwards / SIGA-LED / Make: Honeywell - Morley IAS - IRK-2E or similar) | 4.00 | Each | 587.00 | 500.00 | 2000.00 | 250.00 | 1000.00 | 300.00 | 1200.00 | 250.00 | 1000.00 | 1000.00 | M/s BHARAT ELECTRIC, NAGPUR, M/s LEESHA ELECTRICALS
3.08 | Supply, installation, testing & commissioning of RS-485 to single mode fibre optic signal converter including all accessories, enclosure, connectors, cords, cards etc. to connect the fire alarm panel to repeater panel at Equipment Room through existing OFC network etc. complete as required. (Make: Honeywell / SIGA-CC1 or similar) | 1.00 | Each | 45726.00 | 15000.00 | 15000.00 | 17996.00 | 17996.00 | 55000.00 | 55000.00 | 52000.00 | 52000.00 | 15000.00 | Manish Electricals
3.09 | Supply and laying 2 core X 1.5 sq.mm. size Copper conductor, XLPE insulated, PVC sheathed (FRLS), armoured cable as per IS: 7098 (Part- I) 1988 with up to date amendments of approved make & as per technical specifications etc. complete as required. | 100.00 | Mtr. | 102.00 | 120.00 | 12000.00 | 100.00 | 10000.00 | 80.00 | 8000.00 | 75.00 | 7500.00 | 7500.00 | M/s BHARAT ELECTRIC, NAGPUR
3.10 | Supply of trolley mounted CO2 type fire extinguisher of 6.5 Kgs. Capacity as per IS: 2878 with initial filling of CO2 gas as per IS: 15222 in mild steel body cylinder with powder coated finish, wheel type discharge valve, discharge hose with horn etc. complete as per technical specifications as required. | 6.00 | Each | 11582.00 | 12000.00 | 72000.00 | 12000.00 | 72000.00 | 9200.00 | 55200.00 | 9000.00 | 54000.00 | 54000.00 | M/s BHARAT ELECTRIC, NAGPUR
| Total in Figures |  |  |  |  | 1964922.00 |  | 2045786.00 |  | 2045667.00 |  | 1912290.00
Lowest Amount Quoted BY: M/s BHARAT ELECTRIC, NAGPUR(1912290.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New DVOR at Nagpur Airport. SH- Electrical Works. Tender ID: 2020_AAI_54852_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s BHARAT ELECTRIC, NAGPUR | 1912290.00 | L1
| 2 | Manish Electricals | 1964922.00 | L2
| 3 | M/s V.R. Associates | 2045667.00 | L3
| 4 | M/s LEESHA ELECTRICALS | 2045786.00 | L4