## BoQ1
Government eProcurement System Created By: PREMLATA MEHRA Created Date/Time: 14-Sep-2020 11:28 AM Tender Title: C/o Community Hall-Electrical Works Tender ID: 2020_AAI_55042_1
Tender Inviting Authority: AAI, Shillong Airport
Name of Work: Construction of Community centre, Mini Foot Ball Ground and Sitting arrangement for present use of Residents of AAI Colony at Shillong Airport. SH: Electrical Works.
Contract No: Tender ID: 2020_AAI_55042_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Kiswel Kharbuli(GSTN-17ALGPK8493G1ZO) |  | M/s S.T. Electricals(GSTN-18AJRPK5206C1ZA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying following type of surface/recess mounted LED light luminare with all accessories complete as reqd. at site. Recess mounted 36-42W (2x2) square down LED luminaries complete with non-integral electronic drive, made in powder coated CRCA/Aluminium housing with opel diffuser suitable to operate in 230V,50Hz AC supply etc, as required. (Make:Havells PLUTONEO2x2PLR42WLED857S OR SIMILAR ) | 50.00 | Each |  | 5500.00 | 275000.00 | 5400.00 | 270000.00 | 270000.00 | M/s S.T. Electricals
2.00 | Supplying following type of surface/recess mounted LED light luminare with all accessories complete as reqd. at site. LED Tube Light Complete With Batten , LED Lamp & associated accessories as per manufacturers technical specification, approved makes (Make: Havells MAGNUMRETROILS1x18PC ) | 10.00 | Each |  | 2000.00 | 20000.00 | 2400.00 | 24000.00 | 20000.00 | Kiswel Kharbuli
3.00 | Supplying following type of surface/recess mounted LED light luminare with all accessories complete as reqd. at site. LED street light made up of pressure die cast aluminium housing with high power LED as lighting source and lens embedded PC cover having TOP OPENINg seperate driver compartment with IP65 protection and impact resistance of IK07. (Make: Havells model :ENDURAPEARLSL25WLED757SASYTOPC or similar) | 20.00 | Each |  | 2650.00 | 53000.00 | 2657.00 | 53140.00 | 53000.00 | Kiswel Kharbuli
4.00 | Supply of 180 W LED Flood lights fitting with high power LED , epoxy powder coated high pressure die - cast aluminium housing with weather proof gasket, control gear, toughend glass cover/ clear polycarbonate front cover , with IP-66 protection and a colour temperature CCT of 5700K, high power LED 's with individual lense optics to get optimum optical performance, LED light fixture efficiency > 80 Lumen/ per watt, inbuilt surge protection upto 5KV, heat sinks, Average life of LED ≥ 50000 burning hrs, and suitable for voltage range of 140- 280V AC Supply with suitable fixing arrangement on truss work complete as required. | 18.00 | Each |  | 27500.00 | 495000.00 | 30000.00 | 540000.00 | 495000.00 | Kiswel Kharbuli
5.00 | Supply of surface & wall mounted 20-22W LED Batten with extruded aluminum housing and robust construction complete with integral electronic drive, suitable to operate in 230V,50Hz AC supply etc, along with mounting accessories complete as required.(Equivalent to Havells Model No.ENDURALINERNEOBS20WLED865SPCWH or Similar) | 20.00 | Each |  | 1050.00 | 21000.00 | 1300.00 | 26000.00 | 21000.00 | Kiswel Kharbuli
6.00 | Supply of 70 W LED type designer Post top Lantern light fixtures having high pressure powder coated die cast aluminium housing with top cover and high impact polycarbonate/arcylic protector/diffuser , with min IP-65 protection and a colour temperature CCT of 5700 + 300K, high power LED 's with individual lense optics to get optimum optical performance, LED light fixture efficiency > 80 Lumen/ per watt, Average life of LED ≥ 50000 burning hrs, and suitable for voltage range of 140- 280V AC Supply with fixing arrangement on min 65 mm dia GI pipe, complete as reqd. (Make: Havells Model No. TYCOONPT70WLED&%&PSYMTOPC or Similar). | 8.00 | Each |  | 41600.00 | 332800.00 | 4300.00 | 34400.00 | 34400.00 | M/s S.T. Electricals
7.00 | Supply of following type of fan suitable for operation on 230 volts,single phase, 50 Hz A.C supply and as per the makes & detail specification . (a) Exhaust fan 300mm , 1400 rpm heavy duty. | 2.00 | Each |  | 3830.00 | 7660.00 | 4250.00 | 8500.00 | 7660.00 | Kiswel Kharbuli
8.00 | Supply of 450 mm sweep 1400 rpm with metallic lustre finish, minimum 85° oscillation for wider coverage, integral switchgear box, height adjustable stand and push Button regulator, Air circulator Pedestal fan suitable for operation on 230V, 50HZ single phase AC supply as required. | 15.00 | Each |  | 8200.00 | 123000.00 | 8279.00 | 124185.00 | 123000.00 | Kiswel Kharbuli
9.00 | Supply of Automatic Hand Dryers of 2500W with full Stainless Steel Body and projected nozzle with timer auto cut off with all standard accessories etc as required. | 2.00 | Each |  | 8000.00 | 16000.00 | 7900.00 | 15800.00 | 15800.00 | M/s S.T. Electricals
10.00 | Supply of Hot & Cold RO+UV water purifier with storage capacity of cold tank of 4litres hot tank of 1.5litres and header tank of 11 litres of make Aquaguard or its equivalent. | 1.00 | Each |  | 38300.00 | 38300.00 | 4300.00 | 4300.00 | 4300.00 | M/s S.T. Electricals
11.00 | Supply of following sizes XLPE insulated and PVC sheathed Aluminium conductor, armoured LT cable of 1.1 KV grade conforming to IS-7098 (Part-I) with upto date amendments etc complete as required. (a) 3 ½ X 150 Sq.mm | 800.00 | Meter |  | 585.00 | 468000.00 | 700.00 | 560000.00 | 468000.00 | Kiswel Kharbuli
12.00 | Supply of following sizes XLPE insulated and PVC sheathed Aluminium conductor, armoured LT cable of 1.1 KV grade conforming to IS-7098 (Part-I) with upto date amendments etc complete as required. (b) 4 X 35 Sq.mm | 200.00 | Meter |  | 190.00 | 38000.00 | 200.00 | 40000.00 | 38000.00 | Kiswel Kharbuli
13.00 | Supply of following sizes XLPE insulated and PVC sheathed Aluminium conductor, armoured LT cable of 1.1 KV grade conforming to IS-7098 (Part-I) with upto date amendments etc complete as required. (b) 4 X 16 Sq.mm | 400.00 | Meter |  | 125.00 | 50000.00 | 150.00 | 60000.00 | 50000.00 | Kiswel Kharbuli
14.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. Group A | 15.00 | Point |  | 990.00 | 14850.00 | 1350.00 | 20250.00 | 14850.00 | Kiswel Kharbuli
15.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. Group C | 20.00 | Point |  | 1315.00 | 26300.00 | 1791.00 | 35820.00 | 26300.00 | Kiswel Kharbuli
16.00 | Wiring for circuit/ submain wiring with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required (a) 2 x 2.5sqmm + 1 x 2.5 sq.mm | 400.00 | Meter |  | 275.00 | 110000.00 | 500.00 | 200000.00 | 110000.00 | Kiswel Kharbuli
17.00 | Wiring for circuit/ submain wiring with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required (b) 4 x 2.5sqmm + 2 x 2.5 sq.mm | 200.00 | Meter |  | 440.00 | 88000.00 | 590.00 | 118000.00 | 88000.00 | Kiswel Kharbuli
18.00 | Wiring for circuit/ submain wiring with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required (c) 2x 4 sqmm + 1 x 4 sq.mm | 300.00 | Meter |  | 350.00 | 105000.00 | 400.00 | 120000.00 | 105000.00 | Kiswel Kharbuli
19.00 | Wiring for circuit/ submain wiring with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required (d) 4x 4 sqmm + 2 x 4 sq.mm | 100.00 | Meter |  | 570.00 | 57000.00 | 700.00 | 70000.00 | 57000.00 | Kiswel Kharbuli
20.00 | Wiring for circuit/ submain wiring with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required (e) 2x 6 sqmm + 1 x 6 sq.mm | 200.00 | Meter |  | 480.00 | 96000.00 | 500.00 | 100000.00 | 96000.00 | Kiswel Kharbuli
21.00 | Supplying and fixing of following sizes of steel conduit along with the accessories in surface /recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. (a) 20 mm Steel Conduit | 50.00 | Meter |  | 165.00 | 8250.00 | 200.00 | 10000.00 | 8250.00 | Kiswel Kharbuli
22.00 | Supplying and fixing of following sizes of steel conduit along with the accessories in surface /recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. (b) 25 mm Steel Conduit | 50.00 | Meter |  | 220.00 | 11000.00 | 215.00 | 10750.00 | 10750.00 | M/s S.T. Electricals
23.00 | Supplying and fixing suitable size GI box with modular plate and cover in Front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 30.00 | Each |  | 550.00 | 16500.00 | 690.00 | 20700.00 | 16500.00 | Kiswel Kharbuli
24.00 | Supplying and fixing 6 Module (200mmX75mm) modules, GI box along with modular base & cover plate for modular switches in recess etc as required. | 5.00 | Each |  | 380.00 | 1900.00 | 370.00 | 1850.00 | 1850.00 | M/s S.T. Electricals
25.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. a)15/16 A switch | 20.00 | Each |  | 165.00 | 3300.00 | 200.00 | 4000.00 | 3300.00 | Kiswel Kharbuli
26.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. b)3 pin 5/6 A socket outlet | 5.00 | Each |  | 165.00 | 825.00 | 200.00 | 1000.00 | 825.00 | Kiswel Kharbuli
27.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) (a) 4 way (8 + 12), Double door | 2.00 | Each |  | 3285.00 | 6570.00 | 4200.00 | 8400.00 | 6570.00 | Kiswel Kharbuli
28.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) (a) 4 way, Double door | 1.00 | Each |  | 1530.00 | 1530.00 | 1800.00 | 1800.00 | 1530.00 | Kiswel Kharbuli
29.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) (b) 8 way, Double door | 1.00 | Each |  | 1645.00 | 1645.00 | 2000.00 | 2000.00 | 1645.00 | Kiswel Kharbuli
30.00 | Supplying and fixing following ratings and following series, miniature circuit breaker/Isolator suitable for lighting and other loads of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required from Havells Eurobreaker or equivalent. (a) TPN C series MCB-63 Amp-Incomer | 2.00 | Each |  | 1970.00 | 3940.00 | 2600.00 | 5200.00 | 3940.00 | Kiswel Kharbuli
31.00 | Supplying and fixing following ratings and following series, miniature circuit breaker/Isolator suitable for lighting and other loads of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required from Havells Eurobreaker or equivalent. (b) SPN C series MCB-32 Amp-Incomer | 2.00 | Each |  | 1370.00 | 2740.00 | 1900.00 | 3800.00 | 2740.00 | Kiswel Kharbuli
32.00 | Supplying and fixing following ratings and following series, miniature circuit breaker/Isolator suitable for lighting and other loads of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required from Havells Eurobreaker or equivalent. (c ) C series SP MCB 6-32 A 240 V rating | 32.00 | Each |  | 275.00 | 8800.00 | 325.00 | 10400.00 | 8800.00 | Kiswel Kharbuli
33.00 | ITC of street light fitting including supplying and fixing of 32 mm dia X 2.00 metres long G.I. pipe (medium class) bracket for mounting of LED street light fitting on pole including bending the pipe to the required shape, with suitable clamping, painting with primer and finish paint etc. as required. | 20.00 | Each |  | 1150.00 | 23000.00 | 1950.00 | 39000.00 | 23000.00 | Kiswel Kharbuli
34.00 | Installation testing and commissioning of following fittings by fixing fasteners on ceiling /surface/recess by drilling holes, supplying and fixing chain/clamp for fixing of fitting including connection with 1.5 sqmm FRLS PVC insulated, copper conductor, single core cable and earthing etc. complete as reqd. | 50.00 | Each |  | 140.00 | 7000.00 | 210.00 | 10500.00 | 7000.00 | Kiswel Kharbuli
35.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc.as required. a) 150 mm width x 50 mm depth x 1.6 mm thickness. | 200.00 | Meter |  | 560.00 | 112000.00 | 750.00 | 150000.00 | 112000.00 | Kiswel Kharbuli
36.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. (a) Above 95 sq. mm and upto 185 sq. mm | 400.00 | Meter |  | 470.00 | 188000.00 | 620.00 | 248000.00 | 188000.00 | Kiswel Kharbuli
37.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. (b) upto 35 sq. mm | 500.00 | Meter |  | 525.00 | 262500.00 | 500.00 | 250000.00 | 250000.00 | M/s S.T. Electricals
38.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. (a)Above 95 sq. mm and upto 185 sq. mm | 400.00 | Meter |  | 50.00 | 20000.00 | 50.00 | 20000.00 | 20000.00 | Kiswel Kharbuli, M/s S.T. Electricals
39.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. (b)upto 35 sq. mm | 50.00 | Meter |  | 22.00 | 1100.00 | 25.00 | 1250.00 | 1100.00 | Kiswel Kharbuli
40.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. (a)upto 35 sq. mm | 50.00 | Meter |  | 33.00 | 1650.00 | 50.00 | 2500.00 | 1650.00 | Kiswel Kharbuli
41.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for 3½ X 150 sq. mm size of PVC insulated and PVC sheathed / XLPE conductor cable of 1.1 KV grade as required. | 2.00 | Each |  | 3065.00 | 6130.00 | 3595.00 | 7190.00 | 6130.00 | Kiswel Kharbuli
42.00 | Providing , fixing and laying of 100 mm dia G.I. pipe (medium class) in existing trench i/c threading and coupling etc as required. | 60.00 | Meter |  | 1100.00 | 66000.00 | 1850.00 | 111000.00 | 66000.00 | Kiswel Kharbuli
43.00 | Cutting the bituminous road / PCC surface upto 20 cm width and 50 cm depth manually or with help of suitable tools and plants and disposal of debris upto 50 mtr suitable and making good the road with cement concrete of mix 1:3:6 etc complete as required | 60.00 | Meter |  | 450.00 | 27000.00 | 600.00 | 36000.00 | 27000.00 | Kiswel Kharbuli
44.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 x 150 sq. mm. | 4.00 | Set |  | 650.00 | 2600.00 | 700.00 | 2800.00 | 2600.00 | Kiswel Kharbuli
45.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 x 35 sq. mm. | 4.00 | Set |  | 350.00 | 1400.00 | 400.00 | 1600.00 | 1400.00 | Kiswel Kharbuli
46.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 x 16 sq. mm. | 15.00 | Set |  | 300.00 | 4500.00 | 300.00 | 4500.00 | 4500.00 | Kiswel Kharbuli, M/s S.T. Electricals
47.00 | Design, Fabrication, Installation, Testing & Commissioning of out door Feeder Pillar, cubicle type, made out of 2 mm thick CRCA sheet with 100 x 50 mm channel base frame in the bottom, totally enclosed, IP 54, free standing dust and vermin proof, compartmentalised with front lockable double doors, suitable for operation on 3 phase, 415 V, 50Hz AC system with TPN busbars and internal control wiring of minimum 2.5 sqmm copper FRLS PVC insulated wires, interconnection, duly powder coated of approved shade with angle iron stand size 50mm x 50mm x 5mm and 75cm height, i/c digging & grounding with cement concrete base and brick pedestal with dimension (100cm*30cm*30cm-2nos)etc. as per specifications having following switchgears and accessories, and as approved by EIC, complete as required. Incomer i. MCCB, 4P, 200 A , 25 KA Breaking Capacity , with Ics=Icu*100% & Adjustable over load setting (0.8-1.0In)with spreader terminals and rotary handle with castell type lock Make :L&T Model :DU 125D or its equivalent ]- 2Nos. Buscoupler i. MCCB, 4P, 200 A , 25 KA Breaking Capacity , with Ics=Icu*100% & Adjustable over load setting (0.8-1.0In)with spreader terminals and rotary handle with castell type lock Make :L&T Model :DU 125D or its equivalent ]- 1Nos. ii. 250 A TPN bus bars of high conductivity electrolytic quality Aluminium alloy- 1 Set each. iii. MCB, FP 32 A , 10 KA Breaking Capacity, C Curve - 2 No. OUTGOING i. MCCB, FP 100 A , 10 KA Breaking Capacity, C Curve - 1 No. ii. MCCB, FP 63 A , 10 KA Breaking Capacity, C Curve - 3 No. iii. MCB, FP 32 A , 10 KA Breaking Capacity, C Curve - 4 No. iv. MCB, FP 16 A , 10 KA Breaking Capacity, C Curve - 4 No. v. 3Phase LED Voltmeter [ Make: L&T, model WL132010OOOO or its equivalent] -2 sets vi. 3Phase Digital Ammeter with inbuilt selector switch along with 3 nos. CT's - 100/5 Amp, for incomers [ Make: L&T, model WL131010OOOO or its equivalent ] -2 set | 1.00 | Each |  | 235000.00 | 235000.00 | 226800.00 | 226800.00 | 226800.00 | M/s S.T. Electricals
48.00 | SITC of flood light mast made up of 100 mm dia GI pole of 6 mtrs, with suitable bracket arrangement with supports for installation of 3 nos. of 180 watt LED flood lights, including necessary provision for taking in/out the cable, required foundation arrangement with MS base plate 300mmx300mmx5mm welding at bottom of pole, painting on the pole etc. required as per site. | 6.00 | Each |  | 21900.00 | 131400.00 | 23000.00 | 138000.00 | 131400.00 | Kiswel Kharbuli
49.00 | SITC of light mast made up of 65 mm dia GI pole of 3 mtrs, with suitable bracket arrangement with supports for installation of lantern type LED flood lights, including necessary provision for taking in/out the cable, required foundation arrangement with MS base plate 300mmx300mmx5mm welding at bottom of pole, painting on the pole etc. required as per site. | 8.00 | Each |  | 18600.00 | 148800.00 | 20000.00 | 160000.00 | 148800.00 | Kiswel Kharbuli
50.00 | Supply and fixing of side hinged-door fixed with base SMC junction Box of size 250 x 200 x 105mm (Loop-in-Loop-out Box) on the GI pole with suitable size MS clamp including providing & fixing 63A, 4Pole connector for loop in & loop out to terminate 2Nos, 4 core 16 sq. mm. armoured aluminium cable, 6Amp SP MCB in din rail, Interconnection etc. as required.(make: Sintex: model no. JS-JB-2520 or its equivalent) | 14.00 | Each |  | 1300.00 | 18200.00 | 1400.00 | 19600.00 | 18200.00 | Kiswel Kharbuli
51.00 | Supply and fixing of side hinged-door fixed with base SMC junction Box of size 325 x 220 x 150mm (Double Door Hinged) (Loop-in-Loop-out Box) on the GI pole with suitable size MS clamp including providing & fixing 63A, 4Pole connector for loop in & loop out to terminate 2Nos, 4 core 16 sq. mm. armoured aluminium cable, & 5 no,s 16 Amp SP MCB in din rail, Interconnection etc. as required.(make: Sintex: model no. JS-JB-3726 or its equivalent) | 1.00 | Each |  | 2400.00 | 2400.00 | 2600.00 | 2600.00 | 2400.00 | Kiswel Kharbuli
52.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set |  | 11000.00 | 22000.00 | 12000.00 | 24000.00 | 22000.00 | Kiswel Kharbuli
53.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtr |  | 1200.00 | 24000.00 | 1500.00 | 30000.00 | 24000.00 | Kiswel Kharbuli
54.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | Mtr |  | 930.00 | 18600.00 | 1100.00 | 22000.00 | 18600.00 | Kiswel Kharbuli
| Total in Figures |  |  |  |  | 3825190.00 |  | 4011635.00
Lowest Amount Quoted BY: Kiswel Kharbuli(3825190.00)

## BOQ Summary
BOQ Summary Details Tender Title: C/o Community Hall-Electrical Works Tender ID: 2020_AAI_55042_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Kiswel Kharbuli | 3825190.00 | L1
| 2 | M/s S.T. Electricals | 4011635.00 | L2