## BoQ1
Government eProcurement System Created By: SONAM NURBOO Created Date/Time: 30-Sep-2020 04:45 PM Tender Title: Construction of New DVOR at Leh Airport. SH SITC of 30KVA DG, Servo Stabilizer, Split AC, Fire Alarm System and other Electrical Works Tender ID: 2020_AAI_55467_1
Tender Inviting Authority: Asst GM Engg.(Electrical)-I, AAI,KBR Airport ,Leh
Name of work:- Construction of New DVOR at Leh Airport . SH: SITC of 30KVA DG,Servo Stablizer, Split AC ,Fire Alarm System and other Electrical Works
Tender ID: 2020_AAI_55467_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | National Engineering(GSTN-01AJFPM5466Q1ZS) |  | Anzen Projects Private Limited(GSTN-06AANCA5052C1ZZ)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH:-I ( MV feeder pillar panel) Supply, Installation, Testing and Commissioning of cubicle type LT panel suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply system, IP 42 ..........(For Details please refer SOQ in Tender Document.) Incomer: 63A, 36KA, 4P MCCB with Microprocessor based releases as incomer with R,Y,B,ON,OFF, Trip indication lamps, resin cast CT's with multifuction meter ( Schheider EM 6459 or Equivalent)-2 sets. Buscoupler: 63A, 36KA, 4P MCCB with Microprocessor based releases as buscoupler with R,Y,B, ON, OFF and three locks two key mechanical interlock- 1 set Outgoing: 40A, 36KA, 4P MCCB with microprocessor based releases with ON, OFF, Trip indication lamps as outgoing with digital ammeter and surge protection Device (class C, Type-2) - 4 sets. Spare compartment: suitable for providing 40 A 4P MCCB with all necessary arrangements etc complete as required - 2 Nos. Primary surge protection: Supply, installation, Testing & commissioning of Block MOV based surge Divertor (BMOVSD) 100 KA, 3 phase, 4 wire class-B, Qty-1 Secondary protection: Supply, Installation, Testing & commissioning of Block MOV based surge divertor 40KA, 3 phase, 4 wire class-B, Qty-1. h) With all necessary accessories including DSITC of suitable isolating switch gear of appropriate rating for surge protectors etc, complete as required | 1.00 | Job | 0.00 | 300000.00 | 300000.00 | 682000.00 | 682000.00 | 300000.00 | National Engineering
2.00 | Supply installation , testing & commissioning of Class 2 (Type -2) low voltage 3P+N SPDs with protection against overload currents and short-circuit currents SPDs compliant with Uc=275V,and In=20KA/pole suitable For 230V power networks (50 Hz) | 2.00 | Each | 0.00 | 10000.00 | 20000.00 | 14807.50 | 29615.00 | 20000.00 | National Engineering
3.00 | SH:-II (A/C and Heating System ) Supply installation, testing & commissioning of 1.5 TR Inverter Type air cooled split air conditioning unit of 5 star rating with R-410A refrigerant consist of outdoor unit, indoor unit. Wireless remote control. The outdoor unit shall comprise of rotary/reciprocating compressor, refrigerant should be CFC free, aircooled condenser, fan, fan motor, with corded remote controller, electrical accessories & suitable stand of MS angle iron painted for installation of outdoor unit. The indoor unitr shall be Hi-wall type complete with cooling coil, drain pan, washable pre-filter, first chargeor refrigerant complete as required & as specified. | 3.00 | Each | 0.00 | 55000.00 | 165000.00 | 45700.00 | 137100.00 | 137100.00 | Anzen Projects Private Limited
4.00 | Dismantling of 1 Nos 1.5 Ton Split Type Air Conditioning unit including indoor unit,outdoor unit with stand and shifting and installation at new location i/c refilling of refrigerant gas and commissioning as per direction of Engineering incharge | 1.00 | Each | 0.00 | 8000.00 | 8000.00 | 2250.00 | 2250.00 | 2250.00 | Anzen Projects Private Limited
5.00 | Supply of 4 KVA Voltage stabilizer wall mounting type suitable for 1.5 ton split / window A/C units with input volt range 170V to 270 V & output 220 +10% etc., as required) | 3.00 | Each | 0.00 | 6000.00 | 18000.00 | 2500.00 | 7500.00 | 7500.00 | Anzen Projects Private Limited
6.00 | Supply of oil-filled radiator type Room heater with 11 fins, 2900 watts rating ,Thermostatic heat control PTC Fan ,Castor wheel for easy mobility ,Thermostat, Manual thermal cutout, Auto Thermal Cutout, Safety tilt switch to safeguard against improper installation sutable for operaton on 240V 50 HZ supply | 15.00 | Each | 0.00 | 22000.00 | 330000.00 | 11500.00 | 172500.00 | 172500.00 | Anzen Projects Private Limited
7.00 | SH:III(Fire Alarm System ) Supply, installation, testing and commissioning of UL/EN listed Intelligent Addressable Photo Elecrtic Smoke Detector with mounting based LED with Electronic Addressing Feature to programme the detectors. Complete as required to be installed under/above false ceiling, roof and concealed space, etc. interconnecting to loop cable complete as required. ( To be executed through specialized agency only after due approval of Engineer In-Charge) . | 8.00 | Each | 0.00 | 2500.00 | 20000.00 | 2950.00 | 23600.00 | 20000.00 | National Engineering
8.00 | Supply, installation, testing and commissioning of UL /EN listed intelligent Electronic Addressable type Heat Detector (Fixed cum-rate of rise type) with fixed temperature range upto 57 degree Census complete with all fixing accessories like base, base box, self adhesive sticker indicating loop number and address etc. to be installed under/above false ceiling, roof and concealed space, etc. interconnecting to loop cable complete as required. ( To be executed through specialized agency only after due approval of Engineer In-Charge) . | 1.00 | Each | 0.00 | 2500.00 | 2500.00 | 3200.00 | 3200.00 | 2500.00 | National Engineering
9.00 | Supply, installation, testing and commissioning of UL/EN listed Addressable type Manual Call Point (break glass type) complete with Input Module, push button, enclosed in box with provision for cable or conduit coupling, self adhesive sticker indicating loop number and address.The unit to be painted fire red outside, white inside and written 'In case of fire break glass. ( To be executed through specialized agency only after due approval of Engineer In-Charge) . | 1.00 | Each | 0.00 | 3500.00 | 3500.00 | 1550.00 | 1550.00 | 1550.00 | Anzen Projects Private Limited
10.00 | Supplying, installation, testing & commissioning of Response Indicator (METAL CLADE) which consists of steady glowing LED. This LED shall be mounted within a M.S. box and connected in parallel to the built in indicator of the detector as per specifications. The RI shall come "ON" as soon as the detector activates complete in all respects as per specification. ( To be executed through specialized agency only after due approval of Engineer In-Charge) . | 4.00 | Each | 0.00 | 140.00 | 560.00 | 275.00 | 1100.00 | 560.00 | National Engineering
11.00 | Supply, installation, testing and commissioning of UL/EN listed Hooter cum Strobe with control module interconnecting to loop cable complete as required. The strobes shall be synchronized for better evacuation as per specification complete as required. ( To be executed through specialized agency only after due approval of Engineer In-Charge) . | 1.00 | Each | 0.00 | 6500.00 | 6500.00 | 2500.00 | 2500.00 | 2500.00 | Anzen Projects Private Limited
12.00 | Supply, installation, testing & commissioning of UL /EN listed Fault Isolator Module as per specifications complete as required. ( To be executed through specialized agency only after due approval of Engineer In-Charge) . | 1.00 | Each | 0.00 | 3000.00 | 3000.00 | 3200.00 | 3200.00 | 3000.00 | National Engineering
13.00 | Supply, Installation, Testing & Commissioning of Microprocessor based 02 loop intellegent analogue Addressable Type UL/EN listed Fire Alarm Control Panel, with LCD display ,The panel should be equiped of Sufficiant number of loops with loop capacity to take 125+125 intellegent addressable detectors/ devices in one loop for connecting smoke detectors, manual call points, Hooters etc suitable for operation on 220 Volts, 50 Hz AC power supply, LED indicators to indicate fire and normal operation & power supply status, push button for accept and Reset, maintenance free batteries with minimum 1 hour backup on alarm mode & 8 hours on normal operation mode with battery charger etc., shall be complete as required. Panel shall have necessary provision for connecting and functioning with auto dialer etc as required. ( To be executed through specialized agency only after due approval of Engineer In-Charge) . | 1.00 | Each | 0.00 | 105000.00 | 105000.00 | 150000.00 | 150000.00 | 105000.00 | National Engineering
14.00 | Supply, installation, testing and commissioning of auto dialer with all necessary accessories including connections, modules if any required for integrating with Addressable Fire Alarm Panels etc complete as required.( To be executed through specialized agency only after due approval of Engineer In-Charge) . | 1.00 | Each | 0.00 | 9500.00 | 9500.00 | 25000.00 | 25000.00 | 9500.00 | National Engineering
15.00 | Supply and drawing of 2X1.5 Sq.mm. FRLS XLPE insulated PVC sheathed, stranded copper conductor armoured cable 1100 V grade as per IS 7098(part 1)1988, amended upto date complete as required. ( To be executed through specialized agency only after due approval of Engineer In-Charge) . | 100.00 | Meter | 0.00 | 42.00 | 4200.00 | 55.00 | 5500.00 | 4200.00 | National Engineering
16.00 | SITC of ABC ( Powder Type) SQUEEZE GRIP CARTRIDGE TYPE 6kg fire extinguisher with Mild Steel Cylinders ISI marked fully charged with ABC MAP 90 powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspension bracket complete and conforming to IS:15683 as required and as per specifications including all mounting accessories | 5.00 | Each | 0.00 | 3000.00 | 15000.00 | 1800.00 | 9000.00 | 9000.00 | Anzen Projects Private Limited
17.00 | Supply, installation, testing and commissioning ISI marked (IS:15683) Fire Extinguisher, Carbon-di-oxide type capacity 9Kg trolley mounted . Flat base including valve, discharge hose of not less than 10 mm dia, 1M long and complete in all respects including initial fill with CO2 gas conforming to IS:307-1966 complete as required & as per specifications. | 3.00 | Each | 0.00 | 13500.00 | 40500.00 | 8000.00 | 24000.00 | 24000.00 | Anzen Projects Private Limited
18.00 | Supply of Red colour Fire bucket with MS Iron Stand having four Fire bucket made of stainless steel metal | 2.00 | Sets | 0.00 | 5000.00 | 10000.00 | 2500.00 | 5000.00 | 5000.00 | Anzen Projects Private Limited
19.00 | Supply of Medium First Aid Kit suitable for office/Industries as per India Red Cross society containing atleast item mentioned in Specification sheet. | 2.00 | Each | 0.00 | 3500.00 | 7000.00 | 3000.00 | 6000.00 | 6000.00 | Anzen Projects Private Limited
20.00 | SH:-4 (LT CABLE Supply Laying & End Termination) Supply of following size of 1.1kv grade multicore aluminium conductor XLPE insulated and PVC sheathed armoured cable as per IS: 7098:1988 (Part - I) with upto date amendments. 3.5 core, 35 Sq.mm. | 360.00 | Meter | 0.00 | 225.00 | 81000.00 | 120.00 | 43200.00 | 43200.00 | Anzen Projects Private Limited
21.00 | Laying of One number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing DWC HDPE pipe as required. Upto 35 sq. mm | 290.00 | Meter |  | 42.00 | 12180.00 | 45.00 | 13050.00 | 12180.00 | National Engineering
22.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 50.00 | Meter |  | 50.00 | 2500.00 | 40.00 | 2000.00 | 2000.00 | Anzen Projects Private Limited
23.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 120.00 | Meter |  | 55.00 | 6600.00 | 40.00 | 4800.00 | 4800.00 | Anzen Projects Private Limited
24.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc.conforming to IS 16205 Part 24 complete with fitting(couplers and 'O' rings ) and cutting,jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 140.00 | Meter |  | 480.00 | 67200.00 | 184.00 | 25760.00 | 25760.00 | Anzen Projects Private Limited
25.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc.conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 130.00 | Meter |  | 240.00 | 31200.00 | 140.00 | 18200.00 | 18200.00 | Anzen Projects Private Limited
26.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required 3½ X 35 sq. mm (32mm) | 18.00 | Sets |  | 580.00 | 10440.00 | 450.00 | 8100.00 | 8100.00 | Anzen Projects Private Limited
27.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 15.00 | Each |  | 580.00 | 8700.00 | 600.00 | 9000.00 | 8700.00 | National Engineering
28.00 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 35 sq. mm | 2.00 | Each |  | 300.00 | 600.00 | 2208.10 | 4416.20 | 600.00 | National Engineering
29.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc.as required. 150 mm width X 50 mm depth X 1.6 mm thickness | 30.00 | Meter |  | 780.00 | 23400.00 | 270.00 | 8100.00 | 8100.00 | Anzen Projects Private Limited
30.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. 150 mm width X 50 mm depth X 1.6 mm thickness | 5.00 | Each |  | 300.00 | 1500.00 | 925.00 | 4625.00 | 1500.00 | National Engineering
31.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "Tee" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. 150 mm width X 50 mm depth X 1.6 mm thickness | 3.00 | Each |  | 300.00 | 900.00 | 925.00 | 2775.00 | 900.00 | National Engineering
32.00 | SH:-5 (DG Set ,AMF and Servo Stablizer) Providing, Installing, Testing and Commissioning of Silent Type diesel generating set alongwith having prime power rating of 30 KVA, 415 Volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz., 3-Phase system and for 0.85 Load factor and consisting of the followings : A) Diesel Engine :Diesel Engine 4 Stroke water cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at NTP conditions and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted completed with all the required accessories. B) Engine mounted Instrument Panel fitted with and having digital display for following : i) Start-Sop switch with key. ii) Water temperature indication iii).Lubrication oil ......(For Details please refer SOQ in Tender Document.) C) Alternator :Synchronous, alternator rated at 30KVA, 415 Volts at 1500 RPM, 3-Phase 50 Hz., AC Supply with 0.8 lagging power factor at NTP condition. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR conforming to IS: 4772/BS 2613 suitable for tropical conditions and with class-F/H insulation. D) Base Frame & Foundation : Both the engine and alternator shall be mounted on suitable base frame made of MS channel.........(For Details please refer SOQ in Tender Document.) | 2.00 | Job |  | 450000.00 | 900000.00 | 350000.00 | 700000.00 | 700000.00 | Anzen Projects Private Limited
33.00 | Fabricating, Installing, Testing and commissioning of automatic mains failure control Panel made up of 2 mm thick CRCA sheet duly powder coated including auto by pass panel suitable for 30KVA silent type DG set complete with relays, timers, set of CTs for metering and protection and energy analyser to indicate currents, phase and line voltages, frequency, power factor, KWH, KVARH & provision for overload, short circuit, restricted earth fault, under frequency, control cabling from AMF panel to diesel engine and elsewhere, if required all complete and inter locking including the following : a)2 Nos. 63 Amp., 4 Pole power contactor with required auxilary contacts. b) Auto/Manual/Test/Off Selector switch. c) Auto Mains Failure Relay EC-2 make C&S or equivalent d)................(For Details please refer SOQ in Tender Document.) | 2.00 | Job |  | 70000.00 | 140000.00 | 97000.00 | 194000.00 | 140000.00 | National Engineering
34.00 | Supplying and fixing exhaust gas piping of suitable dia welded black M.S. 'B' class pipe 2.5 inch (65mm) conforming to IS:1239 cut to required lengths and installed with necessary bends, supports and clamps, anti-vibration mountings, insulation of exhaust system with mineral wool/Rockwool, 50 mm thick wiremesh and aluminium cladding etc. as required as per specifications. | 12.00 | Meter |  | 600.00 | 7200.00 | 500.00 | 6000.00 | 6000.00 | Anzen Projects Private Limited
35.00 | Dismantling , Transportation and Shifting of 25 KVA make DG sets from existing location to AAI Stor as directed by the E-I-C with all acessories AMF Panel, Power cable, Diesel Tank and pipe lines, Exaust pipe lines etc complete as required. | 2.00 | Job |  | 5000.00 | 10000.00 | 8000.00 | 16000.00 | 10000.00 | National Engineering
36.00 | Supply Installation testing and commissioning of 25 KVA output, 3 phase, natural Air cooled and unbalanced type Servo controlled voltage Stabilizer having input voltage range 360-460 V and out put voltage 415±1% at frequency 50 HZ with a efficeny of >98% having input and output digital Voltmeter with seclector switch and digital ammeter with seclector switch, with over and under voltage tripping and inbuilt bypass & MCCB and other specification mentioned in Specification sheet. | 1.00 | Job |  | 80000.00 | 80000.00 | 57000.00 | 57000.00 | 57000.00 | Anzen Projects Private Limited
37.00 | Dismantling and Shifting of 1 no 20 KVA Servo Stablizer from existing location to AAI Store as directed by the E-I-C with all acessories Power cable etc complete al as required. | 1.00 | Job |  | 5000.00 | 5000.00 | 2000.00 | 2000.00 | 2000.00 | Anzen Projects Private Limited
38.00 | SITC of 63A ,4 pole Onload Changeover Switches with spreaser links, Terminal Shrouds, Source Separator and PhaseBarriers and Sheet steel enclosure as per OEM recommendation | 1.00 | Job |  | 8500.00 | 8500.00 | 5675.00 | 5675.00 | 5675.00 | Anzen Projects Private Limited
39.00 | S.H.6 : EARTHING : Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure withcover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 7.00 | Sets |  | 7000.00 | 49000.00 | 6000.00 | 42000.00 | 42000.00 | Anzen Projects Private Limited
40.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut,bolt, spring, washer excavation and re-filling etc. as required. | 40.00 | Meter |  | 650.00 | 26000.00 | 394.00 | 15760.00 | 15760.00 | Anzen Projects Private Limited
41.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/terminating with G.I. nut, bolt, spring, washer etc. as required.(Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 35.00 | Meter |  | 200.00 | 7000.00 | 158.00 | 5530.00 | 5530.00 | Anzen Projects Private Limited
42.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 26.00 | Meter |  | 100.00 | 2600.00 | 123.00 | 3198.00 | 2600.00 | National Engineering
43.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosurewith cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 3.00 | Sets |  | 16000.00 | 48000.00 | 8000.00 | 24000.00 | 24000.00 | Anzen Projects Private Limited
44.00 | Providing and fixing 25 mm x 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode with connection with brass nuts bolts, spring washer etc complete all as required | 20.00 | Meter |  | 800.00 | 16000.00 | 800.00 | 16000.00 | 16000.00 | National Engineering, Anzen Projects Private Limited
45.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | Meter |  | 500.00 | 10000.00 | 500.00 | 10000.00 | 10000.00 | National Engineering, Anzen Projects Private Limited
46.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/terminating with nut, bolt, spring, washer etc. as required.(Jointing shall be done by overlapping and with 2 sets of brass | 15.00 | Meter | 0.00 | 650.00 | 9750.00 | 500.00 | 7500.00 | 7500.00 | Anzen Projects Private Limited
47.00 | SITC of 1mtr Wide 2.00 mm thick Class A synthetic insulation mat suitable for 0-3.3KV Voltage grade confirming to IS 15652:2006 and fixing the same with appropriate adhesive etc complete all as required | 15.00 | Meter | 0.00 | 900.00 | 13500.00 | 300.00 | 4500.00 | 4500.00 | Anzen Projects Private Limited
| Total in Figures |  |  |  |  | 2647030.00 |  | 2543804.20
Lowest Amount Quoted BY: Anzen Projects Private Limited(2543804.20)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New DVOR at Leh Airport. SH SITC of 30KVA DG, Servo Stabilizer, Split AC, Fire Alarm System and other Electrical Works Tender ID: 2020_AAI_55467_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Anzen Projects Private Limited | 2543804.20 | L1
| 2 | National Engineering | 2647030.00 | L2