## BoQ1
Government eProcurement System Created By: Pankaj Wanjari Created Date/Time: 01-Oct-2020 11:57 AM Tender Title: Provision of UPS system for GLF installations at Birsi Airport Gondia Tender ID: 2020_AAI_56666_1
Tender Inviting Authority: < AGM (Engg-Elect), AAI, Birsi Airport, Gondia>
Name of Work: < Provision of UPS system for GLF installations at Birsi Airport, Gondia >
Contract No: <2020_AAI_56666_1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Novateur Electrical and Digital Systems Private Limited(GSTN-33AACCE4671N1ZF) |  | Weartech Engineers Pvt Ltd(GSTN-23AABCW1561C1ZV) |  | RVD INFRA SOLUTION PVT.LTD.(GSTN-24AAGCR7767L1ZQ) |  | Aviosat Technology Pvt Ltd(GSTN-06AAKCA3377P1Z3) |  | RS Power Systems Pvt. Ltd.(GSTN-08AAICR2572F1ZA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and Commissioning of true online UPS with minimum 160 KVA capacity, 3 phase in and 3 Phase out with double conversion PWM IGBT technology, in built isolation transformer suitable to drive constant current regulators with 100% unbalanced load at output at full load condition as per technical specifications/data sheet enclosed. The UPS shall have standard features like in built automatic 100% rated static by pass, maintenance by pass, active input power factor correction, phase sequence corrector, pure sine wave output, input-output isolation, compatibility with generator supply, cold start capability, EMI/RFI noise filter, advanced communication-RS485 port, user friendly LCD display, provision of auto load sharing / parallel operation, suitable to operate at 415V, 50Hz, 3 Phase AC supply and delivering 2 phase & single phase loads with 3 phase output of the UPS and necessary safety protection. The job also includes supply and connecting the suitable required number of 12V, SMF batteries of suitable amp hour, for each UPS separately/Individually to give a backup time of minimum 30 minutes for each UPS separately/Individually at the rated full load along with battery management feature integrated with UPS, battery rack, connectors, wiring, cabling between battery bank and UPS with insulated copper conductor of required size, termination as per site condition etc. complete as required. | 2.00 | Job |  | 1648000.00 | 3296000.00 | 1975000.00 | 3950000.00 | 2160000.00 | 4320000.00 | 2100000.00 | 4200000.00 | 2715200.00 | 5430400.00 | 3296000.00 | Novateur Electrical and Digital Systems Private Limited
2.00 | Design, fabricate, supply, installation, testing and commissioning of indoor compartmentalized type Panel for UPS, having panel of suitable size, bus bars with SMC/DMC supports, made of 14 SWG CRCA sheet steel, totally enclosed, IP-42, free standing, floor / wall mounting, powder coated painting, suitable to the existing space, operation on 3 phase and neutral, 415V, 50 Hz AC system with bus bars, G.I flat Earth strip on both side , Removable gland plates at bottom with suitable size of predrilled holes for cables, cable interconnections, wiring, earthing, rotary handles & spreader links to all MCCBs, powder coated painting etc. with following items and installation on suitable channels /elevated concrete foundation as per site requirement/ directions of E-I-C. INCOMER MCCB of 400 Amps, 35 kA, 4 pole, microprocessor based release with Rotary operating mechanism, shunt trip, auxiliary contact etc. - 04 Nos. 96 Sqmm Digital Multifunction Meter with RS485 port long with MCB & CTs of suitable ratings - 04 Sets. Indication Lamps, (LED type for R, Y & B) - 04 Sets BUSBAR One set of 400 Amp. TPN aluminium bus bars of suitable rupturing capacity. OUTGOING MCCB of 400 Amps, 35 kA, 4 pole, microprocessor based release with Rotary operating mechanism, shunt trip, auxiliary contact etc. - 01 Nos. 96 Sqmm Digital Multifunction Meter with RS485 port long with MCB & CTs of suitable ratings - 01 Sets. Indication Lamps, (LED type for R, Y & B) - 01 Sets | 1.00 | Each |  | 401100.00 | 401100.00 | 240000.00 | 240000.00 | 1020000.00 | 1020000.00 | 420000.00 | 420000.00 | 400000.00 | 400000.00 | 240000.00 | Weartech Engineers Pvt Ltd
3.00 | Supply of 3.5 Core x 300 Sqmm size XLPE insulated PVC sheathed, aluminium conductor, armoured, power cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 amended upto date. | 450.00 | Mtrs |  | 1145.00 | 515250.00 | 820.00 | 369000.00 | 780.00 | 351000.00 | 150.00 | 67500.00 | 950.00 | 427500.00 | 67500.00 | Aviosat Technology Pvt Ltd
4.00 | Supply and installation of 300 mm width X 62.5 mm depth X 2.0 mm thickness size perforated Hot Dipped Galvanised Iron cable tray cable tray (Galvanisation thikness not less than 50 micron) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts etc as required. | 60.00 | Mtrs |  | 1155.00 | 69300.00 | 700.00 | 42000.00 | 1260.00 | 75600.00 | 520.00 | 31200.00 | 1150.00 | 69000.00 | 31200.00 | Aviosat Technology Pvt Ltd
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size above 185 sq. mm and upto 400 sq. mm in the existing RCC/HUME/METAL pipe as required. | 320.00 | Mtrs |  | 200.00 | 64000.00 | 150.00 | 48000.00 | 60.00 | 19200.00 | 450.00 | 144000.00 | 220.00 | 70400.00 | 19200.00 | RVD INFRA SOLUTION PVT.LTD.
6.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size above 185 sq. mm and upto 400 sq. mm in the existing masonry open duct as required. | 20.00 | Mtrs |  | 179.00 | 3580.00 | 200.00 | 4000.00 | 72.00 | 1440.00 | 430.00 | 8600.00 | 220.00 | 4400.00 | 1440.00 | RVD INFRA SOLUTION PVT.LTD.
7.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size above 185 sq. mm and upto 400 sq. mm on wall surface (clamped with 40x3mm MS flat clamp) as required. | 10.00 | Mtrs |  | 200.00 | 2000.00 | 200.00 | 2000.00 | 48.00 | 480.00 | 490.00 | 4900.00 | 180.00 | 1800.00 | 480.00 | RVD INFRA SOLUTION PVT.LTD.
8.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size above 185 sq. mm and upto 400 sq. mm on cable tray (clamped with 40x3mm MS flat clamp) as required. | 90.00 | Mtrs |  | 210.00 | 18900.00 | 150.00 | 13500.00 | 108.00 | 9720.00 | 490.00 | 44100.00 | 180.00 | 16200.00 | 9720.00 | RVD INFRA SOLUTION PVT.LTD.
9.00 | Supply and making end termination with brass compression gland and aluminium and/copper lugs as per cable for 3.5 Core x 300 Sqmm size PVC insulated PVC sheathed aluminium conductor cable of 1.1 KV grade complete as required. | 11.00 | Each |  | 1890.00 | 20790.00 | 1100.00 | 12100.00 | 1200.00 | 13200.00 | 2200.00 | 24200.00 | 250.00 | 2750.00 | 2750.00 | RS Power Systems Pvt. Ltd.
10.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for 3.5 Core x 300 Sqmm size PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 1.00 | Each |  | 9975.00 | 9975.00 | 10000.00 | 10000.00 | 10800.00 | 10800.00 | 80000.00 | 80000.00 | 9500.00 | 9500.00 | 9500.00 | RS Power Systems Pvt. Ltd.
11.00 | Supply, Installation, Testing & Commissioning of earth pits & chemical earth material using ISOGEL earth enhanced compound of 20kgs, ISOROD advanced chemical earth rod made with k type copper tube of 2.5" dia, 8 fts long, 1.6 mm thick installed vertically complete with flanges bends top cover heavy duty plastic inspection chamber including excavation and refilling etc as required. | 2.00 | Set |  | 36750.00 | 73500.00 | 17500.00 | 35000.00 | 12000.00 | 24000.00 | 80000.00 | 160000.00 | 9500.00 | 19000.00 | 19000.00 | RS Power Systems Pvt. Ltd.
12.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia medium class G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 10.00 | Mtrs |  | 1785.00 | 17850.00 | 900.00 | 9000.00 | 1260.00 | 12600.00 | 950.00 | 9500.00 | 200.00 | 2000.00 | 2000.00 | RS Power Systems Pvt. Ltd.
13.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 10.00 | Mtrs |  | 971.00 | 9710.00 | 900.00 | 9000.00 | 1440.00 | 14400.00 | 900.00 | 9000.00 | 200.00 | 2000.00 | 2000.00 | RS Power Systems Pvt. Ltd.
14.00 | Supply of 1 Core x 70 Sqmm size XLPE insulated PVC sheathed, stranded copper conductor, unarmoured power cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 amended upto date. | 100.00 | Mtrs |  | 604.00 | 60400.00 | 700.00 | 70000.00 | 600.00 | 60000.00 | 850.00 | 85000.00 | 525.00 | 52500.00 | 52500.00 | RS Power Systems Pvt. Ltd.
15.00 | Supply of 1 Core x 120 Sqmm size XLPE insulated PVC sheathed, stranded copper conductor, unarmoured power cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 amended upto date. | 300.00 | Mtrs |  | 1066.00 | 319800.00 | 950.00 | 285000.00 | 1020.00 | 306000.00 | 1600.00 | 480000.00 | 850.00 | 255000.00 | 255000.00 | RS Power Systems Pvt. Ltd.
16.00 | Supply of 2 TR capacity BEE 5 Star rated wall mounted inverter type split air-conditioner unit fitted with high EER rotary compressors operating on refrigerant R-410A suitable for operation on 230V, 50 Hz, Single phase, AC supply complete with suitable filter, drain & refrigerant pipe with insulation & electrical connection with 3/4 core flexible copper cable complete as required. (Note: cost of drain (UPVC), refrigerant piping with insulation and electrical cable all upto 3 mtr length is included with this item). | 3.00 | Each |  | 60375.00 | 181125.00 | 50000.00 | 150000.00 | 66000.00 | 198000.00 | 75000.00 | 225000.00 | 50000.00 | 150000.00 | 150000.00 | Weartech Engineers Pvt Ltd, RS Power Systems Pvt. Ltd.
17.00 | Installation, testing and commissioning of for 1.5 / 2 TR split type air-conditioner (Indoor & Outdoor unit) i/c Copper piping work, providing suitable MS/GI stand for outdoor unit, complete with wall cutting, hole cutting, plastering etc. complete as required. | 3.00 | Job |  | 4200.00 | 12600.00 | 5000.00 | 15000.00 | 3600.00 | 10800.00 | 12000.00 | 36000.00 | 8000.00 | 24000.00 | 10800.00 | RVD INFRA SOLUTION PVT.LTD.
18.00 | Supply and Fixing of copper piping (suction & discharge line) including suitable insulation with nitrile rubber and 3/4 core flexible copper cable suitable for 1.5 / 2 TR Split air-conditioning unit including brazing, clamping, chipping and minor civil work complete with all accessories as required. | 45.00 | Mtrs |  | 998.00 | 44910.00 | 350.00 | 15750.00 | 1440.00 | 64800.00 | 1900.00 | 85500.00 | 300.00 | 13500.00 | 13500.00 | RS Power Systems Pvt. Ltd.
19.00 | Supply and fixing of rigid UPVC / flexible drain pipe of 25 mm dia. Including suitable insulation complete with all fittings, U straps, clamps etc. | 45.00 | Mtrs |  | 210.00 | 9450.00 | 50.00 | 2250.00 | 36.00 | 1620.00 | 250.00 | 11250.00 | 60.00 | 2700.00 | 1620.00 | RVD INFRA SOLUTION PVT.LTD.
20.00 | Supply Installation, testing and commissioning of smart controller / Timer for automatic changing operation (4 hr / 8 hr duration) suitable for 1.5 / 2 TR split air-conditioning units and having OV & UV indication / protection complete as required. | 1.00 | Each |  | 9450.00 | 9450.00 | 5000.00 | 5000.00 | 14400.00 | 14400.00 | 15000.00 | 15000.00 | 6000.00 | 6000.00 | 5000.00 | Weartech Engineers Pvt Ltd
21.00 | Supplying and fixing of CPRI / ERDA approved insulated synthetic sheet / insulation polymer mat of size 2.5 mm +/-10% thick suitable for Class-B up to 11 KV and conforming to IS15652:2006 alongwith suitable adheshive . | 20.00 | SqM |  | 1890.00 | 37800.00 | 1700.00 | 34000.00 | 600.00 | 12000.00 | 1500.00 | 30000.00 | 750.00 | 15000.00 | 12000.00 | RVD INFRA SOLUTION PVT.LTD.
22.00 | Comprehensive maintenance contract of UPS at Birsi Airport, Gondia after completion of Two (02) year defect liability period. (Excluding batteries) FOR 3rd YEAR | 1.00 | Per Year |  | 66000.00 | 66000.00 | 100000.00 | 100000.00 | 120000.00 | 120000.00 | 125000.00 | 125000.00 | 300000.00 | 300000.00 | 66000.00 | Novateur Electrical and Digital Systems Private Limited
23.00 | Comprehensive maintenance contract of UPS at Birsi Airport, Gondia after completion of Two (02) year defect liability period. (Excluding batteries) FOR 4th YEAR | 1.00 | Per Year |  | 69960.00 | 69960.00 | 200000.00 | 200000.00 | 132000.00 | 132000.00 | 125000.00 | 125000.00 | 350000.00 | 350000.00 | 69960.00 | Novateur Electrical and Digital Systems Private Limited
24.00 | Comprehensive maintenance contract of UPS at Birsi Airport, Gondia after completion of Two (02) year defect liability period. (Excluding batteries) FOR 5th YEAR | 1.00 | Per Year |  | 74158.00 | 74158.00 | 220000.00 | 220000.00 | 144000.00 | 144000.00 | 125000.00 | 125000.00 | 400000.00 | 400000.00 | 74158.00 | Novateur Electrical and Digital Systems Private Limited
25.00 | Comprehensive maintenance contract of UPS at Birsi Airport, Gondia after completion of Two (02) year defect liability period. (Excluding batteries) FOR 6th YEAR | 1.00 | Per Year |  | 78607.00 | 78607.00 | 235000.00 | 235000.00 | 168000.00 | 168000.00 | 125000.00 | 125000.00 | 450000.00 | 450000.00 | 78607.00 | Novateur Electrical and Digital Systems Private Limited
26.00 | Comprehensive maintenance contract of UPS at Birsi Airport, Gondia after completion of Two (02) year defect liability period. (Excluding batteries) FOR 7th YEAR | 1.00 | Per Year |  | 83323.00 | 83323.00 | 250000.00 | 250000.00 | 216000.00 | 216000.00 | 125000.00 | 125000.00 | 500000.00 | 500000.00 | 83323.00 | Novateur Electrical and Digital Systems Private Limited
| Total in Figures |  |  |  |  | 5549538.00 |  | 6325600.00 |  | 7320060.00 |  | 6795750.00 |  | 8973650.00
Lowest Amount Quoted BY: Novateur Electrical and Digital Systems Private Limited(5549538.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of UPS system for GLF installations at Birsi Airport Gondia Tender ID: 2020_AAI_56666_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Novateur Electrical and Digital Systems Private Limited | 5549538.00 | L1
| 2 | Weartech Engineers Pvt Ltd | 6325600.00 | L2
| 3 | Aviosat Technology Pvt Ltd | 6795750.00 | L3
| 4 | RVD INFRA SOLUTION PVT.LTD. | 7320060.00 | L4
| 5 | RS Power Systems Pvt. Ltd. | 8973650.00 | L5