## BoQ1
Government eProcurement System Created By: Savio Noronha Created Date/Time: 27-Oct-2020 05:07 PM Tender Title: Up gradation of Jabalpur Airport to make it Suitable for Operation of AB 320 Type Aircraft Apron Isolation Bay Flood Lighting Perimeter Lighting Ring Main System for Power Supply and Associated works Tender ID: 2020_AAI_57833_1
Tender Inviting Authority: Asstt. Gen. Manager (E-E) Project, Jabalpur Airport, Jabalpur
Name of Work:- Development of jabalpur airport to make it suitable for AB-320 type Aircraft. SH -Apron & Isolation bay flood lighting,Perimeter Lighting,Ring main system for power supply and associated works.
Contract No: AAI/JGM/ENGG.ELE/JBP/PROJ/05.3/2019-20
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO.(GSTN-24AAEFD3355K1ZI) |  | TRANSRAIL LIGHTING LIMITED(GSTN-26AACCT8765G2ZY) |  | PRASHANT ELECTRICALS(GSTN-23AABFP1106H1ZX) |  | Choubay And Co.(Agencies) Pvt.Ltd.(GSTN-09AAACC6073E1ZT) |  | Naagar Infrastructure Pvt Ltd(GSTN-07AACCN7477R1ZJ) |  | M R ELECTRICALS(GSTN-27AARPV8927A1Z5) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | Ascent Electrification Engineers(GSTN-24AAOFA2574R1ZU) |  | Shakti Infrastructure(GSTN-NA) |  | GAYATRI ELECTRICAL(GSTN-NA) |  | Surya Roshni Limited(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation, testing,& commissioning of 20 M high mast in two sections suitable for wind speed as per IS: 875 part-III,with head frame,winch mounting bracket, luminaries carriage suitable to install minimum 11 nos luminaries in symmetrical arrangement, top pully arrangement complete with dip galvanised finished,civil RCC foundation with excavation in soil, foundation bolts,anchor plates nuts,washers, anchor plate complete in all respects I/C electrically operated raising lowering system double drum winch, 6mm diameter SS wire rope, ,multi core copper conductor cable (Trailing cable(EPR)) of suitable current carrying capacity between top carriage and the base terminal (inside mast),including provision of outdoor type double doors feeder pillar made out of 14 SWG,CRCA sheet with powder coated paint comprising of rating one number incomer 63 A TP MCCB of 25KA and two numbers out going circuits with Suitable TP MCBs of 10KA innterconnecting copper wiring,Auto/manual Switch,0-24 hr .timer & suitable contactor including suitable PCC foundation etc. as required suitable for operation on 415 V, 3 phase, 50HZ, AC power supply. connector, integral power tool motor, manual handle, junction box, lightening finial,including Two number LED Aviation Obstruction Lights shall be on the existing lantern carriage including wiring of all luminaires with all wiring material like PVC insulated PVC sheathed flexible cable of suitable copper conductor cores of 1.5 sqmm junction box of lantern carriege to individual light fitting, lugs,mounting accessories and all labour etc. including 1.1 KV power cables from feeder pillars to individual mast distribution box all complete as required as per technical specification attached. | 6.00 | Each |  | 215000.00 | 1290000.00 | 303455.00 | 1820730.00 | 350000.00 | 2100000.00 | 380000.00 | 2280000.00 | 700000.00 | 4200000.00 | 276000.00 | 1656000.00 | 353000.00 | 2118000.00 | 429088.00 | 2574528.00 | 250000.00 | 1500000.00 | 501500.00 | 3009000.00 | 280000.00 | 1680000.00 | 1290000.00 | DOSHI ELECTRIC ENGG. CO.
2.00 | Supply ,assembly and erection of 2.6 Mtr height (height above ground is 2.75 mtr. as per the drawing attached), G.I Octagonal pole suitable to withstand wind speed as per IS -875 made out of HT steel confirming to grade S355J0 or equivalent with single arm bracket made out of suitable dia GI pipe EN 8 grade foundation bolt,base plate with Fe 410 confirming to IS 226 / IS 2062 etc. with complete accessories.The poles shall be hot dip galvanised as per IS 2629 /IS 2633 /IS 4759 standards with average coating thickness of 70 micron.The poles shall be provided with a vandal resistant and weather proof/water proof flush door of 500 mm length(Approx.) at a height of 500 mm from base plate with proper strenghtening to cut out of the door opening. An outdoor IP66 rated junction box/ looping box with heavy duty single phase and neutral connector with 6 amp. DP MCB shall be provided inside the cutout.Poles shall be provided with two earth studs at the bottom Poles shall be fixed to foudation with a set of four foundation bolts etc as required as per technical specification attached. | 950.00 | No. |  | 6000.00 | 5700000.00 | 5814.00 | 5523300.00 | 7700.00 | 7315000.00 | 5000.00 | 4750000.00 | 4000.00 | 3800000.00 | 6000.00 | 5700000.00 | 5500.00 | 5225000.00 | 5777.00 | 5488150.00 | 3500.00 | 3325000.00 | 5900.00 | 5605000.00 | 4000.00 | 3800000.00 | 3325000.00 | Shakti Infrastructure
3.00 | Erection of Octagonal pole provided in item no. 2 (SH-II Sr. no 1) above in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation refilling providing 2 no X 50 mm dia DWC Pipes for cable entery etc. as required
3.01 | Above 1 metre and upto 6.5 metre | 950.00 | Jobs |  | 3000.00 | 2850000.00 | 5313.00 | 5047350.00 | 3900.00 | 3705000.00 | 1800.00 | 1710000.00 | 2500.00 | 2375000.00 | 4200.00 | 3990000.00 | 1500.00 | 1425000.00 | 2680.00 | 2546000.00 | 2500.00 | 2375000.00 | 3000.00 | 2850000.00 | 2921.00 | 2774950.00 | 1425000.00 | Manish Electricals
4.00 | Supply,installation,testing commissioning of high pressure die cast aluminium LED Flood light luminaire with toughened glass/Borosilicate glass lense with minimum system lumen output of 38500 lumens & minimum system efficiency of 110lm/w and as per technical specification attached etc.complete as required.. | 25.00 | No |  | 16000.00 | 400000.00 | 14250.00 | 356250.00 | 17500.00 | 437500.00 | 19000.00 | 475000.00 | 5000.00 | 125000.00 | 12360.00 | 309000.00 | 18000.00 | 450000.00 | 14318.00 | 357950.00 | 16000.00 | 400000.00 | 35000.00 | 875000.00 | 11450.00 | 286250.00 | 125000.00 | Naagar Infrastructure Pvt Ltd
5.00 | Supply,installation,testing commissioning of high pressure die cast aluminium LED Flood light luminaire with toughened/Borosilicate glass lense with minimum system lumen output of 33000 lumens & minimum system efficcancy of 110lm/w and as per technical specification attached etc. complete as required.. | 6.00 | No |  | 14000.00 | 84000.00 | 12113.00 | 72678.00 | 15500.00 | 93000.00 | 15500.00 | 93000.00 | 5000.00 | 30000.00 | 11400.00 | 68400.00 | 15000.00 | 90000.00 | 12018.00 | 72108.00 | 14000.00 | 84000.00 | 30000.00 | 180000.00 | 10280.00 | 61680.00 | 30000.00 | Naagar Infrastructure Pvt Ltd
6.00 | Supply,installation,testing commissioning of high pressure die cast aluminium LED street light luminaire with toughened glass with minimum system lumen output of 1500 lumens & minimum system efficcancy of 110lm/w and as per technical specification attached etc. as complete required.. | 950.00 | no |  | 1500.00 | 1425000.00 | 938.00 | 891100.00 | 1250.00 | 1187500.00 | 1800.00 | 1710000.00 | 6500.00 | 6175000.00 | 1320.00 | 1254000.00 | 1200.00 | 1140000.00 | 1063.00 | 1009850.00 | 1800.00 | 1710000.00 | 2031.48 | 1929906.00 | 1010.00 | 959500.00 | 891100.00 | TRANSRAIL LIGHTING LIMITED
7.00 | Supply of following size of 1.1 kv grade FR aluminium conductor XLPE insulated and PVC sheathed armoured cable as per IS: 7098:1988 (Part-I) with upto date amendments.
7.01 | 3½ core X 400 Sq.mm. A2XFY | 6800.00 | Meter |  | 1400.00 | 9520000.00 | 1245.00 | 8466000.00 | 1200.00 | 8160000.00 | 1300.00 | 8840000.00 | 1180.00 | 8024000.00 | 1031.00 | 7010800.00 | 1350.00 | 9180000.00 | 942.00 | 6405600.00 | 950.00 | 6460000.00 | 750.00 | 5100000.00 | 848.00 | 5766400.00 | 5100000.00 | GAYATRI ELECTRICAL
7.02 | 3½ core X 120 Sq.mm. A2XFY | 3664.00 | Meter |  | 700.00 | 2564800.00 | 436.00 | 1597504.00 | 400.00 | 1465600.00 | 418.00 | 1531552.00 | 450.00 | 1648800.00 | 355.00 | 1300720.00 | 380.00 | 1392320.00 | 325.00 | 1190800.00 | 380.00 | 1392320.00 | 250.00 | 916000.00 | 295.00 | 1080880.00 | 916000.00 | GAYATRI ELECTRICAL
7.03 | 3½ core X 25 Sq.mm. A2XFY | 9480.00 | Meter |  | 190.00 | 1801200.00 | 132.00 | 1251360.00 | 150.00 | 1422000.00 | 152.00 | 1440960.00 | 140.00 | 1327200.00 | 112.00 | 1061760.00 | 125.00 | 1185000.00 | 103.00 | 976440.00 | 125.00 | 1185000.00 | 125.00 | 1185000.00 | 96.00 | 910080.00 | 910080.00 | Surya Roshni Limited
8.00 | Supply of following size of 1.1 kv COPPER grade Armoured PVC Control Cable IS:1554(PT-I)-1988
8.01 | 6 CX2.5 Sqmm | 7700.00 | Meter |  | 190.00 | 1463000.00 | 195.00 | 1501500.00 | 160.00 | 1232000.00 | 165.00 | 1270500.00 | 158.00 | 1216600.00 | 145.00 | 1116500.00 | 155.00 | 1193500.00 | 100.00 | 770000.00 | 150.00 | 1155000.00 | 110.00 | 847000.00 | 130.00 | 1001000.00 | 770000.00 | Ascent Electrification Engineers
9.00 | supply, erection , testing and commissioning of cubicle type compartmentalised , rear/front access free standing, dust and vermin proof (Minimum IP 54 ingress protection) double door main switchboards conforming to IEC‐60439(PTTA) upto 250 A MCCB and As per IEC-61439 (TTA ) above 250 A MCCB suitable for use at 433 volts, 3 phase 4 wire 50 Hertz system suitable for a symmetrical fault level of 50 kA (as specified with the respective panel item) at 433 volts, fabricated from 2 mm outer thick CRCA sheets with hinged, gasketted (metal based neoprene) and lockable doors having structural reinforcement with suitable angle/channel/T/flat sections including 3 mm thick gland plates on top and bottom including lifting hooks and earth bus of required size with 2 nos. earthing terminals, coating, paint finish of approved shade over metal surface cleaned and treated with nine tank process complete with interconnections etc. as per specifications, as required and as below. The incoming and outgoing feeders shall be accommodated in a modular arrangement, detachable gland plates, adequate size cable alley, Sign writing, Painting, Earthing,Numbering, Danger plate, including PVC insulated copper FRLSH wires of minimum1.5sq.mm( for metering )& 2.5sq.mm (protection)for CT's etc. complete with metering & protection as required & civil foundation as per specifications.The Surge Protection Device (SPD) manufacturer shall offer a complete line of Surge Protection Devices to support the requirements for Main LT Panel Incoming feeders & automatic fire suppression system etc. as requires as per attached specification. (Note: The contractor may select the next higher fault rating of ACB/MCCB if it is not readily available, without any extra cost.)
10.00 | Main distribution Panel(F/P-1)(For Panel Detail Ref Item NO 9) Consisting of following | 1.00 | Set |  | 1100000.00 | 1100000.00 | 1193943.00 | 1193943.00 | 1400000.00 | 1400000.00 | 1100000.00 | 1100000.00 | 620000.00 | 620000.00 | 201600.00 | 201600.00 | 910000.00 | 910000.00 | 896425.00 | 896425.00 | 690000.00 | 690000.00 | 675000.00 | 675000.00 | 835280.00 | 835280.00 | 201600.00 | M R ELECTRICALS
10.01 | Incomers:
10.02 | i) 2 No. 600 Amps. 4P MCCB 50KA, Icu=Ics with Microprocessor based release having O/L ,S/C earth fault protection & necessary equipped with the following:
10.03 | a) 3 Nos. Phase indication LED lamps with 2Amp back up MCB, breaker 'ON/OFF/TRIP' indicating light with 2A MCB
10.04 | Digital Multifunction Meter, accuracy class 0.5s, with LED screen as per specs. with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 15 VA Class1.0 metering. ,protection MCBs as required accessories to complete the system.
10.05 | Bus couplers:
10.06 | i) 1 No. 600 Amps. 4P MCCB 50 KA, Icu=Ics with Microprocessor based release having O/L ,S/C protection.
10.07 | Bus Bar :
10.08 | 2 Sections of Electrolytic high conductivity Aluminium extensible three phase and neutral busbars rated at 600 amps , & auxiliary Bus Bars of suitable capacity insulated with heat shrinkable coloured PVC sleeves & suitable to withstand symmetrical fault level of 50 kA at 433 volts, i/c DMC/SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc.
10.09 | Outgoings:
10.10 | All MCCB (Ics=lcu) with O/L, S/C,E/F followings shall be applicable to each.
10.11 | All outgoing with MCCB for O/C, S/C,E/F protection with On, off trip indications of following capacity and rating,50 KA (Ics=Icu=100% ) with Set of Digital flush type calibrated Intelligent multifunction meters (with communication port) suitable rating class ‐ 1.0 accuracy , showing V, A, KW with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 5 VA Class 1.0 metering. , Spreader links and phase barrier, solid neutral link complete with wiring , connections etc.
10.12 | i) 2 Nos. ‐ Thermal Magnetic 250 Amp. 4P MCCB (LLZ) F/P-5
10.13 | ii)2 Nos. ‐ Thermal Magnetic 250 Amp. 4P MCCB,(DVOR & GP) F/P-3
10.14 | (iii) 2no.- Thermal magnetuc 125 Amp. 4P MCCB,(Perimeter Light F/P-4)
10.15 | (iv) 2no.- Thermal magnetuc 125 Amp. 4P MCCB,(Apron high mast F/P-2)
10.16 | (v) 4no.- Thermal magnetuc 100 Amp. 4P MCCB,(Spare)
10.17 | Necessary interlocking shall be successfully operational in all possible combinations.
11.00 | High mast feedar pillar panel -2 (For Panel Detail Ref Item NO 9) Consisting of following | 1.00 | set |  | 550000.00 | 550000.00 | 409291.00 | 409291.00 | 600000.00 | 600000.00 | 360000.00 | 360000.00 | 150000.00 | 150000.00 | 88800.00 | 88800.00 | 310000.00 | 310000.00 | 140645.00 | 140645.00 | 295000.00 | 295000.00 | 275000.00 | 275000.00 | 260163.00 | 260163.00 | 88800.00 | M R ELECTRICALS
11.01 | Incomers:
11.02 | i) 2 No. 125 Amps. 4P MCCB 50KA, Icu=Ics with thermo magnetic based release having O/L ,S/C earth fault protection & necessary equipped with the following:
11.03 | a) 3 Nos. Phase indication LED lamps with 2Amp back up MCB, breaker 'ON/OFF/TRIP' indicating light with 2A MCB
11.04 | Digital Multifunction Meter, accuracy class 0.5s, with LED screen as per specs. with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 15 VA Class1.0 metering. ,protection MCBs as required accessories to complete the system.
11.05 | Bus couplers:
11.06 | i) 1 No. 125 Amps. 4P MCCB 50 KA, Icu=Ics with Thermal Magnetic based release having O/L ,S/C protection.
11.07 | Bus Bar :
11.08 | 2 Sections of Electrolytic high conductivity Aluminium extensible three phase and neutral busbars rated at 200 amps , & auxiliary Bus Bars of suitable capacity insulated with heat shrinkable coloured PVC sleeves & suitable to withstand symmetrical fault level of 50 kA at 433 volts, i/c DMC/SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc.
11.09 | Outgoings:
11.10 | All MCCB (Ics=lcu) with O/L, S/C,E/F followings shall be applicable to each.
11.11 | All outgoing with MCCB for O/C, S/C,E/F protection with On, off trip indications of following capacity and rating, 50 KA (Ics=Icu=100% ) with Set of Digital flush type calibrated Intelligent multifunction meters (with communication port) suitable rating class ‐ 1.0 accuracy , showing V, A, KW with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 5 VA Class 1.0 metering. , Spreader links and phase barrier, solid neutral link complete with wiring , connections etc.
11.12 | i) 4 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCCB, ( High mast feedar piller)
11.13 | ii)2 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCB, ( Spares)
11.14 | Necessary interlocking shall be successfully operational in all possible combinations.
12.00 | DVOR &GP feedar Panel-3(For Panel Detail Ref Item NO 9) Consisting of following | 1.00 | set |  | 900000.00 | 900000.00 | 634727.00 | 634727.00 | 1000000.00 | 1000000.00 | 700000.00 | 700000.00 | 240000.00 | 240000.00 | 148800.00 | 148800.00 | 585000.00 | 585000.00 | 377373.00 | 377373.00 | 590000.00 | 590000.00 | 315000.00 | 315000.00 | 487967.00 | 487967.00 | 148800.00 | M R ELECTRICALS
12.01 | Incomers:
12.02 | i) 2 No. 250 Amps. 4P MCCB 50 KA, Icu=Ics with thermo magnetic based release having O/L ,S/C earth fault protection & necessary equipped with the following:
12.03 | a) 3 Nos. Phase indication LED lamps with 2Amp back up MCB, breaker 'ON/OFF/TRIP' indicating light with 2A MCB
12.04 | Digital Multifunction Meter, accuracy class 0.5s, with LED screen as per specs. with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 15 VA Class1.0 metering. ,protection MCBs as required accessories to complete the system.
12.05 | Bus couplers:
12.06 | i) 1 No. 250 Amps. 4P MCCB 35 KA, Icu=Ics with Thermal Magnetic based release having O/L ,S/C protection.
12.07 | Bus Bar :
12.08 | 2 Sections of Electrolytic high conductivity Aluminium extensible three phase and neutral busbars rated at 300 amps , & auxiliary Bus Bars of suitable capacity insulated with heat shrinkable coloured PVC sleeves & suitable to withstand symmetrical fault level of 50 kA at 433 volts, i/c DMC/SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc.
12.09 | Outgoings:
12.10 | All MCCB (Ics=lcu) with O/L, S/C,E/F followings shall be applicable to each.
12.11 | All outgoing with MCCB for O/C, S/C,E/F protection with On, off trip indications of following capacity and rating, 50 KA (Ics=Icu=100% ) with Set of Digital flush type calibrated Intelligent multifunction meters (with communication port) suitable rating class ‐ 1.0 accuracy , showing V, A, KW with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 5 VA Class 1.0 metering. , Spreader links and phase barrier, solid neutral link complete with wiring , connections etc.
12.12 | i) 2 Nos. ‐ Thermal Magnetic 125 Amp. 4P MCCB, ( GP)
12.13 | i) 2 Nos. ‐ Thermal Magnetic 125 Amp. 4P MCCB, ( DVOR)
12.14 | ii)4 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCCB, ( Spares)
12.15 | iii) 2 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCCB with 20 Amp. 4P contactor ( perimeter Light)
12.16 | 2 no. 0‐24 hour timer auto/manual by pass selector switches along with photo cell sensor to switch on the lights during the day off period.
12.17 | Necessary interlocking shall be successfully operational in all possible combinations.
13.00 | perimeter light feedar pillar panel -4 (For Panel Detail Ref Item NO 9) Consisting of following | 1.00 | Set |  | 400000.00 | 400000.00 | 366223.00 | 366223.00 | 500000.00 | 500000.00 | 325000.00 | 325000.00 | 120000.00 | 120000.00 | 85200.00 | 85200.00 | 318000.00 | 318000.00 | 175375.00 | 175375.00 | 285000.00 | 285000.00 | 225200.00 | 225200.00 | 225116.00 | 225116.00 | 85200.00 | M R ELECTRICALS
13.01 | Incomers:
13.02 | i) 2 No. 125 Amps. 4P MCCB 50KA, Icu=Ics with thermo magnetic based release having O/L ,S/C earth fault protection & necessary equipped with the following:
13.03 | a) 3 Nos. Phase indication LED lamps with 2Amp back up MCB, breaker 'ON/OFF/TRIP' indicating light with 2A MCB
13.04 | Digital Multifunction Meter, accuracy class 0.5s, with LED screen as per specs. with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 15 VA Class1.0 metering. ,protection MCBs as required accessories to complete the system.
13.05 | Bus couplers:
13.06 | i) 1 No. 125 Amps. 4P MCCB 50 KA, Icu=Ics with Thermal Magnetic based release having O/L ,S/C protection.
13.07 | Bus Bar :
13.08 | 2 Sections of Electrolytic high conductivity Aluminium extensible three phase and neutral busbars rated at 200 amps , & auxiliary Bus Bars of suitable capacity insulated with heat shrinkable coloured PVC sleeves & suitable to withstand symmetrical fault level of 50 kA at 433 volts, i/c DMC/SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc.
13.09 | Outgoings:
13.10 | All MCCB (Ics=lcu) with O/L, S/C,E/F followings shall be applicable to each.
13.11 | All outgoing with MCCB for O/C, S/C,E/F protection with On, off trip indications of following capacity and rating, 50KA (Ics=Icu=100% ) with Set of Digital flush type calibrated Intelligent multifunction meters (with communication port) suitable rating class ‐ 1.0 accuracy , showing V, A, KW with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 5 VA Class 1.0 metering. , Spreader links and phase barrier, solid neutral link complete with wiring , connections etc.
13.12 | i) 2 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCCB with 20 Amp. 4P contactor ( perimeter Light)
13.13 | 2 no. 0‐24 hour timer auto/manual by pass selector switches along with photo cell sensor to switch on the lights during the day off period.
13.14 | ii)2 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCB, ( Spares)
13.15 | Necessary interlocking shall be successfully operational in all possible combinations.
14.00 | LLZ Panel: 5 feedar Panel(For Panel Detail Ref Item NO 9) Consisting of following | 1.00 | Set |  | 800000.00 | 800000.00 | 632035.00 | 632035.00 | 900000.00 | 900000.00 | 650000.00 | 650000.00 | 255000.00 | 255000.00 | 136800.00 | 136800.00 | 585000.00 | 585000.00 | 405145.00 | 405145.00 | 545000.00 | 545000.00 | 328500.00 | 328500.00 | 487967.00 | 487967.00 | 136800.00 | M R ELECTRICALS
14.01 | Incomers:
14.02 | i) 2 No. 250 Amps. 4P MCCB 50KA, Icu=Ics with thermo magnetic based release having O/L ,S/C earth fault protection & necessary equipped with the following:
14.03 | a) 3 Nos. Phase indication LED lamps with 2Amp back up MCB, breaker 'ON/OFF/TRIP' indicating light with 2A MCB
14.04 | Digital Multifunction Meter, accuracy class 0.5s, with LED screen as per specs. with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 15 VA Class1.0 metering. ,protection MCBs as required accessories to complete the system.
14.05 | Bus couplers:
14.06 | i) 1 No. 250 Amps. 4P MCCB 50 KA, Icu=Ics with Thermal Magnetic based release having O/L ,S/C protection.
14.07 | Bus Bar :
14.08 | 2 Sections of Electrolytic high conductivity Aluminium extensible three phase and neutral busbars rated at 300 amps , & auxiliary Bus Bars of suitable capacity insulated with heat shrinkable coloured PVC sleeves & suitable to withstand symmetrical fault level of 50 kA at 433 volts, i/c DMC/SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc.
14.09 | Outgoings:
14.10 | All MCCB (Ics=lcu) with O/L, S/C,E/F followings shall be applicable to each.
14.11 | All outgoing with MCCB for O/C, S/C,E/F protection with On, off trip indications of following capacity and rating, 50 KA (Ics=Icu=100% ) with Set of Digital flush type calibrated Intelligent multifunction meters (with communication port) suitable rating class ‐ 1.0 accuracy , showing V, A, KW with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 5 VA Class 1.0 metering. , Spreader links and phase barrier, solid neutral link complete with wiring , connections etc.
14.12 | i) 2 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCB with 20 Amp. 4P contactor ( perimeter Light)
14.13 | 2 no. 0‐24 hour timer auto/manual by pass selector switches along with photo cell sensor to switch on the lights during the day off period.
14.14 | ii) 2 Nos. ‐ Thermal Magnetic 125 Amp. 4P MCCB (Isolation)
14.15 | iii) 2 Nos. ‐ Thermal Magnetic 125 Amp. 4P MCCB, (ATS of LLZ)
14.16 | iv)4 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCCB, ( Spares)
14.17 | Necessary interlocking shall be successfully operational in all possible combinations.
15.00 | Isolation bay feedar pillar panel -6 (For Panel Detail Ref Item NO 9) Consisting of following | 1.00 | Set |  | 400000.00 | 400000.00 | 364877.00 | 364877.00 | 500000.00 | 500000.00 | 340000.00 | 340000.00 | 123000.00 | 123000.00 | 98400.00 | 98400.00 | 270000.00 | 270000.00 | 205810.00 | 205810.00 | 315000.00 | 315000.00 | 237500.00 | 237500.00 | 254331.00 | 254331.00 | 98400.00 | M R ELECTRICALS
15.01 | Incomers:
15.02 | i) 2 No. 125 Amps. 4P MCCB 50KA, Icu=Ics with thermo magnetic based release having O/L ,S/C earth fault protection & necessary equipped with the following:
15.03 | a) 3 Nos. Phase indication LED lamps with 2Amp back up MCB, breaker 'ON/OFF/TRIP' indicating light with 2A MCB
15.04 | Digital Multifunction Meter, accuracy class 0.5s, with LED screen as per specs. with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 15 VA Class1.0 metering. ,protection MCBs as required accessories to complete the system.
15.05 | Bus couplers:
15.06 | i) 1 No. 125 Amps. 4P MCCB 35 KA, Icu=Ics with Thermal Magnetic based release having O/L ,S/C protection.
15.07 | Bus Bar :
15.08 | 2 Sections of Electrolytic high conductivity Aluminium extensible three phase and neutral busbars rated at 300 amps , & auxiliary Bus Bars of suitable capacity insulated with heat shrinkable coloured PVC sleeves & suitable to withstand symmetrical fault level of 50 kA at 433 volts, i/c DMC/SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc.
15.09 | Outgoings:
15.10 | All MCCB (Ics=lcu) with O/L, S/C,E/F followings shall be applicable to each.
15.11 | All outgoing with MCCB for O/C, S/C,E/F protection with On, off trip indications of following capacity and rating, 50 KA (Ics=Icu=100% ) with Set of Digital flush type calibrated Intelligent multifunction meters (with communication port) suitable rating class ‐ 1.0 accuracy , showing V, A, KW with 3 Nos. cast resin current transformers of dual core CT's of suitable Amp. ratio, 5 VA Class 1.0 metering. , Spreader links and phase barrier, solid neutral link complete with wiring , connections etc.
15.12 | 2 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCB, ( Hm-1 &Hm-2)
15.13 | ii) 2 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCCB with 20 Amp. 4P contactor ( perimeter Light)
15.14 | 2 no. 0‐24 hour timer auto/manual by pass selector switches along with photo cell sensor to switch on the lights during the day off period.
15.15 | iii)2 Nos. ‐ Thermal Magnetic 63 Amp. 4P MCB, ( Spares)
15.16 | Necessary interlocking shall be successfully operational in all possible combinations.
16.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE DWC pipe as required.
16.01 | Above 185 sq. mm and upto 400 sq. mm | 6800.00 | Meter |  | 75.00 | 510000.00 | 113.00 | 768400.00 | 55.00 | 374000.00 | 50.00 | 340000.00 | 120.00 | 816000.00 | 40.00 | 272000.00 | 80.00 | 544000.00 | 105.00 | 714000.00 | 49.00 | 333200.00 | 40.00 | 272000.00 | 93.00 | 632400.00 | 272000.00 | M R ELECTRICALS, GAYATRI ELECTRICAL
16.02 | Above 95 sq. mm and upto185 sq. mm | 3664.00 | Meter |  | 60.00 | 219840.00 | 85.00 | 311440.00 | 40.00 | 146560.00 | 40.00 | 146560.00 | 80.00 | 293120.00 | 28.00 | 102592.00 | 60.00 | 219840.00 | 75.00 | 274800.00 | 40.00 | 146560.00 | 28.00 | 102592.00 | 76.00 | 278464.00 | 102592.00 | M R ELECTRICALS, GAYATRI ELECTRICAL
16.03 | Upto 35 Sqmm | 17180.00 | Meter |  | 30.00 | 515400.00 | 26.00 | 446680.00 | 35.00 | 601300.00 | 30.00 | 515400.00 | 20.00 | 343600.00 | 15.00 | 257700.00 | 30.00 | 515400.00 | 32.00 | 549760.00 | 40.00 | 687200.00 | 25.00 | 429500.00 | 41.00 | 704380.00 | 257700.00 | M R ELECTRICALS
17.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required.
17.01 | 200 mm dia (OD-200 mm & ID-175 mm nominal) | 6800.00 | Meter |  | 400.00 | 2720000.00 | 272.00 | 1849600.00 | 325.00 | 2210000.00 | 400.00 | 2720000.00 | 300.00 | 2040000.00 | 333.00 | 2264400.00 | 350.00 | 2380000.00 | 315.00 | 2142000.00 | 275.00 | 1870000.00 | 250.00 | 1700000.00 | 353.00 | 2400400.00 | 1700000.00 | GAYATRI ELECTRICAL
17.02 | 120 mm dia (OD-120 mm & ID-103 mm nominal) | 3664.00 | Meter |  | 250.00 | 916000.00 | 244.00 | 894016.00 | 200.00 | 732800.00 | 270.00 | 989280.00 | 210.00 | 769440.00 | 197.00 | 721808.00 | 240.00 | 879360.00 | 195.00 | 714480.00 | 150.00 | 549600.00 | 180.00 | 659520.00 | 238.00 | 872032.00 | 549600.00 | Shakti Infrastructure
17.03 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 17180.00 | Meter |  | 175.00 | 3006500.00 | 222.00 | 3813960.00 | 135.00 | 2319300.00 | 180.00 | 3092400.00 | 150.00 | 2577000.00 | 138.00 | 2370840.00 | 160.00 | 2748800.00 | 133.00 | 2284940.00 | 100.00 | 1718000.00 | 135.00 | 2319300.00 | 175.00 | 3006500.00 | 1718000.00 | Shakti Infrastructure
18.00 | Supplying and making indoor end termination with brass double compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
18.01 | 3½ core X 400 Sq.mm.(82mm) | 12.00 | set |  | 1500.00 | 18000.00 | 2125.00 | 25500.00 | 1600.00 | 19200.00 | 2000.00 | 24000.00 | 5500.00 | 66000.00 | 960.00 | 11520.00 | 1200.00 | 14400.00 | 2399.00 | 28788.00 | 2000.00 | 24000.00 | 1000.00 | 12000.00 | 2336.00 | 28032.00 | 11520.00 | M R ELECTRICALS
18.02 | 3½ X 120 sq. mm (45mm) | 12.00 | set |  | 1200.00 | 14400.00 | 1063.00 | 12756.00 | 550.00 | 6600.00 | 1400.00 | 16800.00 | 2000.00 | 24000.00 | 480.00 | 5760.00 | 750.00 | 9000.00 | 1120.00 | 13440.00 | 2000.00 | 24000.00 | 1000.00 | 12000.00 | 1577.00 | 18924.00 | 5760.00 | M R ELECTRICALS
18.03 | 6C X 2.5 sqmm(19mm) | 12.00 | set |  | 400.00 | 4800.00 | 213.00 | 2556.00 | 115.00 | 1380.00 | 800.00 | 9600.00 | 750.00 | 9000.00 | 240.00 | 2880.00 | 250.00 | 3000.00 | 270.00 | 3240.00 | 2000.00 | 24000.00 | 200.00 | 2400.00 | 584.00 | 7008.00 | 1380.00 | PRASHANT ELECTRICALS
19.00 | Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. | 100.00 | Each |  | 300.00 | 30000.00 | 142.00 | 14200.00 | 200.00 | 20000.00 | 600.00 | 60000.00 | 500.00 | 50000.00 | 360.00 | 36000.00 | 300.00 | 30000.00 | 350.00 | 35000.00 | 250.00 | 25000.00 | 100.00 | 10000.00 | 310.00 | 31000.00 | 10000.00 | GAYATRI ELECTRICAL
20.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (but with charcoal/ coke and salt ) as required | 12.00 | set |  | 7000.00 | 84000.00 | 5454.00 | 65448.00 | 7100.00 | 85200.00 | 5000.00 | 60000.00 | 5000.00 | 60000.00 | 5400.00 | 64800.00 | 7000.00 | 84000.00 | 7500.00 | 90000.00 | 6500.00 | 78000.00 | 12500.00 | 150000.00 | 8528.00 | 102336.00 | 60000.00 | Choubay And Co.(Agencies) Pvt.Ltd., Naagar Infrastructure Pvt Ltd
21.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 9480.00 | Meter |  | 30.00 | 284400.00 | 14.00 | 132720.00 | 10.00 | 94800.00 | 25.00 | 237000.00 | 30.00 | 284400.00 | 10.80 | 102384.00 | 18.00 | 170640.00 | 15.00 | 142200.00 | 22.00 | 208560.00 | 11.76 | 111484.80 | 21.00 | 199080.00 | 94800.00 | PRASHANT ELECTRICALS
22.00 | Constructing brick masonry road gully chamber 75x75x60 cm with bricks in cement mortar 1:4 (1 cement : 4 coarse sand) including 500x450 mm pre-cast cement mortar 1:4 (1 cement : 4 coarse sand) including 500x450 mm pre-cast cement mortar 1:4 (1 cement : 4 coarse sand) pre-cast R.C.C. horizontal grating with frame complete as per standard design : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 210.00 | Each |  | 9000.00 | 1890000.00 | 10625.00 | 2231250.00 | 4500.00 | 945000.00 | 6000.00 | 1260000.00 | 7500.00 | 1575000.00 | 5400.00 | 1134000.00 | 4500.00 | 945000.00 | 2650.00 | 556500.00 | 2500.00 | 525000.00 | 5500.00 | 1155000.00 | 5228.00 | 1097880.00 | 525000.00 | Shakti Infrastructure
| Total in Figures |  |  |  |  | 41461340.00 |  | 40697394.00 |  | 39573740.00 |  | 37047052.00 |  | 39337160.00 |  | 31573464.00 |  | 34920260.00 |  | 31141347.00 |  | 28519440.00 |  | 31488902.80 |  | 30250000.00
Comparative Chart(eAuction)
Sl.No | Bidder Name | Auction Start Price | Quoted Rate in Figures and Words
|  |  | Bidder Price | Amount in Words
1 | Manish Electricals | 28519440 | 23319440.00 | Two Crore Thirty Three Lakh Ninteen Thousand Four Hundred and Fourty
2 | Surya Roshni Limited | 28519440 | 28419440.00 | Two Crore Eighty Four Lakh Ninteen Thousand Four Hundred and Fourty
3 | DOSHI ELECTRIC ENGG. CO. | 28519440 | Not Quoted | Not Quoted
4 | Choubay And Co.(Agencies) Pvt.Ltd. | 28519440 | Not Quoted | Not Quoted
5 | M R ELECTRICALS | 28519440 | 21719440.00 | Two Crore Seventeen Lakh Ninteen Thousand Four Hundred and Fourty
6 | Naagar Infrastructure Pvt Ltd | 28519440 | Not Quoted | Not Quoted
7 | Ascent Electrification Engineers | 28519440 | 23919440.00 | Two Crore Thirty Nine Lakh Ninteen Thousand Four Hundred and Fourty
8 | TRANSRAIL LIGHTING LIMITED | 28519440 | Not Quoted | Not Quoted
9 | PRASHANT ELECTRICALS | 28519440 | Not Quoted | Not Quoted
10 | GAYATRI ELECTRICAL | 28519440 | Not Quoted | Not Quoted
11 | Shakti Infrastructure | 28519440 | 21919440.00 | Two Crore Ninteen Lakh Ninteen Thousand Four Hundred and Fourty
Lowest Amount Quoted BY: M R ELECTRICALS(2.171944E7)

## BOQ Summary
BOQ Summary Details Tender Title: Up gradation of Jabalpur Airport to make it Suitable for Operation of AB 320 Type Aircraft Apron Isolation Bay Flood Lighting Perimeter Lighting Ring Main System for Power Supply and Associated works Tender ID: 2020_AAI_57833_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Shakti Infrastructure | 28519440.00 | L1
| 2 | Surya Roshni Limited | 30250000.00 | L2
| 3 | Ascent Electrification Engineers | 31141347.00 | L3
| 4 | GAYATRI ELECTRICAL | 31488902.80 | L4
| 5 | M R ELECTRICALS | 31573464.00 | L5
| 6 | Manish Electricals | 34920260.00 | L6
| 7 | Choubay And Co.(Agencies) Pvt.Ltd. | 37047052.00 | L7
| 8 | Naagar Infrastructure Pvt Ltd | 39337160.00 | L8
| 9 | PRASHANT ELECTRICALS | 39573740.00 | L9
| 10 | TRANSRAIL LIGHTING LIMITED | 40697394.00 | L10
| 11 | DOSHI ELECTRIC ENGG. CO. | 41461340.00 | L11