## BoQ1
Government eProcurement System Created By: D Boominathan Created Date/Time: 08-Oct-2020 01:07 PM Tender Title: Up gradation of Indoor Air Quality for Safe Operation of Central Air-Conditioning System during Spread of COVID-19 at Trichy Airport Tender ID: 2020_AAI_57835_1
Tender Inviting Authority: Assistant General Manager (E-E)
Name of Work:Upgradation of Indoor Air Quality for Safe Operation of Central Air-Conditioning System during Spread of COVID-19 at Trichy Airport.
Contract No: CW-02/TRY/20-21 Tender ID:2020_AAI_57835_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOLTAS LIMITED(GSTN-33AAACV2809DIZT) |  | ABS AIRCON ENGINEERS PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of UVGI (Ultra Violet Germicidal irradiation) system suitable for mounting inside the AHU units of following capacities for maintaining Indoor Air Quality through coil microbe disinfection & cleaning without the need for regular chemical cleaning with factory fabricated support for UVGI modules, adequate capacity and numbers of UV lamps to achieve UVC (254+/-1 nm wavelength) irradiation with minimum intensity of 4016 μW/cm² for four air changes at all points of AHU cooling coil & in the drain pan and cooling coil dimensions as given below, including provision of reflector with its mounting assembly, macro based control panel with provision of ballasts, isolating transformers, indication lamps, auto door interlocking, interconnection between control panel and UV lamps, cabling from power source to control panel within AHU room, cable glanding, other safety equipments and mounting accessories complete etc., UVGI system supplied must be in strict conformity with Technical specifications given in he tender document. (Tenderers are requested to refer the technical specifications before quoting the rate)
1.01 | Only For 2000 CFM (5TR) AHU (AHU dimensions 2500 X 1500 X 3000 mm ) | 29.00 | Each |  | 45990.00 | 1333710.00 | 30223.00 | 876467.00 | 876467.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
1.02 | 2400 CFM (6TR) AHU (Coil dimensions: 915X710mm) | 2.00 | Each |  | 46360.00 | 92720.00 | 31955.00 | 63910.00 | 63910.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
1.03 | 6400 CFM (16TR) AHU (Coil dimensions: 1900X770mm) | 2.00 | Each |  | 46360.00 | 92720.00 | 50338.00 | 100676.00 | 92720.00 | VOLTAS LIMITED
1.04 | 8800 CFM (22TR) AHU (Coil dimensions: 2032X765mm) | 2.00 | Each |  | 46360.00 | 92720.00 | 50663.00 | 101326.00 | 92720.00 | VOLTAS LIMITED
1.05 | 9600 CFM (24TR) AHU (Coil dimensions: 1981X1168mm) | 1.00 | Each |  | 46360.00 | 46360.00 | 62918.00 | 62918.00 | 46360.00 | VOLTAS LIMITED
1.06 | 10800 CFM (27TR) AHU (Coil dimensions: 2235X762mm) | 1.00 | Each |  | 47610.00 | 47610.00 | 52316.00 | 52316.00 | 47610.00 | VOLTAS LIMITED
1.07 | 11200 CFM (28TR) AHU (Coil dimensions: 2311X1397mm) | 2.00 | Each |  | 47610.00 | 95220.00 | 79808.00 | 159616.00 | 95220.00 | VOLTAS LIMITED
1.08 | 15200 CFM (38TR) AHU (Coil dimensions: 2184X1397mm) | 2.00 | Each |  | 81540.00 | 163080.00 | 79690.00 | 159380.00 | 159380.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
1.09 | 18000 CFM (45TR) AHU (Coil dimensions: 2335X1486mm) | 4.00 | Each |  | 81540.00 | 326160.00 | 79808.00 | 319232.00 | 319232.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
1.10 | 19200 CFM (48TR) AHU (Coil dimensions: 2185X1524mm) | 1.00 | Each |  | 81540.00 | 81540.00 | 79690.00 | 79690.00 | 79690.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
1.11 | 20000 CFM (50TR) AHU (Coil dimensions: 2425x1511mm) | 2.00 | Each |  | 82780.00 | 165560.00 | 91818.00 | 183636.00 | 165560.00 | VOLTAS LIMITED
1.12 | 24000 CFM (60TR) AHU (Coil dimensions: 1600x1270mm) | 1.00 | Each |  | 116710.00 | 116710.00 | 121430.00 | 121430.00 | 116710.00 | VOLTAS LIMITED
2.00 | Design, Supply, Installation, Testing & Commissioning of washable, Box type Air filters of minimum rated MERV-13 or higher at standard 52.5 minimum efficiency reporting values suitable to retrofit in the existing Air Handling Units (AHUs) of following capacity to achieve the ISHRAE Indoor Air Quality(IAQ) parameters by reducing harmful pollutants(particulate matter (PMx), PM 2.5, allergens, pollen, smoke, bacteria, pathogens virus, VOC's, odor etc.) with dust spot efficiency of 89-90% and Arrestance is greater than 98% including detail engineering of dismantling the existing filters and frames, fabrication and fixing new frames for retrofitting filters and meeting all IAQ parameters i.e. PM2.5, PM-10 etc. as per ISHRAE/ASHRAE/ANSI/ NEA & OSHA etc.as required.
2.10 | 2000 CFM (5TR) AHU (Coil dimensions: 760x530mm) | 10.00 | Each |  | 9450.00 | 94500.00 | 15513.00 | 155130.00 | 94500.00 | VOLTAS LIMITED
2.20 | 6400 CFM (16TR) AHU (Coil dimensions: 1900X770mm) | 1.00 | Each |  | 16920.00 | 16920.00 | 26389.00 | 26389.00 | 16920.00 | VOLTAS LIMITED
2.30 | 20000 CFM (50TR) AHU (Coil dimensions: 2425x1511mm) | 1.00 | Each |  | 39940.00 | 39940.00 | 39984.00 | 39984.00 | 39940.00 | VOLTAS LIMITED
3.00 | Supply, installation, testing and commissioning of 2000 CFM, factory built floor mounted double skin type horizontal Treated Fresh Air(TFA) units made of 45 mm thick panels fabricated with aluminium extruded thermal break profile sections consisting of pre plasticized GI casing of thickness 0.8mm outside layer and 0.8mm inside layer with polyurethane foam(PUF) insulation of density 40±2kg/m3 factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, cooling coil sections with aluminium finned copper tubes(tubes thickness not less than 0.5mm) AHRI certified cooling coil of 6 row deep, complete with pre-filters and fine filters, belt drive package with TEFC drive motor of efficiency class IE3 (as per IS12615) suitable for 415±10%V, 50HZ,3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, mixing box for fresh air duct connection, auto purge valve wherever required, necessary vibration isolation arrangement etc., complete as per Technical specifications as required. | 3.00 | Each |  | 132510.00 | 397530.00 | 120215.00 | 360645.00 | 360645.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
4.00 | Supplying, installation, testing and commissioning of 60 mm dia. MS 'C' class chilled water piping inside the terminal building as per IS:1239 (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 50mm thick insulation of density 20Kg/cum rigid EPS pipe section fixed with hot bitumens and single layer of polythene sheet, GI wire mesh finally finished with 10mm thick sand cement plaster for 80mm dia., MS pipe insulation and joints, repairing the damage portion of building etc. in all respect as per specifications as required. | 30.00 | Mtr |  | 1820.00 | 54600.00 | 1675.00 | 50250.00 | 50250.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
5.00 | Supplying, fixing, testing and commissioning of 60 mm dia, Butterfly valve (manual) having Cast Iron body, SS Disc and SS stem, Black Nitrile Rubber Seal & O- Ring and PN 16 pressure rating for chilled water circulation including insulating the valves with same specifications of chilled water piping, plumbing, and provision of adequate support etc., as per Technical specifications as required. | 6.00 | Each |  | 4380.00 | 26280.00 | 4178.00 | 25068.00 | 25068.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
6.00 | Supplying, fixing, testing and commissioning of 60mm dia. strainers in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. | 3.00 | Each |  | 6580.00 | 19740.00 | 5917.00 | 17751.00 | 17751.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
7.00 | Supply, installation, balancing and commissioning of 1.25 mm thickness factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. | 50.00 | Sq.mtr |  | 1250.00 | 62500.00 | 1400.00 | 70000.00 | 62500.00 | VOLTAS LIMITED
8.00 | Supply and fixing of 400mm sweep wall mounting fan, powder coated plastic body, sleek and unique high speed & aerodynamically designed balanced 3 blade with min.air delivery of 90M3/Min. , thermal protected, High speed powerful motor for high air delivery and uniform oscillation control including making good the damage, connection, testing, commissioning etc. as required (As per AAI list of approved makes) | 30.00 | Each |  | 2110.00 | 63300.00 | 5564.00 | 166920.00 | 63300.00 | VOLTAS LIMITED
9.00 | Wiring for circuit/ sub main wiring along with earth wire with 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. | 300.00 | Mtr |  | 240.00 | 72000.00 | 292.00 | 87600.00 | 72000.00 | VOLTAS LIMITED
10.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 A modular socket outlet and 5/6 A modular switch, connections etc. as required. | 15.00 | Each |  | 640.00 | 9600.00 | 442.00 | 6630.00 | 6630.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
11.00 | Supplying and fixing suitable size PVC box with suitable cover in front on surface or in recess, including providing and fixing 3 pin 5/6 A modular socket outlet and 5/6 A modular switch, connections etc. as required. | 15.00 | Each |  | 660.00 | 9900.00 | 437.00 | 6555.00 | 6555.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
12.00 | Supply of 4CX16 Sq.mm XLPE insulated, PVC sheathed aluminium conductor armoured power cable of 1.1KV grade confirming to IS 7098 (Part I) 1978 with upto date amendments etc as required (Make : As per approved list.) | 300.00 | Mtr |  | 90.00 | 27000.00 | 198.00 | 59400.00 | 27000.00 | VOLTAS LIMITED
13.00 | Supply of 3CX6 Sq.mm XLPE insulated, PVC sheathed copper conductor armoured power cable of 1.1KV grade confirming to IS 7098 (Part I) 1978 with upto date amendments etc as required (Make : As per approved list.) | 100.00 | Mtr |  | 210.00 | 21000.00 | 225.00 | 22500.00 | 21000.00 | VOLTAS LIMITED
14.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade Upto 35 sq. mm (clamped with 1mm thick saddle) on wall surface/cable tray etc., as required | 300.00 | Mtr |  | 70.00 | 21000.00 | 58.00 | 17400.00 | 17400.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
15.00 | Supplying and making end termination with brass compression gland and aluminium lugs for size of 4CX16sq.mm (28mm) PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 6.00 | Set |  | 780.00 | 4680.00 | 323.00 | 1938.00 | 1938.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
16.00 | Supply, Installation, Testing and Commissioning of TFAU control (starter) panel, indoor type floor mounted/ wall fixed type starter Panel of cubicle type made out of 14 SWG CRCA sheet totally enclosed, IP 42, dust and vermin proof, suitable for operation on 3 phase and neutral, 415 volts, 50 Hz, AC System wiring with suitable sizes wire/cable, interconnection, terminating for incoming cable, painting etc. The panel shall have bottom cable entry, including supply, installations and testing of following switchgears, metering instruments and accessories in the Panel and as per specifications. a) 63amps, "C" series 10 kA, 4pole MCB -01 no b) NO + NC Power contactors of MNX18 A - 01 no c) Add on block auxiliary contact 3 NO+1NC - MNX-A1 contactor - 01 no d) Over load relay - 1 No e) Selector switch - 1 No f) Push bottoms (Red & Green) - 2 Nos g) LED indication lamp (RYBG) - 4 Nos h) Multifunction meter - 1 No i) Current Transformer 100/5A- 1 No | 3.00 | Job |  | 11820.00 | 35460.00 | 28889.00 | 86667.00 | 35460.00 | VOLTAS LIMITED
17.00 | Supply, fixing, testing and commissioning of pressure gauges with accuracy of +/- 1% of Full Scale Deflection(FSD) in chilled water pipe line and duly insulated to the same specifications as the connected piping and adequately supported as per specifications | 6.00 | Each |  | 2110.00 | 12660.00 | 1900.00 | 11400.00 | 11400.00 | ABS AIRCON ENGINEERS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 3642720.00 |  | 3492824.00
Lowest Amount Quoted BY: ABS AIRCON ENGINEERS PRIVATE LIMITED(3492824.00)

## BOQ Summary
BOQ Summary Details Tender Title: Up gradation of Indoor Air Quality for Safe Operation of Central Air-Conditioning System during Spread of COVID-19 at Trichy Airport Tender ID: 2020_AAI_57835_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ABS AIRCON ENGINEERS PRIVATE LIMITED | 3492824.00 | L1
| 2 | VOLTAS LIMITED | 3642720.00 | L2