## BoQ1
Government eProcurement System Created By: Moatemjen Pongen Created Date/Time: 09-Nov-2020 04:23 PM Tender Title: Provision of LTAC panels at terminal building along with provision of cable laying at Dimapur Airport. Tender ID: 2020_AAI_58844_1
Tender Inviting Authority: AGM(E-E) AAI, Dimapur Airport.
Name of Work: Provision of LTAC panel at Terminal Building along with provision of cable laying at Dimapur Airport.
Contract No: 2020_AAI_58844_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SHAKTI TECHNO FAB PRODUCTS(GSTN-09AAGPB2824D1Z8) |  | SHREE GOURI ELECTRIC ENTERPRISE(GSTN-19ADDPB4683J1ZE) |  | BR Power Control and Automation Services(GSTN-06AREPS4024K1ZP) |  | M/s K.N.Construction(GSTN-20AAHFK7857Q1ZP) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | Incotech Engineers Pvt Ltd(GSTN-19AAACI5242B1ZZ) |  | D.D.METAL CORPORATION(GSTN-18ACGPD4624F2ZW) |  | Youngmen Traders(GSTN-19AEIPB6323B1ZZ) |  | CIS GLOBAL INFRATECH PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I : SITC OF LT PANEL Supply, Installation, Testing and Commissioning of 50 kA Capacity, TTA type Essential LT panel,indoor and cubicle type, made out of 14 SWG CRCA sheet steel, totally enclosed, IP 54 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's, all incoming feeders with true rms value sensing class 1.0 multifunction power cum energy meters as below,castle type interlocking between incomers and bus couplers and having following Incomers,Bus couplers and Outgoing Moulded Case Circuit breakers,continous GI earth bus of size 50mm x 6 mm throughout the length of panel with earth terminations at the ends ,cable alleys suitable for bottom entry of cables including supply & installation of all items as below and as per detailed specifications: ( A)INCOMER MCCB: 400A,4P,50kA, 01 No. Incomer shall have one set of the following items: Intelligent multi function digital meter of suitable range to read V,A,KVA, KVAH, KWAH, KW, KVAR, PF, Hz etc and LED display with required Nos CTs, 15 VA, class 1.0 and control circuit wiring with HRC control fuses. Digital Voltmeter of suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos of MCB control. RYB,ON/OFF LED type Indicating Lamps-3 set BUS BARS 630 Amps TPN Aluminium refer SOQ item No.1 in Tender Documents | 1.00 | Nos. |  | 280000.00 | 280000.00 | 445000.00 | 445000.00 | 398575.00 | 398575.00 | 300000.00 | 300000.00 | 430000.00 | 430000.00 | 356550.00 | 356550.00 | 330060.00 | 330060.00 | 540000.00 | 540000.00 | 280000.00 | 280000.00 | 280000.00 | SHAKTI TECHNO FAB PRODUCTS, CIS GLOBAL INFRATECH PRIVATE LIMITED
2.00 | Supply, Installation, Testing and Commissioning of 50 kA Capacity, PTTA Type Essential LT panel,indoor and cubicle type, made out of 14 SWG CRCA sheet steel, totally enclosed, IP 54 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's, all incoming feeders with true rms value sensing class 1.0 multifunction power cum energy meters as below,castle type interlocking between incomers and bus couplers and having following Incomers,Bus couplers and Outgoing Moulded Case Circuit breakers,continous GI earth bus of size 50mm x 6 mm throughout the length of panel with earth terminations at the ends ,cable alleys suitable for bottom entry of cables including supply & installation of all items as below and as per detailed specifications: A)INCOMER MCCB: 200A,4P,50kA, 01 No. Incomer shall have one set of the following items: Intelligent multi function digital meter of suitable range to read V,A,KVA, KVAH, KWAH, KW, KVAR, PF, Hz etc and LED display with required Nos CTs, 15 VA, class 1.0 and control circuit wiring with HRC control fuses. Digital Voltmeter of suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos of MCB control. RYB,ON/OFF LED type Indicating Lamps-3 set BUS BARS 630 Amps TPN Aluminium refer SOQ item No.2 in Tender Documents | 1.00 | Nos. |  | 176000.00 | 176000.00 | 210000.00 | 210000.00 | 210999.00 | 210999.00 | 170000.00 | 170000.00 | 160000.00 | 160000.00 | 168125.00 | 168125.00 | 165000.00 | 165000.00 | 300000.00 | 300000.00 | 280000.00 | 280000.00 | 160000.00 | Awasthi Electric Works
3.00 | Supply, Installation, Testing and Commissioning of 35 kA Capacity ,indoor wall mounted type Panel Box made out of 14 SWG CRCA sheet steel, totally enclosed, IP 54 protection, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system , with Aluminium Bus Bar, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with digital type ammeter and voltmeter,LED type indicating lamps, all outgoing feeders to be equipped with AC single phase electronic KWH energy meter of rating 5-30A, Class 1.0, 240V, 50Hz , having following combinationof incoming and outgoing switchgears,continous GI earth bus of size 25mm x 6 mm throughout the length of panel with earth terminations at the ends ,cable alleys suitable for bottom entry of cables including supply & installation of all items as below and as per detailed specifications: ( A)INCOMER MCCB: 63A,4P, 35kA, 01 No. Incomer shall have one set of the following items: Digital Voltmeter of suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos of MCB control. RYB,ON/OFF LED type Indicating Lamps-3 set BUS BARS 25 mm X 6 mm , minimum current carrying capacity of 100 Amps, TPN Aluminium (B ) OUTGOING MCB : 32 A, TPN, 'C' Series, 415 V , 50 Hz, 10kA, 6 Nos. AC single phase electronic KWH energy meter of rating 5-30A, Class 1.0, 240V, 50Hz. 01 no. against each outgoing feeder. Total 06 nos. 06 Sets (1 Set for each Outgoing MCB) of Indicating lamps LED type, for breaker RYB, "ON", "OFF" indication with HRC control fuses. Refer SOQ item no. 3 in Tender documents | 5.00 | Nos. |  | 77000.00 | 385000.00 | 450000.00 | 2250000.00 | 115599.00 | 577995.00 | 70000.00 | 350000.00 | 65000.00 | 325000.00 | 81900.00 | 409500.00 | 90000.00 | 450000.00 | 38000.00 | 190000.00 | 100000.00 | 500000.00 | 190000.00 | Youngmen Traders
4.00 | Dismantalling of existing LT Panel along with accessories, components, etc. from its existing location at Dimapur Airport and keeping it as per direction of EIC. | 7.00 | Job |  | 3000.00 | 21000.00 | 3000.00 | 21000.00 | 1828.00 | 12796.00 | 700.00 | 4900.00 | 7500.00 | 52500.00 | 1000.00 | 7000.00 | 2700.00 | 18900.00 | 5000.00 | 35000.00 | 30000.00 | 210000.00 | 4900.00 | M/s K.N.Construction
5.00 | SH-II : SITC of Cable Change Over Box, Distribution Board etc, SITC of indoor cubicle type double door , IP 54, totally enclosed compartmentalized wall type dust weather and vermin proof Cable Change Over Box of size 600 mmX 600 mm X 250 mm suitable for 415V, 4 wire, 50Hz supply, fabricated from CRCA sheet of 2mm thick complete with 01 no. Manual Changeover Switch ,Copper Bus Bar, interconnecting with suitable size of copper leads and capable for housing Loop-in & Loop Out of 2 X 95 sq mm Incoming and 2 X 95 sq mm Outgoing Cables, supported on suitable size of angle iron frame etc complete as required. | 1.00 | Each |  | 25000.00 | 25000.00 | 15000.00 | 15000.00 | 8196.00 | 8196.00 | 1200.00 | 1200.00 | 20000.00 | 20000.00 | 27300.00 | 27300.00 | 35000.00 | 35000.00 | 25000.00 | 25000.00 | 5000.00 | 5000.00 | 1200.00 | M/s K.N.Construction
6.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB’s (but without MCB’s and incomer ) as required . 8 way (8 I/C + 24 O/G ), Double door | 13.00 | Each |  | 9000.00 | 117000.00 | 10000.00 | 130000.00 | 7784.00 | 101192.00 | 9525.00 | 123825.00 | 8800.00 | 114400.00 | 5092.00 | 66196.00 | 3400.00 | 44200.00 | 9875.00 | 128375.00 | 15000.00 | 195000.00 | 44200.00 | D.D.METAL CORPORATION
7.00 | Supplying and fixing of following rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. (a)63 A , TPN | 13.00 | Each |  | 2000.00 | 26000.00 | 1500.00 | 19500.00 | 1320.00 | 17160.00 | 1625.00 | 21125.00 | 1295.00 | 16835.00 | 1419.00 | 18447.00 | 1480.00 | 19240.00 | 1550.00 | 20150.00 | 1800.00 | 23400.00 | 16835.00 | Awasthi Electric Works
8.00 | (b) 32 A , TPN | 20.00 | Each |  | 1600.00 | 32000.00 | 1000.00 | 20000.00 | 2032.00 | 40640.00 | 1125.00 | 22500.00 | 930.00 | 18600.00 | 921.00 | 18420.00 | 1040.00 | 20800.00 | 1150.00 | 23000.00 | 1500.00 | 30000.00 | 18420.00 | Incotech Engineers Pvt Ltd
9.00 | (c) 6-32 A , SPN | 102.00 | Each |  | 700.00 | 71400.00 | 450.00 | 45900.00 | 946.00 | 96492.00 | 5025.00 | 512550.00 | 430.00 | 43860.00 | 154.00 | 15708.00 | 470.00 | 47940.00 | 530.00 | 54060.00 | 1000.00 | 102000.00 | 15708.00 | Incotech Engineers Pvt Ltd
10.00 | SH-III : SUPPLY AND LAYING OF LT CABLES , INTERNAL WIRING AND OTHER ASSOCIATED WORKS Supply of XLPE insulated,armoured 1.1 KV grade aluminium conductor cable as per IS 7098(Part 1) 1988 with upto date ammendments of following sizes: (a) 3.5 Core, 95 Sq.mm | 800.00 | Mtr. |  | 400.00 | 320000.00 | 300.00 | 240000.00 | 365.00 | 292000.00 | 418.00 | 334400.00 | 350.00 | 280000.00 | 338.00 | 270400.00 | 395.00 | 316000.00 | 460.00 | 368000.00 | 344.00 | 275200.00 | 240000.00 | SHREE GOURI ELECTRIC ENTERPRISE
11.00 | (b) 3.5 Core, 25 sq mm | 2500.00 | Mtr. |  | 150.00 | 375000.00 | 110.00 | 275000.00 | 145.00 | 362500.00 | 168.00 | 420000.00 | 145.00 | 362500.00 | 127.00 | 317500.00 | 150.00 | 375000.00 | 180.00 | 450000.00 | 136.00 | 340000.00 | 275000.00 | SHREE GOURI ELECTRIC ENTERPRISE
12.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of XLPE armoured aluminium conductor cable of 1.1 KV grade as required. (a) 3.5 Core, 95 Sq.mm | 4.00 | Set |  | 600.00 | 2400.00 | 200.00 | 800.00 | 807.00 | 3228.00 | 188.00 | 752.00 | 650.00 | 2600.00 | 669.00 | 2676.00 | 250.00 | 1000.00 | 1100.00 | 4400.00 | 1950.00 | 7800.00 | 752.00 | M/s K.N.Construction
13.00 | (b) 3.5 Core, 25 sq mm | 26.00 | Set |  | 350.00 | 9100.00 | 125.00 | 3250.00 | 597.00 | 15522.00 | 92.00 | 2392.00 | 350.00 | 9100.00 | 416.00 | 10816.00 | 160.00 | 4160.00 | 500.00 | 13000.00 | 1250.00 | 32500.00 | 2392.00 | M/s K.N.Construction
14.00 | Laying and fixing of one number XLPE armoured power cable of 1.1 KV grade of following size on cable tray as required. above 35 sq mm. and upto 95 sq mm | 250.00 | Mtr. |  | 90.00 | 22500.00 | 30.00 | 7500.00 | 40.00 | 10000.00 | 123.00 | 30750.00 | 110.00 | 27500.00 | 50.00 | 12500.00 | 200.00 | 50000.00 | 55.00 | 13750.00 | 55.00 | 13750.00 | 7500.00 | SHREE GOURI ELECTRIC ENTERPRISE
15.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. (a) above 35 sq mm. and upto 95 sq mm | 275.00 | Mtr. |  | 100.00 | 27500.00 | 40.00 | 11000.00 | 183.00 | 50325.00 | 150.00 | 41250.00 | 80.00 | 22000.00 | 50.00 | 13750.00 | 200.00 | 55000.00 | 130.00 | 35750.00 | 65.00 | 17875.00 | 11000.00 | SHREE GOURI ELECTRIC ENTERPRISE
16.00 | (b) upto 35 sq mm | 1200.00 | Mtr. |  | 90.00 | 108000.00 | 25.00 | 30000.00 | 85.00 | 102000.00 | 90.00 | 108000.00 | 80.00 | 96000.00 | 40.00 | 48000.00 | 120.00 | 144000.00 | 55.00 | 66000.00 | 40.00 | 48000.00 | 30000.00 | SHREE GOURI ELECTRIC ENTERPRISE
17.00 | Laying of one number XLPE armoured power cable of 1.1 KV grade of following size in the existing masonary open duct as required. (a) above 35 sq mm. and upto 95 sq mm | 125.00 | Mtr. |  | 50.00 | 6250.00 | 30.00 | 3750.00 | 85.00 | 10625.00 | 110.00 | 13750.00 | 60.00 | 7500.00 | 50.00 | 6250.00 | 200.00 | 25000.00 | 40.00 | 5000.00 | 85.00 | 10625.00 | 3750.00 | SHREE GOURI ELECTRIC ENTERPRISE
18.00 | (b) upto 35 sq mm | 200.00 | Mtr. |  | 40.00 | 8000.00 | 30.00 | 6000.00 | 73.00 | 14600.00 | 60.00 | 12000.00 | 50.00 | 10000.00 | 40.00 | 8000.00 | 120.00 | 24000.00 | 25.00 | 5000.00 | 65.00 | 13000.00 | 5000.00 | Youngmen Traders
19.00 | Supply & Installation of Wall Fans, of Sweep: 450 mm , Power Rating : 60-65 Watt, Air Delivery > 100 cub mtr /min, , , White Colour, Noise < 60 dB , 5 Star/Most Energy Effiecient Model available as Rated by BEE. | 14.00 | Nos. |  | 5000.00 | 70000.00 | 2700.00 | 37800.00 | 5567.00 | 77938.00 | 2300.00 | 32200.00 | 4000.00 | 56000.00 | 2364.00 | 33096.00 | 6600.00 | 92400.00 | 3500.00 | 49000.00 | 3500.00 | 49000.00 | 32200.00 | M/s K.N.Construction
20.00 | Supply & Installation of Decorative ultra slim square profile LED. Aesthetically designed LED Square/Round panel for surface mounting complete with aluminium housing with integrated electronic driver which provides soft-light and glare free symmetrical illumination. Minimum 20 Watt | 16.00 | Nos. |  | 2000.00 | 32000.00 | 1600.00 | 25600.00 | 997.00 | 15952.00 | 6000.00 | 96000.00 | 1300.00 | 20800.00 | 1465.00 | 23440.00 | 1750.00 | 28000.00 | 1900.00 | 30400.00 | 5000.00 | 80000.00 | 15952.00 | BR Power Control and Automation Services
21.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. (Group A) | 30.00 | Point |  | 2000.00 | 60000.00 | 1200.00 | 36000.00 | 61.00 | 1830.00 | 845.00 | 25350.00 | 950.00 | 28500.00 | 986.00 | 29580.00 | 300.00 | 9000.00 | 825.00 | 24750.00 | 999.00 | 29970.00 | 1830.00 | BR Power Control and Automation Services
22.00 | SITC of modular TP+N Type 1+2 SPD , having 100KA 10/350 micro seconds neutral to earth, 50 KA 10/350 micro sec line to neutral, with limiting voltage less than 1.5 kV for installation on the mains power entry point at the incomers before UPS. | 2.00 | Nos. |  | 15000.00 | 30000.00 | 35000.00 | 70000.00 | 1581.00 | 3162.00 | 3500.00 | 7000.00 | 50000.00 | 100000.00 | 10735.00 | 21470.00 | 13800.00 | 27600.00 | 9500.00 | 19000.00 | 45000.00 | 90000.00 | 3162.00 | BR Power Control and Automation Services
23.00 | Supply of Single Core Flame Retardant Low Smoke & Halogen FR-LSH,PVC insulated, PVC round sheathed, unarmoured copper conductor flexible cable, 1.1 KV grade confirming to IS : 694 with upto date amendments as required. (Standard Roll of 90 mtrs.) (a) 1.5 sq mm | 10.00 | Nos. |  | 1700.00 | 17000.00 | 60.00 | 600.00 | 14.00 | 140.00 | 1590.00 | 15900.00 | 1300.00 | 13000.00 | 1195.00 | 11950.00 | 1500.00 | 15000.00 | 1200.00 | 12000.00 | 1800.00 | 18000.00 | 140.00 | BR Power Control and Automation Services
24.00 | (b) 2.5 sq mm | 10.00 | Nos. |  | 2800.00 | 28000.00 | 100.00 | 1000.00 | 22.00 | 220.00 | 2200.00 | 22000.00 | 2200.00 | 22000.00 | 1992.00 | 19920.00 | 2100.00 | 21000.00 | 2200.00 | 22000.00 | 2600.00 | 26000.00 | 220.00 | BR Power Control and Automation Services
25.00 | (c) 4.0 sq mm | 4.00 | Nos. |  | 4500.00 | 18000.00 | 150.00 | 600.00 | 34.00 | 136.00 | 3169.00 | 12676.00 | 3300.00 | 13200.00 | 2790.00 | 11160.00 | 3300.00 | 13200.00 | 1400.00 | 5600.00 | 2900.00 | 11600.00 | 136.00 | BR Power Control and Automation Services
26.00 | SH-IV : EARTHING Earthing with GI earth plate 600mm x 600mm x 6mm thick, including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 9.00 | Set |  | 12000.00 | 108000.00 | 7000.00 | 63000.00 | 6604.00 | 59436.00 | 7890.00 | 71010.00 | 6000.00 | 54000.00 | 7800.00 | 70200.00 | 7000.00 | 63000.00 | 6000.00 | 54000.00 | 12000.00 | 108000.00 | 54000.00 | Awasthi Electric Works, Youngmen Traders
27.00 | Providing & fixing of 25 mm x 5mm GI strip in 40mm dia B- Class GI pipe from earth electrode including connection with G.Inut,bolt,spring washer,excavation and refilling etc as required. | 20.00 | mtr. |  | 500.00 | 10000.00 | 600.00 | 12000.00 | 277.00 | 5540.00 | 350.00 | 7000.00 | 450.00 | 9000.00 | 606.00 | 12120.00 | 570.00 | 11400.00 | 425.00 | 8500.00 | 483.00 | 9660.00 | 5540.00 | BR Power Control and Automation Services
28.00 | Providing & fixing of 25mm x 5mm GI strip on surface or recess for earth connection as required. | 50.00 | mtr. |  | 175.00 | 8750.00 | 80.00 | 4000.00 | 216.00 | 10800.00 | 150.00 | 7500.00 | 350.00 | 17500.00 | 139.00 | 6950.00 | 200.00 | 10000.00 | 175.00 | 8750.00 | 206.00 | 10300.00 | 4000.00 | SHREE GOURI ELECTRIC ENTERPRISE
| Total in Figures |  |  |  |  | 2393900.00 |  | 3984300.00 |  | 2499999.00 |  | 2766030.00 |  | 2332395.00 |  | 2017024.00 |  | 2415900.00 |  | 2510485.00 |  | 2816680.00
Lowest Amount Quoted BY: Incotech Engineers Pvt Ltd(2017024.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of LTAC panels at terminal building along with provision of cable laying at Dimapur Airport. Tender ID: 2020_AAI_58844_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Incotech Engineers Pvt Ltd | 2017024.00 | L1
| 2 | Awasthi Electric Works | 2332395.00 | L2
| 3 | SHAKTI TECHNO FAB PRODUCTS | 2393900.00 | L3
| 4 | D.D.METAL CORPORATION | 2415900.00 | L4
| 5 | BR Power Control and Automation Services | 2499999.00 | L5
| 6 | Youngmen Traders | 2510485.00 | L6
| 7 | M/s K.N.Construction | 2766030.00 | L7
| 8 | CIS GLOBAL INFRATECH PRIVATE LIMITED | 2816680.00 | L8
| 9 | SHREE GOURI ELECTRIC ENTERPRISE | 3984300.00 | L9