## BoQ1
Government eProcurement System Created By: Pawan Singh Created Date/Time: 10-Dec-2020 01:07 PM Tender Title: Provision of Perimeter Road Lighting at AAI, Deoghar Airport. Tender ID: 2020_AAI_58893_1
Tender Inviting Authority: AGM (Engg-Elect), AAI, Deoghar Airport, Deoghar.
Name of Work: Development of Deoghar Airport SH: Provision of Perimeter Road Lighting at AAI, DEOGHAR Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO.(GSTN-24AAEFD3355K1ZI) |  | RVD INFRA SOLUTION PVT.LTD.(GSTN-24AAGCR7767L1ZQ) |  | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | TRANSRAIL LIGHTING LIMITED(GSTN-26AACCT8765G2ZY) |  | M/S AMAR ENTERPRISES(GSTN-20AAMFA2722R1ZE) |  | RASS CONTRACTOR AND ENGINEERS(GSTN-09AFIPR1600N1Z7) |  | Choubay And Co.(Agencies) Pvt.Ltd.(GSTN-09AAACC6073E1ZT) |  | GIRI ENTERPRISES(GSTN-20ACEPG3920H1ZA) |  | instapower ltd(GSTN-05AAACI9712L1ZG) |  | HPL Electric and Power Limited(GSTN-06AAACH0165J2ZT) |  | RANJIT SALES CORPORATION(GSTN-NA) |  | Surya Roshni Limited(GSTN-NA) |  | M/S Jagdish Singh Enterprises(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 5.0mtr high hot dip galvanised Octagonal poles designed to withstand the maximum wind speed as per IS- 875. Poles shall be Made of Materials Hot Rolled Non Alloy Structural steel complying IS-2062 Grade: E 350 / BSEN 10025 AN Grade : S355 with bottom dia 130mm and Top dia 70mm, thickness 3mm. The poles shall be hot dip galvanised (Minimum coating 65 microns) as per IS-4759:1996/ IS-2629 : 1985/ BSEN ISO 1461. HT steel sheet base plate of size 200X200X12mm complying IS: 2062 / BSEN 10025 AN and Cap Type (Cap length Minimum 300mm) Single arm Bracket of 0.5 meter long (With B class G.I Pipes) suitable for fitment with light fixture,cable-entry & exit and earthing lug,including 4Nos of M16X450mm long 'J' type EN 8 grade or equivalent grade steel foundation bolts along with template etc., complete as required. Note: 1.The doors opening of the poles should be waterproof with Reinforcement flat, locking arrangment and 01 no 6Amp. MCB with provision of connector for connection of incoming and outgoing cable size 4C X 25sqm. etc. 2. The tilt angle of bracket shall be decided based on Lux level design as per requirement at site & The tilt angle may not be same for all poles. | 384.00 | Each | 10453.50 | 7500.00 | 2880000.00 | 3960.00 | 1520640.00 | 6900.00 | 2649600.00 | 6231.00 | 2392704.00 | 10700.00 | 4108800.00 | 8500.00 | 3264000.00 | 5400.00 | 2073600.00 | 5900.00 | 2265600.00 | 6730.00 | 2584320.00 | 5866.00 | 2252544.00 | 5200.00 | 1996800.00 | 6000.00 | 2304000.00 | 7050.00 | 2707200.00 | 1520640.00 | RVD INFRA SOLUTION PVT.LTD.
2.00 | Installation, testing & Commissioning of 5.0mtr high hot dip galvanised poles on existing foundation including giving level for light at pole , Numbering of Poles as per Instruction of E-I-C complete as required. | 384.00 | Each | 929.20 | 700.00 | 268800.00 | 110.00 | 42240.00 | 50.00 | 19200.00 | 814.00 | 312576.00 | 1500.00 | 576000.00 | 1500.00 | 576000.00 | 200.00 | 76800.00 | 500.00 | 192000.00 | 800.00 | 307200.00 | 312.50 | 120000.00 | 1000.00 | 384000.00 | 549.00 | 210816.00 | 500.00 | 192000.00 | 19200.00 | jaydeep agency corporation
3.00 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge.. All kinds of soil. | 77.00 | Cum | 139.00 | 225.00 | 17325.00 | 770.00 | 59290.00 | 210.00 | 16170.00 | 678.00 | 52206.00 | 260.00 | 20020.00 | 7500.00 | 577500.00 | 250.00 | 19250.00 | 200.00 | 15400.00 | 1035.00 | 79695.00 | 562.50 | 43312.50 | 800.00 | 61600.00 | 6593.00 | 507661.00 | 200.00 | 15400.00 | 15400.00 | GIRI ENTERPRISES, M/S Jagdish Singh Enterprises
4.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size) | 19.00 | Cum | 3901.00 | 4000.00 | 76000.00 | 4950.00 | 94050.00 | 700.00 | 13300.00 | 4749.00 | 90231.00 | 6000.00 | 114000.00 | 7500.00 | 142500.00 | 4000.00 | 76000.00 | 4000.00 | 76000.00 | 6727.00 | 127813.00 | 5265.00 | 100035.00 | 2000.00 | 38000.00 | 6593.00 | 125267.00 | 3000.00 | 57000.00 | 13300.00 | jaydeep agency corporation
5.00 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement including centring & shuttering. - All work up to plinth level . 1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size) | 49.00 | Cum | 5885.00 | 7000.00 | 343000.00 | 3685.00 | 180565.00 | 2150.00 | 105350.00 | 8142.00 | 398958.00 | 7000.00 | 343000.00 | 7500.00 | 367500.00 | 6000.00 | 294000.00 | 3500.00 | 171500.00 | 5795.00 | 283955.00 | 5265.00 | 257985.00 | 100.00 | 4900.00 | 10989.00 | 538461.00 | 3200.00 | 156800.00 | 4900.00 | RANJIT SALES CORPORATION
6.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level.Thermo-Mechanically Treated bars of grade Fe-415 or more | 2502.00 | Kg | 64.00 | 100.00 | 250200.00 | 55.00 | 137610.00 | 55.00 | 137610.00 | 81.00 | 202662.00 | 67.00 | 167634.00 | 85.00 | 212670.00 | 60.00 | 150120.00 | 70.00 | 175140.00 | 68.00 | 170136.00 | 64.75 | 162004.50 | 50.00 | 125100.00 | 88.00 | 220176.00 | 75.00 | 187650.00 | 125100.00 | RANJIT SALES CORPORATION
7.00 | Supply of high pressure die-cast aluminium / Standard alloy housing having system lumens output not less than 4950 lumens and system efficacy not less than 110 lumens / watt 45 Watt (Max) road way/ street light fitting i/c necessary electronic driver, LED lamps suitable to operate on 230V ac power supply with connector etc as per tender specifications complete as required. | 384.00 | Each | 3136.05 | 2000.00 | 768000.00 | 1870.00 | 718080.00 | 1550.00 | 595200.00 | 1636.00 | 628224.00 | 3200.00 | 1228800.00 | 1450.00 | 556800.00 | 2000.00 | 768000.00 | 1955.00 | 750720.00 | 2070.00 | 794880.00 | 1305.00 | 501120.00 | 800.00 | 307200.00 | 1450.00 | 556800.00 | 1800.00 | 691200.00 | 307200.00 | RANJIT SALES CORPORATION
8.00 | Installation, testing & Commissioning of LED street light fitting on existing pole,supplying and drawing 3 X 2.5sq.m PVC insulated copper couductor single core cable in the pole from fitting to MCB including connection testing and commissioning as required | 384.00 | Each | 354.00 | 500.00 | 192000.00 | 176.00 | 67584.00 | 65.00 | 24960.00 | 467.00 | 179328.00 | 1000.00 | 384000.00 | 250.00 | 96000.00 | 250.00 | 96000.00 | 200.00 | 76800.00 | 350.00 | 134400.00 | 462.50 | 177600.00 | 500.00 | 192000.00 | 236.00 | 90624.00 | 950.00 | 364800.00 | 24960.00 | jaydeep agency corporation
9.00 | Supply of following sizes XLPE insulated & PVC sheathed,1.1 KV grade, aluminium conductor, armoured power cable confirming to IS: 7098, Part-1/1988 with upto date amendments
9.01 | 3½ X 240 sq. mm | 500.00 | Meter | 634.20 | 580.00 | 290000.00 | 631.00 | 315500.00 | 845.00 | 422500.00 | 765.00 | 382500.00 | 350.00 | 175000.00 | 900.00 | 450000.00 | 730.00 | 365000.00 | 600.00 | 300000.00 | 790.00 | 395000.00 | 614.00 | 307000.00 | 600.00 | 300000.00 | 597.00 | 298500.00 | 735.00 | 367500.00 | 175000.00 | M/S AMAR ENTERPRISES
9.02 | 3½ X 185 sq. mm | 11000.00 | Meter | 516.00 | 480.00 | 5280000.00 | 484.00 | 5324000.00 | 655.00 | 7205000.00 | 612.00 | 6732000.00 | 310.00 | 3410000.00 | 550.00 | 6050000.00 | 600.00 | 6600000.00 | 500.00 | 5500000.00 | 594.00 | 6534000.00 | 495.00 | 5445000.00 | 400.00 | 4400000.00 | 472.00 | 5192000.00 | 550.00 | 6050000.00 | 3410000.00 | M/S AMAR ENTERPRISES
9.03 | 4 X25 sq. mm | 12800.00 | Meter | 114.60 | 115.00 | 1472000.00 | 107.00 | 1369600.00 | 187.00 | 2393600.00 | 140.00 | 1792000.00 | 153.00 | 1958400.00 | 140.00 | 1792000.00 | 118.00 | 1510400.00 | 107.00 | 1369600.00 | 140.00 | 1792000.00 | 107.00 | 1369600.00 | 80.00 | 1024000.00 | 111.00 | 1420800.00 | 126.00 | 1612800.00 | 1024000.00 | RANJIT SALES CORPORATION
10.00 | Supply of following sizes HDPE pipe as per specification enclosed in tender document etc. as required.
10.01 | 90 mm dia DWC HDPE pipe Conforming IS- 16205 part 24 / IS 14930 part -II | 11010.00 | Meter | 190.00 | 80.00 | 880800.00 | 82.00 | 902820.00 | 98.00 | 1078980.00 | 84.00 | 924840.00 | 40.00 | 440400.00 | 75.00 | 825750.00 | 115.00 | 1266150.00 | 80.00 | 880800.00 | 98.00 | 1078980.00 | 83.00 | 913830.00 | 120.00 | 1321200.00 | 66.00 | 726660.00 | 140.00 | 1541400.00 | 440400.00 | M/S AMAR ENTERPRISES
10.02 | 40 mm dia PLB HDPE Pipes Conforming TEC specification (OD 40mm ID 33mm). | 12852.00 | Meter | 49.95 | 70.00 | 899640.00 | 50.00 | 642600.00 | 72.00 | 925344.00 | 61.00 | 783972.00 | 40.00 | 514080.00 | 55.00 | 706860.00 | 75.00 | 963900.00 | 40.00 | 514080.00 | 62.00 | 796824.00 | 55.00 | 706860.00 | 100.00 | 1285200.00 | 35.00 | 449820.00 | 54.00 | 694008.00 | 449820.00 | Surya Roshni Limited
11.00 | Laying the following sizes HDPE pipe including digging the earth in such a way that the top of pipe shall not be less than 750 mm below to ground level and refilling with excavated soil etc. Complete as required. Job also includes the interconnection of HDPE pipes with standard accessories, connection etc. as required.
11.01 | 90 mm dia | 11010.00 | Meter | 78.00 | 50.00 | 550500.00 | 55.00 | 605550.00 | 22.00 | 242220.00 | 81.00 | 891810.00 | 30.00 | 330300.00 | 70.00 | 770700.00 | 70.00 | 770700.00 | 50.00 | 550500.00 | 77.00 | 847770.00 | 75.00 | 825750.00 | 80.00 | 880800.00 | 121.00 | 1332210.00 | 135.00 | 1486350.00 | 242220.00 | jaydeep agency corporation
11.02 | 40 mm dia | 12852.00 | Meter | 78.00 | 40.00 | 514080.00 | 55.00 | 706860.00 | 18.00 | 231336.00 | 68.00 | 873936.00 | 30.00 | 385560.00 | 50.00 | 642600.00 | 70.00 | 899640.00 | 50.00 | 642600.00 | 67.00 | 861084.00 | 75.00 | 963900.00 | 100.00 | 1285200.00 | 99.00 | 1272348.00 | 135.00 | 1735020.00 | 231336.00 | jaydeep agency corporation
12.00 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/ HDPE pipe as required.
12.01 | upto 35 sq. mm | 12800.00 | Meter | 22.00 | 30.00 | 384000.00 | 33.00 | 422400.00 | 18.00 | 230400.00 | 27.00 | 345600.00 | 30.00 | 384000.00 | 27.00 | 345600.00 | 20.00 | 256000.00 | 20.00 | 256000.00 | 26.00 | 332800.00 | 31.25 | 400000.00 | 80.00 | 1024000.00 | 38.00 | 486400.00 | 50.00 | 640000.00 | 230400.00 | jaydeep agency corporation
12.02 | Above 95 sq. mm and upto 185 sq. mm | 11000.00 | Meter | 44.00 | 40.00 | 440000.00 | 55.00 | 605000.00 | 25.00 | 275000.00 | 81.00 | 891000.00 | 30.00 | 330000.00 | 37.00 | 407000.00 | 35.00 | 385000.00 | 40.00 | 440000.00 | 41.00 | 451000.00 | 50.00 | 550000.00 | 120.00 | 1320000.00 | 66.00 | 726000.00 | 70.00 | 770000.00 | 275000.00 | jaydeep agency corporation
12.03 | Above 185 sq. mm and upto 400 sq. mm | 200.00 | Meter | 77.00 | 50.00 | 10000.00 | 88.00 | 17600.00 | 38.00 | 7600.00 | 136.00 | 27200.00 | 30.00 | 6000.00 | 50.00 | 10000.00 | 40.00 | 8000.00 | 70.00 | 14000.00 | 62.00 | 12400.00 | 68.75 | 13750.00 | 120.00 | 24000.00 | 110.00 | 22000.00 | 70.00 | 14000.00 | 6000.00 | M/S AMAR ENTERPRISES
13.00 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
13.01 | Above 185 sq. mm and upto 400 sq. mm | 300.00 | Meter | 65.00 | 70.00 | 21000.00 | 88.00 | 26400.00 | 40.00 | 12000.00 | 136.00 | 40800.00 | 50.00 | 15000.00 | 60.00 | 18000.00 | 20.00 | 6000.00 | 60.00 | 18000.00 | 102.00 | 30600.00 | 81.25 | 24375.00 | 120.00 | 36000.00 | 440.00 | 132000.00 | 70.00 | 21000.00 | 6000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
14.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 grade as required.
14.01 | 31/2 x 240 Sq. mm. | 4.00 | Set | 717.00 | 800.00 | 3200.00 | 1320.00 | 5280.00 | 870.00 | 3480.00 | 3094.00 | 12376.00 | 1500.00 | 6000.00 | 1000.00 | 4000.00 | 800.00 | 3200.00 | 700.00 | 2800.00 | 1230.00 | 4920.00 | 990.50 | 3962.00 | 60.00 | 240.00 | 1648.00 | 6592.00 | 3600.00 | 14400.00 | 240.00 | RANJIT SALES CORPORATION
14.02 | 31/2 x 185 Sq. mm. | 14.00 | Set | 621.00 | 600.00 | 8400.00 | 1100.00 | 15400.00 | 740.00 | 10360.00 | 2714.00 | 37996.00 | 1000.00 | 14000.00 | 850.00 | 11900.00 | 650.00 | 9100.00 | 600.00 | 8400.00 | 1130.00 | 15820.00 | 739.00 | 10346.00 | 150.00 | 2100.00 | 1099.00 | 15386.00 | 3600.00 | 50400.00 | 2100.00 | RANJIT SALES CORPORATION
14.03 | 4 X 25 Sq.mm | 782.00 | Set | 221.00 | 200.00 | 156400.00 | 242.00 | 189244.00 | 120.00 | 93840.00 | 81.00 | 63342.00 | 200.00 | 156400.00 | 350.00 | 273700.00 | 210.00 | 164220.00 | 150.00 | 117300.00 | 360.00 | 281520.00 | 184.50 | 144279.00 | 20.00 | 15640.00 | 110.00 | 86020.00 | 1510.00 | 1180820.00 | 15640.00 | RANJIT SALES CORPORATION
15.00 | Supplying and making straight through joint with cast resin compound ferrules and other jointing materials for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 grade as required.
15.01 | 31/2 x 185 Sq. mm. | 8.00 | Each | 4927.00 | 2500.00 | 20000.00 | 8800.00 | 70400.00 | 1850.00 | 14800.00 | 7328.00 | 58624.00 | 5000.00 | 40000.00 | 3000.00 | 24000.00 | 2500.00 | 20000.00 | 5000.00 | 40000.00 | 6000.00 | 48000.00 | 12549.00 | 100392.00 | 1500.00 | 12000.00 | 2198.00 | 17584.00 | 3000.00 | 24000.00 | 12000.00 | RANJIT SALES CORPORATION
16.00 | Earthing with G. I. pipe 4.5 m long x 40 mm dia. including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. ( with charcoal or coke and salt) complete as required. | 48.00 | Set | 4700.00 | 4500.00 | 216000.00 | 8800.00 | 422400.00 | 2350.00 | 112800.00 | 5428.00 | 260544.00 | 6000.00 | 288000.00 | 4000.00 | 192000.00 | 3500.00 | 168000.00 | 5000.00 | 240000.00 | 8800.00 | 422400.00 | 6130.00 | 294240.00 | 2000.00 | 96000.00 | 5055.00 | 242640.00 | 3500.00 | 168000.00 | 96000.00 | RANJIT SALES CORPORATION
17.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 24300.00 | Meter | 32.00 | 20.00 | 486000.00 | 11.00 | 267300.00 | 15.00 | 364500.00 | 14.00 | 340200.00 | 34.00 | 826200.00 | 18.00 | 437400.00 | 15.00 | 364500.00 | 25.00 | 607500.00 | 15.00 | 364500.00 | 13.25 | 321975.00 | 12.00 | 291600.00 | 11.00 | 267300.00 | 12.00 | 291600.00 | 267300.00 | Surya Roshni Limited, RVD INFRA SOLUTION PVT.LTD.
18.00 | Feeder pillars of perimeters light PTTA TYPE PANEL Design, Manufacture, Supplying, Transport to the site, Receiving, Unloading, Shifting to various locations, handling, assembling, installation in correct aligned position, grouting with dash fasteners,GI nuts-bolts,testing and commissioning of the following fabricated in compartmentalize conformto IS: 8623/1993, Suitable for 415V, 3Phase,4Wire 50Hz Ac supply, are housedin CRCA sheet steel of 2mm thick for frame workand covers, 3mm thick for gland plate, bottom base l of Size 50 x 50 x 6 mm MS angle for base with front & back side hinged door with locking arrangement for MDB/MCC and SDBs etc., including cleaning & finishing complete, SMC bus bar supports, with short circuit with stand capacity of 36kA for 1 Sec., fabrication shall be done in transportable sections and all front and backdoors shall be hinged type and earth with frame, Entire panel shall have a Aluminium contineous earth bar of size 50mm x 6mm or as specified below at the rear with 2 Nos. earth stud at each side, inter connections bus bar to switch gears upto cable alley, bus bars and control wiring with suitable size of FRLS PVC insulated copper conductor cable, able alleys, cable gland plate in two half, including providing following switch gears:- The Bus bars will be Copper purity 99.9%/ electrolyticgrade E91 Alumunium duly sleeved with Helogen Free heat shrink coloured Insulated tube confirming to IEC 6068-3-247 Standard. Provide electrical insulating shrouds, reusable type covers for bus bars Bootson corners. Panels will be powder coating (60-80 microns per Is:13871 for indoor and 90-100 micronfor outdoor), include one size higher terminal block in cable alley and interconnecting wires between bus bars and terminals via MCB/MCCB rating 100A. All Bus-Bar alley and relay compartments shall be provided with fully automatic control thermotate with strip heater. SITC of outdoor type double door feeder pillar made of 2 mm thick CRCA sheet steel duly epoxy powder coated (by seven tank process ), 50 x 50 x 6 mm MS angle for base with front & back side hinged door with locking arrangement, providing necessary brick foundation, painting etc. and fixing the following switchgears i/c interconnections etc. suitable to connect Incomer cable size minimum 3.5 x 185 sq.mm and ougoings of 3.5 x 185 sq.mm, 4 x 25sq.mm cable complete as required. a) 100 amps, TPN, Aluminium busbars with insulation. b) Incomer : 4 - pole, 63amp. MCCB , 25 KA , -- 01 No. (c) Outgoings : 4 - pole, 63 amp. MCCB , 25 KA , -- 1no. TPN, 25 amp. MCB -- 02 nos. e) 70 Amp, AC3, 3 pole, power contactor, coil voltage 240 V, 2NO + 2NC, ML 4, ---1no. f) Day Time Switch - 1no. g) Toggle switch for auto manual - 1no. h) Lamp holder - 1 no. i) 5A switch - 1 no. j) 5/15A socket with switch - 1 no. k) RYB Indication lamp at I/cs and On indication lamp at each I/C, B/C and O/Gs. | 7.00 | Job | 81886.00 | 90000.00 | 630000.00 | 82500.00 | 577500.00 | 155500.00 | 1088500.00 | 181832.00 | 1272824.00 | 85500.00 | 598500.00 | 125000.00 | 875000.00 | 100000.00 | 700000.00 | 90000.00 | 630000.00 | 93000.00 | 651000.00 | 51092.00 | 357644.00 | 15000.00 | 105000.00 | 47253.00 | 330771.00 | 48000.00 | 336000.00 | 105000.00 | RANJIT SALES CORPORATION
19.00 | Main outdoor LT Panel for Feeder pillars of perimeters light (PTTA Type) Supply, installation, testing & commissioning of outdoor cubicle type compartmentalized floor mounted free standing with separation system for 415V, 50HZ, 3phase 4 wire AC supply, moisture, dust and vermin proof IP-65, including extra canopy on MS frame for protection from rain, L.T.Panel boards, made out from 2mm thick CRCA sheet steel duly epoxy powder coated (by seven tank process ) in approved colour, complete with interconnections / control/ power wiring with FRLS copper conductor wires & 2A SP MCBs for control circuits ,communicable meters shall be with software, high conductivity Aluminium bus bars, earth bus,Bus bar supports, removable 3mm thick gland plates on top & bottom, M.V. danger notice plate , louvers and following incomer and outgoing feeders (outgoings will be with ON indication with 2A control MCB) complete as per specifications and drawings suitable to connect Incomer cable size minimum 3.5 x 240 sq.mm and ougoings of 3.5 x 185 sq.mm cable complete as required. INCOMER 250 A, 4 pole 35/36kA MCCB with thermal magnetic based protection release ( O/L, S/C & E/F) , extended rotary handle mechanism, 3N0s.250A CTs,1 no. CT operated digital Multifunction meter with minimum main parameters like (V,A,Hz, Pf, KW, KWH,MD) & communication port & software, selector switch, control MCBs. 3- Nos. Phase & ON-OFF indicating LED lights with control MCBs - 2Set. BUSCOUPLER 250 A, 4-pole 35/36kA MCCB without protection , extended rotary handle mechanisim, ON-OFF indicating LED lights with control MCBs - 1Set Mechanical Lock with KEY for incomers & bus coupler MCCBs interlocking- 3 Sets Electrical interlocking for incomers & bus coupler MCCBs interlocking- 3 Sets BUS BAR - 300A, 415V three Phase 4 wire, four equal rateing colour coded, non-adhesive PVC insulated electrolytic 'Al' conductor bus bars OUTGOINGS 100 A, FP MCCB, 35kA MCCB thermal magnetic based protection release with extended rotary handle mechanism, ON LED indicating light with suitable control MCB - 08 Set | 1.00 | Job | 403621.00 | 180000.00 | 180000.00 | 220000.00 | 220000.00 | 401500.00 | 401500.00 | 485796.00 | 485796.00 | 494453.00 | 494453.00 | 195000.00 | 195000.00 | 250000.00 | 250000.00 | 400000.00 | 400000.00 | 238000.00 | 238000.00 | 317911.00 | 317911.00 | 25206.00 | 25206.00 | 283516.00 | 283516.00 | 245000.00 | 245000.00 | 25206.00 | RANJIT SALES CORPORATION
20.00 | Constructing brick masonary manhole chamber of min dimension inside 750mm(L)x750mm(W)x900mm(D) with medium class bricks in cement mortar 1:4 (1 Cement: 4 Coarse Sand) R.C.C top slab with mix 1:2:4 Cement Concrete (1 Cement: 2 Coarse Sand: 4 Graded Stone agreegate 20 mm nominal size), inside and exposed outside plastering 12 mm thick with cement mortar 1:4 (1 Cement: 4 Coarse Sand) including putting the RCC trench cover to the chamber etc. complete as required. | 50.00 | Each | 10000.00 | 10000.00 | 500000.00 | 605.00 | 30250.00 | 4950.00 | 247500.00 | 4071.00 | 203550.00 | 7000.00 | 350000.00 | 12250.00 | 612500.00 | 3000.00 | 150000.00 | 12000.00 | 600000.00 | 6700.00 | 335000.00 | 4375.00 | 218750.00 | 1600.00 | 80000.00 | 6044.00 | 302200.00 | 4500.00 | 225000.00 | 30250.00 | RVD INFRA SOLUTION PVT.LTD.
21.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 50.00 | Each | 509.00 | 100.00 | 5000.00 | 385.00 | 19250.00 | 245.00 | 12250.00 | 271.00 | 13550.00 | 300.00 | 15000.00 | 500.00 | 25000.00 | 500.00 | 25000.00 | 1000.00 | 50000.00 | 520.00 | 26000.00 | 423.00 | 21150.00 | 1400.00 | 70000.00 | 291.00 | 14550.00 | 1500.00 | 75000.00 | 5000.00 | DOSHI ELECTRIC ENGG. CO.
| Total in Figures |  |  |  |  | 17742345.00 |  | 15575413.00 |  | 18934900.00 |  | 20691349.00 |  | 17679547.00 |  | 20461980.00 |  | 18438580.00 |  | 16904740.00 |  | 20002017.00 |  | 16925315.00 |  | 16707786.00 |  | 18179102.00 |  | 21914348.00
Lowest Amount Quoted BY: RVD INFRA SOLUTION PVT.LTD.(15575413.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Perimeter Road Lighting at AAI, Deoghar Airport. Tender ID: 2020_AAI_58893_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RVD INFRA SOLUTION PVT.LTD. | 15575413.00 | L1
| 2 | RANJIT SALES CORPORATION | 16707786.00 | L2
| 3 | GIRI ENTERPRISES | 16904740.00 | L3
| 4 | HPL Electric and Power Limited | 16925315.00 | L4
| 5 | M/S AMAR ENTERPRISES | 17679547.00 | L5
| 6 | DOSHI ELECTRIC ENGG. CO. | 17742345.00 | L6
| 7 | Surya Roshni Limited | 18179102.00 | L7
| 8 | Choubay And Co.(Agencies) Pvt.Ltd. | 18438580.00 | L8
| 9 | jaydeep agency corporation | 18934900.00 | L9
| 10 | instapower ltd | 20002017.00 | L10
| 11 | RASS CONTRACTOR AND ENGINEERS | 20461980.00 | L11
| 12 | TRANSRAIL LIGHTING LIMITED | 20691349.00 | L12
| 13 | M/S Jagdish Singh Enterprises | 21914348.00 | L13