## BoQ1
Government eProcurement System Created By: K SANTHOSH KUMAR Created Date/Time: 06-Nov-2020 12:39 PM Tender Title: AMC of Water Treatment for AC Plant Tender ID: 2020_AAI_58961_1
Tender Inviting Authority: Asstt. Gen. Mgr. (E-E), NATS Complex, IGI Airport, New Delhi
Name of Work : AMC of Water Treatment for AC plant for 02 Yrs at NATS Complex, IGI Airport, New Delhi (2020-22).
Contract No/Tender ID : 2020_AAI_58961_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CLEANFLO INDIA PRIVATE LIMITED(GSTN-07AAACD2211P2ZS) |  | Ess Kay Engineers(GSTN-07AJJPK0766F1Z8)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | 1. Regeneration of salt 200 kg per softener is required approx three times in a month to meet the required parameters of hardness for (2x 120 TR)& (2x250 TR) central A/C plant i/c providing of commercial salt as given below for each regeneration, testing of hardness of water etc. complete as reqd at site & as specified. | 60.00 | Job | 100.00 | 2500.00 | 150000.00 | 4000.00 | 240000.00 | 150000.00 | CLEANFLO INDIA PRIVATE LIMITED
2.00 | 2. Supply & pouring of chemical minimum 0.6 kg/day or as required for each Chiller for prevention of scale in the cooling tower, pipe line and condenser unit to meet the parameter as per site water condition. The chemical must have dispersant and HSP and work upto 250 PPM hardness. The chemical shall be dosed on daily basis. (Make : NALCO - 7401 or its similar specification in venza/Aquachem/ ION Exchange/ GE/ Thermax). | 504.00 | Kg | 100.00 | 205.00 | 103320.00 | 60.00 | 30240.00 | 30240.00 | Ess Kay Engineers
3.00 | 3. Supply & pouring of chemical minimum 0.5 kg/day or as required for each Chiller for prevention of corrosion in the cooling tower, pipe line and condenser unit to meet the required parameters as per site water condition. The chemical must have corrosion inhibitor PSO for effective anodic & chathodic protection.The chemical shall be dosed on daily basis. (Make : NALCO - 1393 or its similar specification in venza/Aquachem/ ION Exchange/ GE/ Thermax). | 420.00 | Kg | 10.00 | 190.00 | 79800.00 | 75.00 | 31500.00 | 31500.00 | Ess Kay Engineers
4.00 | 4. Supply & pouring of chemical 0.2 kg/day for each C.Tower bio dispersant for prevention of algae in the cooling tower.The chemical shall be dosed on daily basis. (Make : NALCO - 7308 or its similar specification in venza/Aquachem/ ION Exchange/ GE/ Thermax). | 292.00 | Kg | 10.00 | 125.00 | 36500.00 | 76.00 | 22192.00 | 22192.00 | Ess Kay Engineers
5.00 | 5. Supply & pouring of chemical 4 kg/week for each C.Tower Non-Oxidizing biocide for prevention of micro organisms in the cooling tower as per site water condition. The chemical shall be dosed on weekly basis. (Make : NALCO - 2593 or its similar specification in venza/Aquachem/ ION Exchange/ GE/ Thermax). | 360.00 | Kg | 100.00 | 185.00 | 66600.00 | 80.00 | 28800.00 | 28800.00 | Ess Kay Engineers
6.00 | 6. Supply & pouring of chemical 4 Kg/day for each C.Tower Oxidizing biocide for prevention of micro organisms in the cooling tower as per site water condition.The chemical shall be dosed on daily basis. (Make : NALCO - 3935 or its similar specification in venza/Aquachem/ ION Exchange/ GE/ Thermax). | 360.00 | Kg | 10.00 | 70.00 | 25200.00 | 15.00 | 5400.00 | 5400.00 | Ess Kay Engineers
7.00 | 7. Supply & pouring of chemical 1 kg/day for each Chiller Alkanity reducer to control pH within control limits. The chemical shall be dosed on daily basis. (Make : NALCO - 70895 or its similar specification in venza/Aquachem/ ION Exchange/ GE/ Thermax). | 1320.00 | Kg | 10.00 | 65.00 | 85800.00 | 30.00 | 39600.00 | 39600.00 | Ess Kay Engineers
8.00 | 8. Supply & pouring of chemical for corrosion inhibitor in the chiller pipe line circuit as per site water condition. Initial dosing (Minimum 160 Kgs) and subsequent dozing 10 Kg per month (Minimum) till the chemical achieve the nitrite product residual range 600-800 PPM. (Make : NALCO - TRAC 109 or its similar specification in venza/Aquachem/ ION Exchange/ GE/ Thermax). | 800.00 | Kg | 100.00 | 175.00 | 140000.00 | 75.00 | 60000.00 | 60000.00 | Ess Kay Engineers
9.00 | 9. Supply & pouring of chemical 8 Kg per month for prevention of micro-organism in the chiller pipe line circuit. The chemical shall be dosed on daily basis. (Make : NALCO - 2593 or its similar specification in venza/Aquachem/ ION Exchange/ GE/ Thermax). | 192.00 | Kg | 10.00 | 198.00 | 38016.00 | 100.00 | 19200.00 | 19200.00 | Ess Kay Engineers
10.00 | 10. Replacement of INDION NA 220 resin (i/c supply) for softening plant as and when required and as per direction of E-I-C.
10.01 | (a) Plant No. 1 | 1300.00 | Ltrs | 10.00 | 180.00 | 234000.00 | 130.00 | 169000.00 | 169000.00 | Ess Kay Engineers
10.02 | (b) Plant No. 2 | 1300.00 | Ltrs | 100.00 | 180.00 | 234000.00 | 130.00 | 169000.00 | 169000.00 | Ess Kay Engineers
11.00 | 11. Replacement of top filter section along with the necessary fitting (i/c supply) suitable for the softening plant (Make: Pentair Water,.Size:4872-6''T/6"B & Volume:1840 litres) at site i/c labour(as & when required) as per satisfaction of E-I-C. | 2.00 | Job | 100.00 | 38150.00 | 76300.00 | 5000.00 | 10000.00 | 10000.00 | Ess Kay Engineers
12.00 | 12. Replacement of bottom filter section along with the necessary fitting (i/c supply) suitable for the softening plant (Make: Pentair Water,Size:4872-6''T/6"B & Volume:1840 litres) at site i/c labour (as & when required)as per satisfaction of E-I-C. | 2.00 | Job | 10.00 | 38150.00 | 76300.00 | 5000.00 | 10000.00 | 10000.00 | Ess Kay Engineers
| Total in Figures |  |  |  |  | 1345836.00 |  | 834932.00
Lowest Amount Quoted BY: Ess Kay Engineers(834932.00)

## BOQ Summary
BOQ Summary Details Tender Title: AMC of Water Treatment for AC Plant Tender ID: 2020_AAI_58961_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Ess Kay Engineers | 834932.00 | L1
| 2 | CLEANFLO INDIA PRIVATE LIMITED | 1345836.00 | L2