## BoQ1
Government eProcurement System Created By: Manish Asawa Created Date/Time: 07-Dec-2020 05:53 PM Tender Title: SITC for Integrated Surge Protection and Equipment bonding for CNS units at AAI, Civil Aerodrome, Rajkot Tender ID: 2020_AAI_59046_1
Tender Inviting Authority: The Airport Director, Airports Autority of India, Civil Aerodrome, Rajkot.
Name of Work: “SITC for Integrated Surge Protection and Equipment bonding for CNS units at AAI, Civil Aerodrome, Rajkot”.
Contract No: AAI/RAJ/CNS/SPD/2020-21 , E-Tender ID: 2020_AAI_59046_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Secom Services India Pvt.Ltd(GSTN-NA) |  | UNEX POWER POINT PVT.LTD(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.01 | Primary Surge Protection: Supply, Installation, testing and commissioning of 100 kA, 3 phase Surge Divertor with neutral protection using single block metal oxide varistor in pre-wired IP55 grade metal enclosure with voltage protection level < 1.5 KV shall be provided on the mains power entry point in compliance with IEC 61643/IEEE C62.41/ASNZ 1768/ANSI Standards complete with sensing circuit, potential free contacts, necessary indications and alarm for Essential / non essential Panel. To be connected in parallel at the essential / non essential panel of following locations: 1. Technical building 1st floor- 1 No. 2. S CCTV- Ground floor-1 No. 3. NDB - 1 No. | 3.00 | Each | 0.00 | 112500.00 | 337500.00 | 110500.00 | 331500.00 | 331500.00 | UNEX POWER POINT PVT.LTD
1.02 | SECONDERY PROTECTION: Supply of Multi Stage Series Power Filter (MSSPF) 125 Amps 3 Phase, 4 wire with neutral protection and built in MOV based surge diverter of 40kA at Input and 40kA rating at load side prewired in IP55 grade Powder coated metal enclosure with 125Amps MCB, service change over switch, complete with sensing circuit, potential free contacts and necessary indicators and alarms connected in series with UPS input in following locations. 1. Automation for 4 nos. of 10 KVA UPS. 2. Equipment Room - 4 x 3KVA UPS. 3. VCCS Room- 2x3 KVA UPS. 4. DVR room - 2x3KVA UPS. 5. DATIS - 2x2KVA UPS. | 2.00 | Each | 0.00 | 206850.00 | 413700.00 | 204000.00 | 408000.00 | 408000.00 | UNEX POWER POINT PVT.LTD
1.03 | SECONDERY PROTECTION: Supply of Multi Stage Series Power Filter (MSSPF) 63 Amps 3 Phase, 4 wire with neutral protection and built in MOV based surge diverter of 40kA at Input and 40kA rating at load side prewired in IP55 grade Powder coated metal enclosure with 63Amps MCB, service change over switch, complete with sensing circuit, potential free contacts and necessary indicators and alarms connected in series with 10 KVA x 2UPS input in following locations. 1. SCCTV for 2 Nos of 10 KVA UPS. | 1.00 | Each | 0.00 | 172500.00 | 172500.00 | 170850.00 | 170850.00 | 170850.00 | UNEX POWER POINT PVT.LTD
1.04 | SECONDERY PROTECTION: Supply of Multi Stage Series Power Filter (MSSPF) 32 Amps 1 Phase, 2 wire with neutral protection and built in MOV based surge diverter of 40kA at Input and 25kA rating at load side prewired in IP55 grade Powder coated metal enclosure with 32Amps MCB, service change over switch, complete with sensing circuit, potential free contacts and necessary indicators and alarms connected in series with 2 KVA x 2 UPS input in following locations. 1. NDB- for 2 Nos of 2 KVA UPS. | 1.00 | Each | 0.00 | 94850.00 | 94850.00 | 93750.00 | 93750.00 | 93750.00 | UNEX POWER POINT PVT.LTD
1.05 | EQUIPMENT LEVEL PROTECTION :- Supply of 120KA. Surge protection device against the protection from Noises, ESD, EPR and abnormal electrical characteristics which enter from power and other service lines and ensuring clear bonding potential (earth to Neutral voltage) less than 1.0V to be connected in parallel to the circuit, Confirming to CE, tested and certified as per latest certification (IEC- 61643-1, IEC-61000-4-5, IEC-61000-6-1, IEC61000-6-3) in Pre-wired metal enclosure with pulverulent body painting including all accessories. 1. Automation -2 Nos. 2. SCCTV - 1 No. 3. Equipment Room -2 Nos. 4. VCCS -1 No. 5. DVR - 1 No. 6. DATIS -1 No. 7. NDB - 1 No. | 9.00 | Each | 0.00 | 245000.00 | 2205000.00 | 242000.00 | 2178000.00 | 2178000.00 | UNEX POWER POINT PVT.LTD
1.06 | Supply of Earth Bonding water proof junction Box. | 3.00 | Each | 0.00 | 16200.00 | 48600.00 | 16000.00 | 48000.00 | 48000.00 | UNEX POWER POINT PVT.LTD
1.07 | Supply of 35 Sq.mm copper flexible wire for earth bonding (ISI Marked). Purity > 95%. | 100.00 | Each | 0.00 | 475.00 | 47500.00 | 472.00 | 47200.00 | 47200.00 | UNEX POWER POINT PVT.LTD
1.08 | Supply of 16 Sq.mm copper flexible wire for equipment bonding (ISI Marked). Purity > 95%. | 200.00 | Each | 0.00 | 252.00 | 50400.00 | 250.00 | 50000.00 | 50000.00 | UNEX POWER POINT PVT.LTD
1.09 | Supply of 10 Sq.mm copper flexible wire for equipment bonding (ISI Marked). Purity > 95%. | 200.00 | Each | 0.00 | 172.00 | 34400.00 | 170.00 | 34000.00 | 34000.00 | UNEX POWER POINT PVT.LTD
1.10 | Supply of 40mm or suitable dia B class GI Pipe for laying cable in surface. | 100.00 | Each | 0.00 | 570.00 | 57000.00 | 568.00 | 56800.00 | 56800.00 | UNEX POWER POINT PVT.LTD
1.11 | Refurbishing of earthing at Technical building and NDB. | 8.00 | Each | 0.00 | 8200.00 | 65600.00 | 8000.00 | 64000.00 | 64000.00 | UNEX POWER POINT PVT.LTD
1.12 | Supply, Installation, testing and commissioning with accessories for item No. 1 to 11. | 1.00 | Each | 0.00 | 330500.00 | 330500.00 | 300000.00 | 300000.00 | 300000.00 | UNEX POWER POINT PVT.LTD
| Total in Figures |  |  |  |  | 3857550.00 |  | 3782100.00
Lowest Amount Quoted BY: UNEX POWER POINT PVT.LTD(3782100.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC for Integrated Surge Protection and Equipment bonding for CNS units at AAI, Civil Aerodrome, Rajkot Tender ID: 2020_AAI_59046_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | UNEX POWER POINT PVT.LTD | 3782100.00 | L1
| 2 | Secom Services India Pvt.Ltd | 3857550.00 | L2