## BoQ1
Government eProcurement System Created By: DOMA JAWALEKAR Created Date/Time: 11-Dec-2020 05:31 PM Tender Title: Provision of UPS for GLF System at Aurangabad Airport. Tender ID: 2020_AAI_59888_1
Tender Inviting Authority: Asstt. Gen.Manager (Engg.-Electrical), Airports Authority of India, Aurangabad Airport, Aurangabad - 431007 (Maharashtra).
Name of Work: Provision of UPS for GLF System at Aurangabad Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Novateur Electrical and Digital Systems Private Limited(GSTN-33AACCE4671N1ZF) |  | ECS ENGINEERING PVT LTD(GSTN-09AABCE5944P1Z1) |  | RS Power Systems Pvt. Ltd.(GSTN-08AAICR2572F1ZA) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing , Commissioning, Transportion, Unloading of true online floor mounted UPS with minimum 120 KVA capacity, 3 phase in and 3 Phase out , with two distinct Earthing terminal , double conversion IGBT three level PWM technology, in built isolation transformer suitable to drive constant current regulators with 100% unbalanced load at output at full load condition as per technical specifications/data sheet enclosed. The UPS shall have standard features like in built automatic 100% rated static by pass, maintenance by pass, Cooling fan should be redundant so as to maintained required CFM if one of the fans failed, inrush current of UPS should be limited by soft start circuit to full load current, active input power factor correction, phase sequence corrector, pure sine wave output, input-output isolation, live part internally shrouded, compatibility with generator supply, cold start capability,common battery bank facility in case one UPS battery banks failed, inbuilt static back feed protection, EMI/RFI noise filter, advanced communication-RS485 port, SNMP card, user friendly LCD display, provision of auto load sharing / parallel operation, suitable to operate at 415V, 50Hz, 3 Phase AC supply and delivering 2 phase & single phase loads with 3 phase output of the UPS and necessary safety protection. The job also includes supply and connecting the suitable required number of SMF batteries of suitable amp hour, for each UPS separately/Individually to give a backup time of minimum 30 minutes for each UPS separately/Individually at the rated full load along with battery management feature integrated with UPS, battery rack of metallic frame of stainless steel of epoxy coated metal for acid resistance, connectors, wiring, cabling between battery bank and UPS with insulated copper conductor of required size, termination, along with supply and laying of insulation Mats of 2 mm thickness poly-synthetic mats/ 12mm rubber mats for UPS front & Backside matching UPS width and around the battery racks as per site condition etc. complete as required. | 1.00 | Job |  | 2977000.00 | 2977000.00 | 3085000.00 | 3085000.00 | 3220400.00 | 3220400.00 | 2841000.00 | 2841000.00 | 2841000.00 | Awasthi Electric Works
2.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. 225 mm width X 50 mm depth X 1.6 mm thickness. | 100.00 | Meter |  | 1150.00 | 115000.00 | 618.00 | 61800.00 | 533.00 | 53300.00 | 625.00 | 62500.00 | 53300.00 | RS Power Systems Pvt. Ltd.
3.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required 225 mm width X 50 mm depth X 1.6 mm thickness. | 20.00 | Each |  | 1265.00 | 25300.00 | 718.00 | 14360.00 | 572.00 | 11440.00 | 1150.00 | 23000.00 | 11440.00 | RS Power Systems Pvt. Ltd.
4.00 | Supply of 1 core , 95 sq.mm , XLPE insulated, armoured, copper conductor cable of 1.1 KV grade confirming to IS - 7098 (part-I) 1988 with upto date ammendements as required. | 800.00 | Meter |  | 1006.00 | 804800.00 | 900.00 | 720000.00 | 817.00 | 653600.00 | 929.00 | 743200.00 | 653600.00 | RS Power Systems Pvt. Ltd.
5.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp). | 800.00 | Meter |  | 86.00 | 68800.00 | 40.00 | 32000.00 | 93.50 | 74800.00 | 65.00 | 52000.00 | 32000.00 | ECS ENGINEERING PVT LTD
6.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 95 sq. mm (38mm). | 8.00 | Set |  | 2125.00 | 17000.00 | 250.00 | 2000.00 | 616.00 | 4928.00 | 650.00 | 5200.00 | 2000.00 | ECS ENGINEERING PVT LTD
7.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set |  | 28000.00 | 56000.00 | 11000.00 | 22000.00 | 19800.00 | 39600.00 | 10500.00 | 21000.00 | 21000.00 | Awasthi Electric Works
8.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. 100 mm width X 50 mm depth X 1.6 mm thickness. | 70.00 | Meter |  | 690.00 | 48300.00 | 432.00 | 30240.00 | 451.00 | 31570.00 | 378.00 | 26460.00 | 26460.00 | Awasthi Electric Works
9.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required. 100 mm width X 50 mm depth X 1.6 mm thickness. | 5.00 | Each |  | 1000.00 | 5000.00 | 532.00 | 2660.00 | 489.50 | 2447.50 | 695.00 | 3475.00 | 2447.50 | RS Power Systems Pvt. Ltd.
10.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Upto 35 sq. mm (clamped with 1mm thick saddle). | 70.00 | Meter |  | 60.00 | 4200.00 | 35.00 | 2450.00 | 43.00 | 3010.00 | 45.00 | 3150.00 | 2450.00 | ECS ENGINEERING PVT LTD
11.00 | Supply of 1 core , 35 sq.mm , XLPE insulated, armoured, copper conductor cable of 1.1 KV grade confirming to IS - 7098 (part-I) 1988 with upto date ammendements as required. | 70.00 | Meter |  | 390.00 | 27300.00 | 365.00 | 25550.00 | 357.50 | 25025.00 | 405.00 | 28350.00 | 25025.00 | RS Power Systems Pvt. Ltd.
12.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 1 X 35 sq. mm (25mm). | 1.00 | Set |  | 1400.00 | 1400.00 | 500.00 | 500.00 | 94.00 | 94.00 | 250.00 | 250.00 | 94.00 | RS Power Systems Pvt. Ltd.
13.00 | All Inclusive Comprehensive Maintenance Contract for 2 X 120 KVA UPS System from OEM excluding replacement of batteries , other electrical accessories/ components etc. complete as required (after expiry of 02 years warrantee period on UPS and 3 years warrantee period on SMS batteries.). For Ist Year | 1.00 | Job |  | 120000.00 | 120000.00 | 40000.00 | 40000.00 | 65000.00 | 65000.00 | 80000.00 | 80000.00 | 40000.00 | ECS ENGINEERING PVT LTD
14.00 | All Inclusive Comprehensive Maintenance Contract for 2 X 120 KVA UPS System from OEM excluding replacement of batteries , other electrical accessories/ components etc. complete as required (after expiry of 02 years warrantee period on UPS and 3 years warrantee period on SMS batteries.). For IInd Year | 1.00 | Job |  | 130000.00 | 130000.00 | 40000.00 | 40000.00 | 70000.00 | 70000.00 | 80000.00 | 80000.00 | 40000.00 | ECS ENGINEERING PVT LTD
15.00 | All Inclusive Comprehensive Maintenance Contract for 2 X 120 KVA UPS System from OEM excluding replacement of batteries , other electrical accessories/ components etc. complete as required (after expiry of 02 years warrantee period on UPS and 3 years warrantee period on SMS batteries.). For IIIrd Year | 1.00 | Job |  | 140000.00 | 140000.00 | 40000.00 | 40000.00 | 75000.00 | 75000.00 | 80000.00 | 80000.00 | 40000.00 | ECS ENGINEERING PVT LTD
| Total in Figures |  |  |  |  | 4540100.00 |  | 4118560.00 |  | 4330214.50 |  | 4049585.00
Lowest Amount Quoted BY: Awasthi Electric Works(4049585.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of UPS for GLF System at Aurangabad Airport. Tender ID: 2020_AAI_59888_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works | 4049585.00 | L1
| 2 | ECS ENGINEERING PVT LTD | 4118560.00 | L2
| 3 | RS Power Systems Pvt. Ltd. | 4330214.50 | L3
| 4 | Novateur Electrical and Digital Systems Private Limited | 4540100.00 | L4