## BoQ1
Government eProcurement System Created By: Tapan Kumar Bala Created Date/Time: 04-Dec-2020 12:42 PM Tender Title: 100KLD Sewage Treatment Plant (STP) based on MBBR Treatment at LGBI Airport, Guwahati - Electrical and Mechanical works Tender ID: 2020_AAI_60051_1
Tender Inviting Authority: Asst. General Manager (Engg – Elect), AAI, LGBI Airport, Guwahati, Assam – 781015
Name of Work: 100KLD Sewage Treatment Plant (STP) based on MBBR Treatment at LGBI Airport, Guwahati - Electrical & Mechanical works.
Contract No: AAI/AGM(E-E)/NIT-09/2020-21
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SAWEN CONSULTANCY SERVICES PVT. LTD.(GSTN-09AAQCS9226F1ZU) |  | Sarvo Technologies Limited(GSTN-06AABCS8661D1ZE) |  | Advance Equipment And Projects Pvt Ltd(GSTN-09AALCA2347N1Z8) |  | SHREE BHARAT ION EXCHANGE ENGINEERS(GSTN-07AAJPK2668P1Z1) |  | Hygienic World(GSTN-18AADFH7826E1ZD) |  | Oxybee Solutions(GSTN-09AADFO1623N1Z3) |  | ENHANCE ECOTECH SOLUTION PVT LTD(GSTN-06AADCE9126D1ZW) |  | HITECH ENVIRO ENGINEERS AND CONSULTANTS PVT LTD(GSTN-09AADCH3746E1ZN) |  | PRIORA WATER SOLUTIONS PVT LTD(GSTN-27AAHCP7125M1ZZ) |  | CLEAR ION EXPERTS PVT LTD(GSTN-06AAACC5410H1Z6) |  | M/S EASTERN ENVO PROTECT(GSTN-NA) |  | GREENTECH ENTERPRISE(GSTN-NA) |  | B S ENVIRO N INFRACON PVT LTD(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SEWAGE TREATMENT PLANT (MBBR TECHNOLOGY) Design, supplying, installing, testing & commissioning of Sewage Treatment Plant (excluding excavation, back filling & disposal of surplus earth MS/Civil construction work) for the following duty: Nature of effluent - Domestic Sewage from toilet, kitchen waste water shall be discharged into the STP. Design to take consideration of same. Daily average flow - 100 Cum / Day pH - 7.5 – 8.5 BOD5 - 250 – 450 Mg/L S. Solids - 200 – 400 Mg/L COD - 600 – 800 Mg/L Oil & Grease - 50 Mg / L Effluent discharge standard after treatment pH - 6.0 – 8.5 BOD5 - Less than 20Mg/L S. Solids - Less than 10 Mg/L COD - Less than 60 Mg/L Oil & Grease - Less than 5 Mg / L Sewage treatment plant shall include the following items: Screen Chamber Sewage equalization tank/sump MBBR Reactor Secondary Settling Tank Chlorine Contact Tank Sludge Holding Tan Filtration through MGF & ACF Air Blowers, Pumps & equipment Piping, valves etc Electrical Panel & Cabling Quoted rate should include Approval from pollution board at initial & various other stages of works including preparation of report/ drawings as per pollution board requirement, arrangement of raw sewage for testing & commissioning. Contractor shall include the cost of all chemicals (consumed during testing & commissioning and the cost of such items of works which are not explicitly mentioned above, but are mendatory to have pollution board approval.
1.01 | Supply, Installation, Testing and Commissioning of Stainless Steel Perforated, Corrugated Bar Screen with manual lifting arrangement. | 1.00 | No. |  | 30000.00 | 30000.00 | 21840.00 | 21840.00 | 12000.00 | 12000.00 | 20000.00 | 20000.00 | 20000.00 | 20000.00 | 11970.00 | 11970.00 | 20000.00 | 20000.00 | 16500.00 | 16500.00 | 45000.00 | 45000.00 | 9900.00 | 9900.00 | 30000.00 | 30000.00 | 9714.47 | 9714.47 | 55000.00 | 55000.00 | 9714.47 | GREENTECH ENTERPRISE
2.00 | Supply of MS hot dip galvanized puddle flanges in accordance to BS:10 table D as required to be provided (in the structural slab and wall) of various diameters. Puddle flanges shall be provided for all the structural component of the STP. The installation of the puddle flanges shall be carried out by the Civil contractor in accordance to the Civil GA drawing (to be prepared by the STP contractor) at the required levels & position; under the supervision of the STP contractor. | 1.00 | Lot |  | 5000.00 | 5000.00 | 118800.00 | 118800.00 | 45000.00 | 45000.00 | 40000.00 | 40000.00 | 30000.00 | 30000.00 | 44100.00 | 44100.00 | 55000.00 | 55000.00 | 70000.00 | 70000.00 | 45000.00 | 45000.00 | 17500.00 | 17500.00 | 30000.00 | 30000.00 | 18584.21 | 18584.21 | 91000.00 | 91000.00 | 5000.00 | SAWEN CONSULTANCY SERVICES PVT. LTD.
3.00 | Supply of plastic manhole step/foot rest (@ 300 mm c/c) with polypropelene compound injection molded around 12 mm dia (Fe-415) steel reinforcing bar. Provision of the foot rest is envisaged in various tanks/ components of the STP for the purpose of accessability. The installation of the foot rest shall be done by the civil contractor as per civil GA drawing. | 1.00 | Lot |  | 250000.00 | 250000.00 | 34000.00 | 34000.00 | 40000.00 | 40000.00 | 65000.00 | 65000.00 | 60000.00 | 60000.00 | 37800.00 | 37800.00 | 10000.00 | 10000.00 | 15000.00 | 15000.00 | 48000.00 | 48000.00 | 5500.00 | 5500.00 | 15000.00 | 15000.00 | 21118.42 | 21118.42 | 49000.00 | 49000.00 | 5500.00 | CLEAR ION EXPERTS PVT LTD
4.00 | Supply, installation, testing & commissioning of electronic type Auto Water Level Controller indicator and controller for automatic operation of the system with high/low level alarm complete with auxillary NO/NC contacts for each tank. | 7.00 | Nos. |  | 15000.00 | 105000.00 | 9296.00 | 65072.00 | 5000.00 | 35000.00 | 15000.00 | 105000.00 | 15000.00 | 105000.00 | 19800.90 | 138606.30 | 9000.00 | 63000.00 | 6050.00 | 42350.00 | 1800.00 | 12600.00 | 13000.00 | 91000.00 | 4500.00 | 31500.00 | 11403.95 | 79827.65 | 9500.00 | 66500.00 | 12600.00 | PRIORA WATER SOLUTIONS PVT LTD
5.00 | Supply, installation, testing & commissioning of non clogging type pumps capable of handling solids upto 35mm having SS casing & SS impeller complete with all accessories, motor of required capacity. Delivery header with isolation valve, pressure gauge on delivery line with isolation cock, level controller (with wiring) to control the level of sump automatically. Pumps shall have following duty:
5.01 | Supply, Installation, Testing and Commissioning of Submersible Sewage lifting pump (from Septic Tank to Equalization Tank) Capacity- 1HP, 0.75KW, Flow Rate- 2m3/hr Head- 8-10m | 3.00 | Nos. |  | 35000.00 | 105000.00 | 37584.00 | 112752.00 | 22000.00 | 66000.00 | 18000.00 | 54000.00 | 35000.00 | 105000.00 | 20790.00 | 62370.00 | 22500.00 | 67500.00 | 26785.00 | 80355.00 | 32750.00 | 98250.00 | 32000.00 | 96000.00 | 30000.00 | 90000.00 | 20093.76 | 60281.28 | 36400.00 | 109200.00 | 54000.00 | SHREE BHARAT ION EXCHANGE ENGINEERS
5.02 | Supply, Installation, Testing and Commissioning of Submersible Sewage lifting pump (from Equalization Tank to MBBR Tank) Capacity- 2HP, 1.5KW Flow Rate- 5-6m3/hr Head- 8-10m | 2.00 | Nos. |  | 65000.00 | 130000.00 | 37584.00 | 75168.00 | 25000.00 | 50000.00 | 22000.00 | 44000.00 | 44000.00 | 88000.00 | 28350.00 | 56700.00 | 22500.00 | 45000.00 | 36630.00 | 73260.00 | 32750.00 | 65500.00 | 39500.00 | 79000.00 | 40000.00 | 80000.00 | 27404.83 | 54809.66 | 36400.00 | 72800.00 | 44000.00 | SHREE BHARAT ION EXCHANGE ENGINEERS
5.03 | Supply, Installation, Testing and Commissioning of Sludge pump (from Clarifier Tank to Sludge Sump) Capacity- 1HP, 0.75KW Flow Rate- 5- m3/hr Head- 3-4m Cost shall be inclusive of PVC flexible Hose pipe ( for piping submeged in effluent) with MS epoxy piping (for piping non-submerged in effluent). Provision of guide ropes to guide submersible pump from upper level to operational level in sump basin with channels / angle section of MSEP shall be made by the STP contractor. | 2.00 | Nos. |  | 65000.00 | 130000.00 | 37000.00 | 74000.00 | 18000.00 | 36000.00 | 14500.00 | 29000.00 | 42000.00 | 84000.00 | 17640.00 | 35280.00 | 13600.00 | 27200.00 | 37660.00 | 75320.00 | 32750.00 | 65500.00 | 40000.00 | 80000.00 | 25000.00 | 50000.00 | 15914.21 | 31828.42 | 45000.00 | 90000.00 | 27200.00 | ENHANCE ECOTECH SOLUTION PVT LTD
6.00 | Air diffusion system shall include the following:
6.01 | Supply, Installation, Testing and Commissioning of twin type rotary air blowers (1W + 1S) capable of delivering 287 cum/hr of free air at 0.45 kg/cm2 driven through “V” belt or directly coupled through flexible coupling to a TEF Cmotor of suitable HP Suitable for 415 ± 10% volts, 3 phase, 50 cycles A/C supply. (for MBBR Tanks) | 2.00 | Nos. |  | 150000.00 | 300000.00 | 123120.00 | 246240.00 | 95000.00 | 190000.00 | 90000.00 | 180000.00 | 130000.00 | 260000.00 | 97020.00 | 194040.00 | 85600.00 | 171200.00 | 133100.00 | 266200.00 | 185000.00 | 370000.00 | 156000.00 | 312000.00 | 250000.00 | 500000.00 | 119741.45 | 239482.90 | 210000.00 | 420000.00 | 171200.00 | ENHANCE ECOTECH SOLUTION PVT LTD
6.02 | Supply, Installation, Testing and Commissioning of twin type rotary air blowers (1W + 1S) capable of delivering 215 cum/hr of free air at 0.45 kg/cm2 driven through “V” belt or directly coupled through flexible coupling to a TEF Cmotor of suitable HP Suitable for 415 ± 10% volts, 3 phase, 50 cycles A/C supply. (for Equalization Tank) | 2.00 | Nos. |  | 150000.00 | 300000.00 | 123120.00 | 246240.00 | 90000.00 | 180000.00 | 80000.00 | 160000.00 | 150000.00 | 300000.00 | 85680.00 | 171360.00 | 65800.00 | 131600.00 | 121000.00 | 242000.00 | 175000.00 | 350000.00 | 144000.00 | 288000.00 | 226000.00 | 452000.00 | 91231.58 | 182463.16 | 210000.00 | 420000.00 | 131600.00 | ENHANCE ECOTECH SOLUTION PVT LTD
6.03 | Air piping shall comprise of pipes droppers/ laterals with MS (epoxy coated) Header complete with all fittings such as tees, crosses, plugs, sockets, elbows, reducers, supports & clamps, puddle flanges etc cutting chases & making good. Contactor to submit detailed P & I indicating their proposal. | 1.00 | Lot |  | 1200000.00 | 1200000.00 | 129600.00 | 129600.00 | 35000.00 | 35000.00 | 150000.00 | 150000.00 | 155000.00 | 155000.00 | 69300.00 | 69300.00 | 45000.00 | 45000.00 | 88000.00 | 88000.00 | 45000.00 | 45000.00 | 49500.00 | 49500.00 | 200000.00 | 200000.00 | 111505.27 | 111505.27 | 95000.00 | 95000.00 | 35000.00 | Advance Equipment And Projects Pvt Ltd
6.04 | Supply, Installation, Testing and Commissioning of Fine Bubble Diffusers, Dimensions: 63mm dia. x 1000mm long, EPDM Membrane Type, Air Flow Rate: 3m3/hr- 9m3/hr (Optimal 2m3/hr - 5m3/hr) | 102.00 | Nos. |  | 2000.00 | 204000.00 | 1080.00 | 110160.00 | 1500.00 | 153000.00 | 1000.00 | 102000.00 | 1200.00 | 122400.00 | 1008.00 | 102816.00 | 1440.00 | 146880.00 | 2750.00 | 280500.00 | 1200.00 | 122400.00 | 1300.00 | 132600.00 | 200.00 | 20400.00 | 3125.53 | 318804.06 | 1700.00 | 173400.00 | 20400.00 | M/S EASTERN ENVO PROTECT
6.05 | Bronze Ball valve and air dispersion grid as required for STP as described above. | 1.00 | Lot |  | 30000.00 | 30000.00 | 25200.00 | 25200.00 | 1250.00 | 1250.00 | 24000.00 | 24000.00 | 90000.00 | 90000.00 | 37800.00 | 37800.00 | 15000.00 | 15000.00 | 11800.00 | 11800.00 | 25000.00 | 25000.00 | 19800.00 | 19800.00 | 30000.00 | 30000.00 | 32100.00 | 32100.00 | 30000.00 | 30000.00 | 1250.00 | Advance Equipment And Projects Pvt Ltd
7.00 | Providing and fixing all piping (as described below) and isolation control valves for making the system complete. SS 304 : Submerged air piping MS Epoxy : Air piping & pumped effluent riser (non-submerged) PVC piping : Pumped effluent (submerged) & tank overflow pipe line GI (Heavy) : Interconnecting pipe line after delivery header of pump/ filter | 1.00 | Lot |  | 250000.00 | 250000.00 | 144000.00 | 144000.00 | 150000.00 | 150000.00 | 116200.00 | 116200.00 | 200000.00 | 200000.00 | 302400.00 | 302400.00 | 360000.00 | 360000.00 | 165000.00 | 165000.00 | 175000.00 | 175000.00 | 97900.00 | 97900.00 | 200000.00 | 200000.00 | 97651.59 | 97651.59 | 450000.00 | 450000.00 | 97651.59 | GREENTECH ENTERPRISE
8.00 | Supply, installation, testing and commissioning of FAB (MBBR) Media, High Strength Hollow Fiber, Pore Size- 0.6micron | 36.00 | M3 |  | 15000.00 | 540000.00 | 14400.00 | 518400.00 | 12500.00 | 450000.00 | 20000.00 | 720000.00 | 16000.00 | 576000.00 | 12219.90 | 439916.40 | 14200.00 | 511200.00 | 15950.00 | 574200.00 | 18500.00 | 666000.00 | 13200.00 | 475200.00 | 12000.00 | 432000.00 | 18161.84 | 653826.24 | 3675.00 | 132300.00 | 132300.00 | B S ENVIRO N INFRACON PVT LTD
9.00 | Supply, installation, testing and commissioning of PVC tube deck settling media to be installed in Clarifier Tank, V-Type Media, Settling Velocity- 0.5m/s | 15.00 | M3 |  | 15000.00 | 225000.00 | 10800.00 | 162000.00 | 11000.00 | 165000.00 | 12000.00 | 180000.00 | 15000.00 | 225000.00 | 10111.50 | 151672.50 | 9200.00 | 138000.00 | 10450.00 | 156750.00 | 11500.00 | 172500.00 | 9300.00 | 139500.00 | 14000.00 | 210000.00 | 15374.21 | 230613.15 | 3780.00 | 56700.00 | 56700.00 | B S ENVIRO N INFRACON PVT LTD
10.00 | Supply, installation, testing & commissioning of Chlorine dosing system comprising of 200 ltrs HDPE / FRP tank with 0-12 lph electronic metering type pump. | 1.00 | No. |  | 45000.00 | 45000.00 | 28800.00 | 28800.00 | 20000.00 | 20000.00 | 20000.00 | 20000.00 | 35000.00 | 35000.00 | 20790.00 | 20790.00 | 18500.00 | 18500.00 | 20800.00 | 20800.00 | 22500.00 | 22500.00 | 15000.00 | 15000.00 | 3000.00 | 3000.00 | 11066.05 | 11066.05 | 21000.00 | 21000.00 | 3000.00 | M/S EASTERN ENVO PROTECT
11.00 | Supplying, installing, testing & commissioning of horizontal centrifugal filter feed water pumps CI Head & Base, Bronze Impeller along with motor, pressure gauge with isolation cock, Isolation valve, NRV on delivery line. Isolation valve, stainer (with by-pass) at suction. Mechanical seal, suitable vibration elimination pads of approved design, drain pipe with valve (25 dia) for the pump. The pump shall be suitable for 415±10% volts 3 phase AC supply. (1 Working + 1 Standby)
11.01 | Supply, Installation, Testing and Commissioning of Centrifugal Filter Feed pump (from Chlorination Tank to MGF) Capacity- 1.5HP, 1.12KW Flow Rate- 5-6m3/hr Head- 3-4m | 2.00 | Nos. |  | 45000.00 | 90000.00 | 37962.00 | 75924.00 | 20000.00 | 40000.00 | 20000.00 | 40000.00 | 40000.00 | 80000.00 | 16380.00 | 32760.00 | 18200.00 | 36400.00 | 16830.00 | 33660.00 | 43500.00 | 87000.00 | 31000.00 | 62000.00 | 30000.00 | 60000.00 | 8401.29 | 16802.58 | 29400.00 | 58800.00 | 16802.58 | GREENTECH ENTERPRISE
12.00 | Providing, fixing, testing & commissioning of vertical FRP filter with adequate dirt holding capacity. Fabricated from FRP as per manufacturer's specifications complete with initial charge filter media including painting Including concrete foundation with cement plaster complete as required. The filter shall also be provided with set of internals for raw water inlet and bottom collecting system. Complete with frontal piping (heavy) and butterfly valves designed on 1.50 m / sec velocity.
12.01 | Multigrade Filter Filtration Rate 5000-6000L/Sqm/Hr Capacity : 1.4-1.7 LPS each | 1.00 | No. |  | 125000.00 | 125000.00 | 64800.00 | 64800.00 | 135000.00 | 135000.00 | 150000.00 | 150000.00 | 330000.00 | 330000.00 | 70560.00 | 70560.00 | 63000.00 | 63000.00 | 98500.00 | 98500.00 | 125000.00 | 125000.00 | 62500.00 | 62500.00 | 87000.00 | 87000.00 | 109815.80 | 109815.80 | 190000.00 | 190000.00 | 62500.00 | CLEAR ION EXPERTS PVT LTD
12.02 | Activated Carbon Filter Filtration Rate 5000-6000L/Sqm/Hr Capacity : 1.4-1.7 LPS each | 1.00 | No. |  | 150000.00 | 150000.00 | 64800.00 | 64800.00 | 145000.00 | 145000.00 | 200000.00 | 200000.00 | 370000.00 | 370000.00 | 88200.00 | 88200.00 | 75000.00 | 75000.00 | 115000.00 | 115000.00 | 135000.00 | 135000.00 | 71500.00 | 71500.00 | 87000.00 | 87000.00 | 119952.64 | 119952.64 | 210000.00 | 210000.00 | 64800.00 | Sarvo Technologies Limited
13.00 | Providing and laying GI pipes (heavy class) (Tertiary Treatment Equipment Piping) of approved make conforming to IS:1239-1982 complete with GI fittings such as tees, crosses, plugs, sockets, elbows, reducers, unions, flanges, sleeve pieces, check nuts etc in including cutting and making good the walls, floors, RCC work etc cutting chases & filling the same with cement concrete 1:3:6 (1cement :3 coarse sand : 6 graded stone aggregate 20 mm nominal size) or cement mortar 1:4 (1 cement:4 coarse sand) as required, including painting the exposed pipes with desired shade of enamel paint over a coat of primer.
13.01 | 50 mm dia | 70.00 | M |  | 1200.00 | 84000.00 | 1080.00 | 75600.00 | 350.00 | 24500.00 | 1800.00 | 126000.00 | 550.00 | 38500.00 | 1325.52 | 92786.40 | 680.00 | 47600.00 | 605.00 | 42350.00 | 650.00 | 45500.00 | 1000.00 | 70000.00 | 650.00 | 45500.00 | 574.42 | 40209.40 | 750.00 | 52500.00 | 24500.00 | Advance Equipment And Projects Pvt Ltd
14.00 | Providing and fixing cast iron butterfly valves tested to 15 kg/ Sqcm pressure (Including flanges).
14.01 | 50 mm dia | 12.00 | Nos. |  | 1500.00 | 18000.00 | 2952.00 | 35424.00 | 2000.00 | 24000.00 | 3200.00 | 38400.00 | 2500.00 | 30000.00 | 1648.08 | 19776.96 | 1810.00 | 21720.00 | 2325.00 | 27900.00 | 2950.00 | 35400.00 | 1700.00 | 20400.00 | 1850.00 | 22200.00 | 675.79 | 8109.48 | 2970.00 | 35640.00 | 8109.48 | GREENTECH ENTERPRISE
15.00 | Providing and fixing horizontal flap type non-return valve tested to 15 kg/Sqcm pressure of approved make (including flanges)
15.01 | 50 mm dia | 12.00 | Nos. |  | 1500.00 | 18000.00 | 2520.00 | 30240.00 | 1500.00 | 18000.00 | 2200.00 | 26400.00 | 3000.00 | 36000.00 | 2089.08 | 25068.96 | 1920.00 | 23040.00 | 3300.00 | 39600.00 | 2850.00 | 34200.00 | 1500.00 | 18000.00 | 3000.00 | 36000.00 | 549.08 | 6588.96 | 4725.00 | 56700.00 | 6588.96 | GREENTECH ENTERPRISE
16.00 | Supply, installation, testing and commissioning of Magnetic flow meter suitable capacity with preamplifier and microprocessor including necessary cabling, conduit, etc. complete suitable for raw sewage application. | 2.00 | Nos. |  | 65000.00 | 130000.00 | 48600.00 | 97200.00 | 40000.00 | 80000.00 | 120000.00 | 240000.00 | 45000.00 | 90000.00 | 20790.00 | 41580.00 | 65000.00 | 130000.00 | 40000.00 | 80000.00 | 58500.00 | 117000.00 | 57200.00 | 114400.00 | 40000.00 | 80000.00 | 48994.74 | 97989.48 | 84000.00 | 168000.00 | 41580.00 | Oxybee Solutions
17.00 | Supply, installation, testing & commissioning of Filter Press; MS Structure, P.P. Recessed Plate Type, Vertical 470mm x 470mm x 18 Chambers, along with 2nos. of 1HP Screw Pump for feeding of the Sludge (1 W + 1 Standby) | 1.00 | No. |  | 250000.00 | 250000.00 | 252000.00 | 252000.00 | 250000.00 | 250000.00 | 250000.00 | 250000.00 | 200000.00 | 200000.00 | 144900.00 | 144900.00 | 155000.00 | 155000.00 | 269000.00 | 269000.00 | 485000.00 | 485000.00 | 198000.00 | 198000.00 | 250000.00 | 250000.00 | 380126.44 | 380126.44 | 335000.00 | 335000.00 | 144900.00 | Oxybee Solutions
18.00 | MAIN DISTRIBUTION BOARD (SEWAGE TREATMENT PLANT) Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of motor control centre shall be fabricated out of 14 gauge CRCA sheet steel in form in 3b formation with reinforcement of suitable size angle iron, channel ‘T’ sections irons and /or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before painting as per specifications with 2 coats of red oxide primer and final approved shade of powder coated paint. 2 Nos. earthing terminals shall be provided for 3 phase, 4 wire, 50 Hz supply system. Lifting hooks shall also be provided in case of large panels. Approval shall be taken for each panel before fabrication. Cadmium Plated hardware shall be used in fabrication of panels. Quoted rates shall inclusive of cables, cable trays, control cabling, earthing (in accordance to specification) with earthing from panel to each motor / equipment. INCOMER: 1 Nos. 100 Amp four pole Moulded Case Circuit Breaker (Ics value 25 KA) with built in thermal based release unit with adjustable setting. BUSBARS: 200 Amp TPN busbars of high conductivity electrolytic quality aluminium alloy. INSTRUMENTS: 1 Set of digital multifunction meter (Ammeter + Voltmeter) for 3 phase, 4 wire operation as per specification. 1 Sets of RYB phase indicating lamps controlled by 2 amp MCB. OUTGOING: a. 2 Nos. suitable rating MPCB for 7.5HP Blower Motor Starter (Auto/Manual) (3 Phase) and timer. Each compartment shall contain auto / manual selector swtich and indicating / pushbutton lamps with MCB for ON / OFF / TRIP of motor. b. 2 Nos. suitable rating MPCB for 3HP Blower Motor Starter (Auto/Manual) (3 Phase) and timer. Each compartment shall contain auto/manual selector switch and indicating lamps with MCB’s for ‘ON/OFF/TRIP' status of motor. c. 3 Nos. suitable rating MPCB for 1HP Submersible Sewage Lifting Pump Motor Starter (3 Phase). Compartment shall contain auto/manual selector switch and indicating lamps with MCB’s for ‘ON/OFF/TRIP’ status of motor d. 2 Nos. suitable rating MPCB for Nos. 7.5 KW direct on line starter and outgoing feeders to filter feed pump (including 1 no. standby). Each compartment shall contain auto/manual selector switch and indicating lamps with MCB for ‘ON/OFF/TRIP’ status of motor. e. 2 Nos. suitable rating MPCB for Nos. 2.5 KW direct on line starter and outgoing feeders to irrigation water pump (including 1 no. standby). Each compartment shall contain auto / manual selector switch and indicating lamps with MCB for ‘ON/OFF/TRIP’ status of motor. f. 2 Nos. suitable rating MPCB for 2HP Submersible Sewage Lifting Pump Motor Starter (3 Phase). Each compartment shall contain auto/manual selector switch and indicating lamps with MCB for ‘ON/OFF/TRIP’ status of motor. g. 2 Nos. suitable rating MPCB for 1HP Filter Feed Pump Motor Starter (3 Phase). Each compartment shall contain auto/manual selector switch and indicating lamps with MCB’s for ‘ON/OFF/TRIP’ status of motor.h. 2 Nos. suitable rating MPCB for 1HP Sludge Pump Motor Starter (3 Phase). Each compartment shall contain auto/manual selector switch and indicating lamps with MCB’s for ‘ON/OFF/TRIP’ status of motor. i. 2 Nos. suitable rating MPCB for 1HP Screw Pump Starter (3 Phase). Each compartment shall contain auto/manual selector switch and indicating lamps with MCB’s for ‘ON/OFF/TRIP’ status of motor. 20A TP MCB - 2 Nos. 6A SP MCB - 4 Nos | 1.00 | No. |  | 300000.00 | 300000.00 | 779000.00 | 779000.00 | 280000.00 | 280000.00 | 300000.00 | 300000.00 | 180000.00 | 180000.00 | 304584.84 | 304584.84 | 630000.00 | 630000.00 | 275000.00 | 275000.00 | 485000.00 | 485000.00 | 350000.00 | 350000.00 | 250000.00 | 250000.00 | 164723.69 | 164723.69 | 561000.00 | 561000.00 | 164723.69 | GREENTECH ENTERPRISE
19.00 | Annual Operation, upkeeing and maintenance of all equipments, machineries and accessories related to 100KLD Sewage Treatment Plant involving operation minor condition of the system, ensuring serviceability / satisfactory working condition of the system, maintenance of records / documentation of the above works etc., as per the detailed specification, terms & conditions covered under this contract on all days including Sundays & holidays of the month complete as required. The required minimum man power (One Technician cum Operator and One Helper in each shift for round the clock operation and One sweeper in General shift) to be deployed for each shift of 8 hrs for the equipments to be operated and upkeeped shall be as per Technical specification and special condition of contract. Required spares and chemicals shall be issued by department as per site requirement.
19.01 | During DLP | 1.00 | Job |  | 480000.00 | 480000.00 | 950000.00 | 950000.00 | 1350000.00 | 1350000.00 | 960000.00 | 960000.00 | 480000.00 | 480000.00 | 1109253.60 | 1109253.60 | 770000.00 | 770000.00 | 720000.00 | 720000.00 | 720000.00 | 720000.00 | 1080000.00 | 1080000.00 | 1000000.00 | 1000000.00 | 958335.00 | 958335.00 | 650000.00 | 650000.00 | 480000.00 | SAWEN CONSULTANCY SERVICES PVT. LTD., Hygienic World
19.02 | First Year | 1.00 | Job |  | 540000.00 | 540000.00 | 998000.00 | 998000.00 | 1400000.00 | 1400000.00 | 1080000.00 | 1080000.00 | 480000.00 | 480000.00 | 1130382.24 | 1130382.24 | 845000.00 | 845000.00 | 780000.00 | 780000.00 | 760000.00 | 760000.00 | 1200000.00 | 1200000.00 | 1200000.00 | 1200000.00 | 958335.00 | 958335.00 | 670000.00 | 670000.00 | 480000.00 | Hygienic World
19.03 | Second Year | 1.00 | Job |  | 600000.00 | 600000.00 | 1047000.00 | 1047000.00 | 1450000.00 | 1450000.00 | 1080000.00 | 1080000.00 | 480000.00 | 480000.00 | 1151510.88 | 1151510.88 | 890000.00 | 890000.00 | 820000.00 | 820000.00 | 790000.00 | 790000.00 | 1320000.00 | 1320000.00 | 1200000.00 | 1200000.00 | 958335.00 | 958335.00 | 750000.00 | 750000.00 | 480000.00 | Hygienic World
| Total in Figures |  |  |  |  | 6634000.00 |  | 6582260.00 |  | 6824750.00 |  | 6500000.00 |  | 5249900.00 |  | 6088285.08 |  | 5511840.00 |  | 5479045.00 |  | 6147350.00 |  | 6475200.00 |  | 6691600.00 |  | 5973000.00 |  | 6069540.00
Lowest Amount Quoted BY: Hygienic World(5249900.00)

## BOQ Summary
BOQ Summary Details Tender Title: 100KLD Sewage Treatment Plant (STP) based on MBBR Treatment at LGBI Airport, Guwahati - Electrical and Mechanical works Tender ID: 2020_AAI_60051_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Hygienic World | 5249900.00 | L1
| 2 | HITECH ENVIRO ENGINEERS AND CONSULTANTS PVT LTD | 5479045.00 | L2
| 3 | ENHANCE ECOTECH SOLUTION PVT LTD | 5511840.00 | L3
| 4 | GREENTECH ENTERPRISE | 5973000.00 | L4
| 5 | B S ENVIRO N INFRACON PVT LTD | 6069540.00 | L5
| 6 | Oxybee Solutions | 6088285.08 | L6
| 7 | PRIORA WATER SOLUTIONS PVT LTD | 6147350.00 | L7
| 8 | CLEAR ION EXPERTS PVT LTD | 6475200.00 | L8
| 9 | SHREE BHARAT ION EXCHANGE ENGINEERS | 6500000.00 | L9
| 10 | Sarvo Technologies Limited | 6582260.00 | L10
| 11 | SAWEN CONSULTANCY SERVICES PVT. LTD. | 6634000.00 | L11
| 12 | M/S EASTERN ENVO PROTECT | 6691600.00 | L12
| 13 | Advance Equipment And Projects Pvt Ltd | 6824750.00 | L13