## BoQ1
Government eProcurement System Created By: RAGHU RAMA REDDY DODDA Created Date/Time: 13-Nov-2020 01:12 PM Tender Title: Construction of New Barracks accommodation for CISF officials at Palavanthangal at Chennai .SH_ SITC of LED Light Fixtures,Fans, Panel, earthing, cable laying etc Tender ID: 2020_AAI_60517_1
Tender Inviting Authority: JGM.Engg(Elect)-II
Name of Work: Construction of New Barracks accommodation for CISF officials at Palavanthangal at Chennai SH: SITC of LED Light Fixtures, Fans, Panel, Earthing, Cable Laying etc.
Contract No: AAM/ENGG (E)/AMED-IX/CISF/PH-III/ 20-21/01
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | R.K.M. ELECTRICALS(GSTN-33ACAPM4207B2ZE) |  | LAKSHMI ELECTRICAL ENTERPRISES(GSTN-33AACFL6352N1Z4) |  | Shantha ELectricals and Engineers Pvt Ltd(GSTN-29AARCS2866G1ZP) |  | PREMIER ENGINEERING TECHNICS PVT. LTD.(GSTN-27AADCP1420F1ZW) |  | CHENNAI ENGINEERING SERVICES(GSTN-33AADFC4373K1ZH) |  | Manoprabha Electricals(GSTN-33AGNPM4749D3Z9) |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.01 | SH-I: Supply of Fans, Fixtures, Cables & Geysers etc
1.02 | Supply of BEE Maximum Star rated / Energy efficent ceiling fan of 1400mm sweep dia with copper wound with double ball bearings, blades Brown in color, ISI marked complete with capacitor, down rod, split pin , reel but without regulator complete as required. (Cromption High speed model / Havells Pacer or equivalent as per approved make list) | 207.00 | Nos |  | 1320.00 | 273240.00 | 1560.00 | 322920.00 | 1925.00 | 398475.00 | 1750.00 | 362250.00 | 1978.00 | 409446.00 | 1999.00 | 413793.00 | 2100.00 | 434700.00 | 1999.00 | 413793.00 | 273240.00 | vk sam engineering
1.03 | Supply of 300 mm sweep, 900 RPM heavy duty Exhaust Fan with pre lubricated double ball bearing, Minimum Air delivery of 1125 CMH, power consumtion:50-60 Watts with lovers etc as required. (Havells / or as per approved make list) | 31.00 | Nos |  | 2200.00 | 68200.00 | 2600.00 | 80600.00 | 2850.00 | 88350.00 | 1250.00 | 38750.00 | 2415.00 | 74865.00 | 2299.00 | 71269.00 | 2500.00 | 77500.00 | 2999.00 | 92969.00 | 38750.00 | Shantha ELectricals and Engineers Pvt Ltd
1.04 | Supply of 4 feet LED batten made of extruded aluminium housing,Opal diffuser creates optimum light uniformity with minimum glare. It has a system level lumen output not less than 4000 lumens with luminaire efficacy of not less than 100 lm/W. constant current output driver, operating range 150 – 270V AC supply, voltages, LED Colour Temp. from 5700K- 6500K with PF≥0.95 and THD<10% & surge protection ≥ 2.5kv, CRI>80, lumen maintainence of 70% at the end of 50000 burning hours. The luminaire is IP 20 protected. LM 79 report to be submitted for luminaire from NABL accrediated lab and LM 80 for LED source issued by LED manufacturer. (Similar to baja CAT No. BCLAB SP 44L LED CW PC SD or as per approved make list) | 285.00 | Nos |  | 790.00 | 225150.00 | 800.00 | 228000.00 | 780.00 | 222300.00 | 1100.00 | 313500.00 | 792.00 | 225720.00 | 1099.00 | 313215.00 | 540.00 | 153900.00 | 699.00 | 199215.00 | 153900.00 | Manoprabha Electricals
1.05 | Supply of 5W 1 feet LED battenmade of Polycarbonate co-extrusion tube for LED light housing with end caps. It has a system level lumen output not less than 500 lumens with luminaire efficacy of not less than 100 lm/W. constant current output driver, operating range 150 – 270V AC supply, voltages, LED Colour Temp. from 6500+- 500 K with PF≥0.95 and THD<10% & surge protection ≥ 2.5kv, CRI>70. The luminaire is IP 20 protected. LM 79 report to be submitted for luminaire from NABL accrediated lab and LM 80 for LED source issued by LED manufacturer. (Similar to bajaj CAT No. BCLSB 5W WH or equivalent as per approved make list) | 368.00 | Nos |  | 230.00 | 84640.00 | 300.00 | 110400.00 | 210.00 | 77280.00 | 175.00 | 64400.00 | 300.00 | 110400.00 | 349.00 | 128432.00 | 300.00 | 110400.00 | 189.00 | 69552.00 | 64400.00 | Shantha ELectricals and Engineers Pvt Ltd
1.06 | Supplying of plastic polycorbonate B22 angle holder including connections etc. as required. | 101.00 | Nos |  | 65.00 | 6565.00 | 75.00 | 7575.00 | 150.00 | 15150.00 | 55.00 | 5555.00 | 40.00 | 4040.00 | 79.00 | 7979.00 | 25.00 | 2525.00 | 79.00 | 7979.00 | 2525.00 | Manoprabha Electricals
1.07 | Supply of LED bulb suitable to B22 type holder with minimum lumen output of 900 lumens with luminaire efficacy of not less than 95 lm/W and LED Colour Temp. from 5700K- 6500K etc. | 101.00 | Nos |  | 85.00 | 8585.00 | 120.00 | 12120.00 | 180.00 | 18180.00 | 175.00 | 17675.00 | 96.00 | 9696.00 | 119.00 | 12019.00 | 100.00 | 10100.00 | 140.00 | 14140.00 | 8585.00 | vk sam engineering
1.08 | Supply of LED street light fitting having system lumen output not less than 6600 lumens and system efficacy of not less than 110 lumens per watt and lumen maintainence of 70% at the end of 50000 burning hours, Power Factor≥0.95 & THD<10%, CRI>70, CCT : 5500K ± 500K, made of high pressure die cast Aluminium/ standard alloy housing with separate optics and control gear compartment, toughened glass protector, permanently sealed and a removable control gear plate, mounting spigot suitable for horizontal mounting (Ø 32 – 42mm) with tilt flexibility upto (+)(-) 15 degrees, operating range 150 – 270V AC supply voltages, surge protection≥10KV with minimum IP:65 Protection. LM 79 report to be submitted for luminaire from NABL accrediated lab and LM 80 for LED source issued by LED manufacture. LED shall have reverse polarity, open and short circuit protection. (Similar to Bajaj CAT No.ENXT P 72L WH CR PC SD or or as per approved make list) | 46.00 | Nos |  | 2900.00 | 133400.00 | 3500.00 | 161000.00 | 2700.00 | 124200.00 | 3100.00 | 142600.00 | 2818.00 | 129628.00 | 3949.00 | 181654.00 | 2800.00 | 128800.00 | 2999.00 | 137954.00 | 124200.00 | LAKSHMI ELECTRICAL ENTERPRISES
1.09 | Supply of LED flood light with powder coated pressure die cast Aluminium housing design. LED fitting should have secondary optics to get optimum optical output.. It has a system lumen output not less than 11000 lumens with luminaire efficacy of not less than 110 lm/W and lumen maintainence of 70% at the end of 50000 burning hours with constant current driver output, operating range 150V – 270V, 50Hz AC supply, CCT of 5700K - 6500K with PF≥0.95 and THD<10% & surge proctection of ≥10kv. The luminaire shall be minimum IP:65 protected. LM 79 report to be submitted for luminaire from NABL accrediated lab and LM 80 for LED source issued by LED manufacture. LED shall have reverse polarity, open and short circuit protection. (Similar to bajaj CAT No BJFL 100 LED I or as per approved make list) | 9.00 | Nos |  | 5375.00 | 48375.00 | 5800.00 | 52200.00 | 4740.00 | 42660.00 | 5200.00 | 46800.00 | 5175.00 | 46575.00 | 6999.00 | 62991.00 | 4800.00 | 43200.00 | 4199.00 | 37791.00 | 37791.00 | DElite System Engineering (India) Pvt. Ltd.
1.10 | Supply of following sizes of Aluminium Power Cables,multi stranded conductor, XLPE Insulated Armoured , 1100V grade as per IS 7098(Part 1) 1988.
1.11 | a) 4 C x 16 Sq.mm | 950.00 | Mtr |  | 112.00 | 106400.00 | 140.00 | 133000.00 | 110.00 | 104500.00 | 95.00 | 90250.00 | 108.00 | 102600.00 | 99.00 | 94050.00 | 100.00 | 95000.00 | 99.00 | 94050.00 | 90250.00 | Shantha ELectricals and Engineers Pvt Ltd
1.12 | b) 31/2 C x 95 Sq.mm | 130.00 | Mtr |  | 370.00 | 48100.00 | 400.00 | 52000.00 | 358.00 | 46540.00 | 360.00 | 46800.00 | 399.00 | 51870.00 | 359.00 | 46670.00 | 350.00 | 45500.00 | 309.00 | 40170.00 | 40170.00 | DElite System Engineering (India) Pvt. Ltd.
1.13 | c) 31/2 C x 185 Sq.mm | 350.00 | Mtr |  | 670.00 | 234500.00 | 800.00 | 280000.00 | 660.00 | 231000.00 | 610.00 | 213500.00 | 748.00 | 261800.00 | 599.00 | 209650.00 | 620.00 | 217000.00 | 699.00 | 244650.00 | 209650.00 | CHENNAI ENGINEERING SERVICES
1.14 | Supply of Electric water Gyser of minimum 25 litres storage capacity, wattage : 2000 W ,Minimum 4 star Rating with all standard accessories etc. | 21.00 | Nos |  | 7500.00 | 157500.00 | 8800.00 | 184800.00 | 6900.00 | 144900.00 | 12000.00 | 252000.00 | 9991.00 | 209811.00 | 7999.00 | 167979.00 | 6000.00 | 126000.00 | 6999.00 | 146979.00 | 126000.00 | Manoprabha Electricals
1.15 | Providing and fixing loop-in loop out SMC control box similer to Sintex having hinged Single door with locking arrangement & consisting of 6A DP MCB on DIN rail , 4way 63A connectors etc on wall /poles etc complete as required. Sintex :GSJB-3525 or Equivalent approved make | 48.00 | Nos |  | 1965.00 | 94320.00 | 1500.00 | 72000.00 | 1900.00 | 91200.00 | 2600.00 | 124800.00 | 1620.00 | 77760.00 | 2269.00 | 108912.00 | 2200.00 | 105600.00 | 1999.00 | 95952.00 | 72000.00 | R.K.M. ELECTRICALS
1.16 | SH-II:ITC of Light fixtures, Fans, and SITC of panel, earthing, pipes etc
1.17 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube/lamp etc. directly on ceiling/ wall, including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 285.00 | Nos |  | 100.00 | 28500.00 | 100.00 | 28500.00 | 150.00 | 42750.00 | 225.00 | 64125.00 | 173.00 | 49305.00 | 149.00 | 42465.00 | 100.00 | 28500.00 | 249.00 | 70965.00 | 28500.00 | vk sam engineering, R.K.M. ELECTRICALS, Manoprabha Electricals
1.18 | ITC of 1 feet batten light/ angle holder of all types, complete with all accessories and tube/lamp etc. directly on ceiling/ wall, including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 469.00 | Nos |  | 60.00 | 28140.00 | 75.00 | 35175.00 | 150.00 | 70350.00 | 120.00 | 56280.00 | 75.00 | 35175.00 | 129.00 | 60501.00 | 75.00 | 35175.00 | 250.00 | 117250.00 | 28140.00 | vk sam engineering
1.19 | I/T/C of Ceiling fan including wiring the down rods of standard length (upto 30 cm) with 1.5 Sq.mm. FR PVC insulated copper conductor cable etc. as required: | 207.00 | Nos |  | 120.00 | 24840.00 | 140.00 | 28980.00 | 125.00 | 25875.00 | 300.00 | 62100.00 | 201.00 | 41607.00 | 99.00 | 20493.00 | 100.00 | 20700.00 | 199.00 | 41193.00 | 20493.00 | CHENNAI ENGINEERING SERVICES
1.20 | I/T/C of exhaust fan upto 450 mm in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | 31.00 | Nos |  | 150.00 | 4650.00 | 140.00 | 4340.00 | 350.00 | 10850.00 | 250.00 | 7750.00 | 518.00 | 16058.00 | 999.00 | 30969.00 | 150.00 | 4650.00 | 750.00 | 23250.00 | 4340.00 | R.K.M. ELECTRICALS
1.21 | Extra for fixing the louvers/ shutters complete with frame for a exhaust fan of all sizes. | 31.00 | Nos |  | 70.00 | 2170.00 | 140.00 | 4340.00 | 100.00 | 3100.00 | 650.00 | 20150.00 | 115.00 | 3565.00 | 999.00 | 30969.00 | 100.00 | 3100.00 | 300.00 | 9300.00 | 2170.00 | vk sam engineering
1.22 | Numbering of ceiling fan/ exhaust fan/ Light fittings as required. | 523.00 | Nos |  | 15.00 | 7845.00 | 75.00 | 39225.00 | 75.00 | 39225.00 | 5.00 | 2615.00 | 49.00 | 25627.00 | 2.99 | 1563.77 | 10.00 | 5230.00 | 99.00 | 51777.00 | 1563.77 | CHENNAI ENGINEERING SERVICES
1.23 | Supplying and laying of Following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc..direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
1.24 | 120 mm dia (OD-120 mm & ID-103 mm nominal) | 110.00 | Mtr |  | 305.00 | 33550.00 | 550.00 | 60500.00 | 350.00 | 38500.00 | 250.00 | 27500.00 | 328.00 | 36080.00 | 319.00 | 35090.00 | 300.00 | 33000.00 | 500.00 | 55000.00 | 27500.00 | Shantha ELectricals and Engineers Pvt Ltd
1.25 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 80.00 | Mtr |  | 245.00 | 19600.00 | 300.00 | 24000.00 | 300.00 | 24000.00 | 210.00 | 16800.00 | 293.00 | 23440.00 | 229.00 | 18320.00 | 300.00 | 24000.00 | 350.00 | 28000.00 | 16800.00 | Shantha ELectricals and Engineers Pvt Ltd
1.26 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep) and re-filling etc as required
1.27 | 100 mm dia | 30.00 | Mtr |  | 1100.00 | 33000.00 | 1100.00 | 33000.00 | 1200.00 | 36000.00 | 1100.00 | 33000.00 | 1415.00 | 42450.00 | 1199.00 | 35970.00 | 950.00 | 28500.00 | 1900.00 | 57000.00 | 28500.00 | Manoprabha Electricals
1.28 | 150 mm dia | 24.00 | Mtr |  | 1650.00 | 39600.00 | 1650.00 | 39600.00 | 1800.00 | 43200.00 | 1750.00 | 42000.00 | 1954.00 | 46896.00 | 1999.00 | 47976.00 | 1600.00 | 38400.00 | 2500.00 | 60000.00 | 38400.00 | Manoprabha Electricals
1.29 | Laying of one number PVC insulated ad PVC sheathed / XLPE power cable of 1.1 KV grade of following sizes in the existing RCC/ HUME /STONEWARE / METAL pipe/ HDPE pipe as required.
1.30 | Size not exceeding 35 sq.mm | 438.00 | Mtrs |  | 30.00 | 13140.00 | 110.00 | 48180.00 | 30.00 | 13140.00 | 38.00 | 16644.00 | 32.00 | 14016.00 | 19.00 | 8322.00 | 10.00 | 4380.00 | 25.00 | 10950.00 | 4380.00 | Manoprabha Electricals
1.31 | above 35 sq. mm and upto 95 sq. mm | 120.00 | Mtrs |  | 40.00 | 4800.00 | 130.00 | 15600.00 | 35.00 | 4200.00 | 60.00 | 7200.00 | 50.00 | 6000.00 | 29.00 | 3480.00 | 15.00 | 1800.00 | 32.00 | 3840.00 | 1800.00 | Manoprabha Electricals
1.32 | Size exceeding 95 sq.mm but not exceeding 185 sq.mm | 160.00 | Mtrs |  | 55.00 | 8800.00 | 150.00 | 24000.00 | 50.00 | 8000.00 | 85.00 | 13600.00 | 70.00 | 11200.00 | 39.00 | 6240.00 | 20.00 | 3200.00 | 49.00 | 7840.00 | 3200.00 | Manoprabha Electricals
1.33 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE aluminium conductor power cable of 1.1 KV grade of following sizes on wall surface as required.
1.34 | Size not exceeding 35 sq.mm | 400.00 | Mtrs |  | 40.00 | 16000.00 | 75.00 | 30000.00 | 40.00 | 16000.00 | 30.00 | 12000.00 | 45.00 | 18000.00 | 39.00 | 15600.00 | 50.00 | 20000.00 | 25.00 | 10000.00 | 10000.00 | DElite System Engineering (India) Pvt. Ltd.
1.35 | Size above 35 sq. mm and upto 95 sq. mm | 10.00 | Mtrs |  | 50.00 | 500.00 | 110.00 | 1100.00 | 45.00 | 450.00 | 60.00 | 600.00 | 75.00 | 750.00 | 69.00 | 690.00 | 100.00 | 1000.00 | 39.00 | 390.00 | 390.00 | DElite System Engineering (India) Pvt. Ltd.
1.36 | Size exceeding 95 sq.mm but not exceeding 185 sq.mm | 180.00 | Mtrs |  | 70.00 | 12600.00 | 130.00 | 23400.00 | 60.00 | 10800.00 | 85.00 | 15300.00 | 104.00 | 18720.00 | 79.00 | 14220.00 | 100.00 | 18000.00 | 49.00 | 8820.00 | 8820.00 | DElite System Engineering (India) Pvt. Ltd.
1.37 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE armoured aluminium conductor cable of 1.1 KV grade as required.
1.38 | 4C X 16 Sq.mm | 34.00 | Sets |  | 200.00 | 6800.00 | 100.00 | 3400.00 | 200.00 | 6800.00 | 350.00 | 11900.00 | 403.00 | 13702.00 | 179.00 | 6086.00 | 200.00 | 6800.00 | 399.00 | 13566.00 | 3400.00 | R.K.M. ELECTRICALS
1.39 | 3.5 C X 95 Sq.mm | 2.00 | Sets |  | 350.00 | 700.00 | 150.00 | 300.00 | 800.00 | 1600.00 | 650.00 | 1300.00 | 920.00 | 1840.00 | 349.00 | 698.00 | 400.00 | 800.00 | 750.00 | 1500.00 | 300.00 | R.K.M. ELECTRICALS
1.40 | 3.5 C X 185 Sq.mm | 4.00 | Sets |  | 625.00 | 2500.00 | 300.00 | 1200.00 | 1300.00 | 5200.00 | 950.00 | 3800.00 | 1380.00 | 5520.00 | 999.00 | 3996.00 | 600.00 | 2400.00 | 900.00 | 3600.00 | 1200.00 | R.K.M. ELECTRICALS
1.41 | Supply and Installation of maintenance free copper bonded single rod earthing system inclusive of earthing rod size dia 17.2 mm length 3000mm, copper bonded earth terminal with ultrasafe ground enhancement material ( Min 25Kg) and construction of Earth pit chamber and CI Cover for earth pit chamber etc as required. | 2.00 | Nos |  | 7500.00 | 15000.00 | 15000.00 | 30000.00 | 9500.00 | 19000.00 | 12000.00 | 24000.00 | 15000.00 | 30000.00 | 14999.00 | 29998.00 | 7000.00 | 14000.00 | 15000.00 | 30000.00 | 14000.00 | Manoprabha Electricals
1.42 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtrs |  | 530.00 | 10600.00 | 300.00 | 6000.00 | 400.00 | 8000.00 | 290.00 | 5800.00 | 460.00 | 9200.00 | 499.00 | 9980.00 | 300.00 | 6000.00 | 220.00 | 4400.00 | 4400.00 | DElite System Engineering (India) Pvt. Ltd.
1.43 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 60.00 | Mtrs |  | 195.00 | 11700.00 | 125.00 | 7500.00 | 180.00 | 10800.00 | 240.00 | 14400.00 | 151.00 | 9060.00 | 119.00 | 7140.00 | 250.00 | 15000.00 | 150.00 | 9000.00 | 7140.00 | CHENNAI ENGINEERING SERVICES
1.44 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface / recessed conduit/ submain wiring / cable as required. | 950.00 | Mtrs |  | 24.00 | 22800.00 | 10.00 | 9500.00 | 25.00 | 23750.00 | 35.00 | 33250.00 | 30.00 | 28500.00 | 19.00 | 18050.00 | 15.00 | 14250.00 | 25.00 | 23750.00 | 9500.00 | R.K.M. ELECTRICALS
1.45 | Supply, Installation, Testing & Commissioning , cubicle type body made out of 2mm thick CRCA sheet,totally enclosed, IP 42, floor mounted with channel base frame, dust and vermin proof, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system having mechanical interlocking arrangement between incomers breakers, including control wiring with 2.5 sq mm size FRLS wires/cable, interconnection, duly powder coated painting etc. including supply & installation of following switchgears,metering instruments and accessories as per specifications. INCOMER 2 No.-250 Amp 4P with Thermal Magnetic based release Moulded Case Circuit Breaker (Ics value 35 KA) with built in thermal based release unit with adjustable setting. BUSBARS 400 Amp TP and 200 Amp neutral busbars of high conductivity electrolytic quality aluminium alloy. INSTRUMENTS a)2 Nos. digital multifunction meter including suitable rating CTs for 3 phase, 4 wire operation as per specification. b)2 Sets of RYB phase indicating lamps controlled by 2 amp MCB. OUTGOING a)2 No. 125 Amp 4P Moulded Case circuit breaker (Ics value 35 KA). b)8 Nos. 40 Amp 4P MCB (Ics value 10 KA). c)10 Nos. 32 Amp 4P MCB (Ics value 10 KA). Note: a)Incoming breakers shall be mechanical interlocked with suitable accessories. b)Mechnical interlocks shall be 2 locks and 1 key type c)All breakers breaking capacities shall be ICU=ICS | 1.00 | Job |  | 155000.00 | 155000.00 | 125000.00 | 125000.00 | 179000.00 | 179000.00 | 190000.00 | 190000.00 | 334880.00 | 334880.00 | 224999.00 | 224999.00 | 150000.00 | 150000.00 | 229999.00 | 229999.00 | 125000.00 | R.K.M. ELECTRICALS
| Total in Figures |  |  |  |  | 1991810.00 |  | 2319455.00 |  | 2245325.00 |  | 2400994.00 |  | 2535802.00 |  | 2492428.77 |  | 2029110.00 |  | 2466584.00
Lowest Amount Quoted BY: vk sam engineering(1991810.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New Barracks accommodation for CISF officials at Palavanthangal at Chennai .SH_ SITC of LED Light Fixtures,Fans, Panel, earthing, cable laying etc Tender ID: 2020_AAI_60517_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | vk sam engineering | 1991810.00 | L1
| 2 | Manoprabha Electricals | 2029110.00 | L2
| 3 | LAKSHMI ELECTRICAL ENTERPRISES | 2245325.00 | L3
| 4 | R.K.M. ELECTRICALS | 2319455.00 | L4
| 5 | Shantha ELectricals and Engineers Pvt Ltd | 2400994.00 | L5
| 6 | DElite System Engineering (India) Pvt. Ltd. | 2466584.00 | L6
| 7 | CHENNAI ENGINEERING SERVICES | 2492428.77 | L7
| 8 | PREMIER ENGINEERING TECHNICS PVT. LTD. | 2535802.00 | L8