## BoQ1
Government eProcurement System Created By: Rahul S Mankar Created Date/Time: 17-Nov-2020 03:21 PM Tender Title: Construction of DVOR Building at Jalgaon Airport. SH- Electrical Works. Tender ID: 2020_AAI_60696_1
Tender Inviting Authority: Asstt. Gen. Manager (Engg-Elect), AAI, Nagpur
Name of Work :- Construction of DVOR Building at Jalgaon Airport. SH:-Electrical Works.
Contract No: Ref:- AAI/NGP/E-E/JAL/2020-21/04/DVOR/NIT-02 Date: 29.10.2020
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | Techno Electricals(GSTN-24AAGFT9086M1ZG)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH: I - Electrical Panel & Outdoor Feeder Pillars
1.01 | Supply, installation, testing and commissioning of cubicle type, floor mounted, indoor type, IP-42 rating LT panel suitable for operation on 415V, 3 phase, 4 wire 50Hz AC supply system, fabricated in totally enclosed and compartmentalized design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick for segmented gland plates, powder coating in approved shade, with TPN Aluminium Alloy bus bars of high conductivity extensible type on both sides, rated for 200 Amps with short circuit withstand capacity of 50 kA for 1 Sec., bottom base channel of MS frame of suitable size, common earth bus bar of size 25mm X 5mm at the rear with 2 nos. earth studs, connections from main bus bars to switch gears with required size of copper / aluminium conductors / bus bars, control wiring with 2.5 sqmm PVC insulated copper conductor flexible cable, i/c providing following switch gears etc. as per technical specifications as required. | 1.00 | Job | 221617.00 | 190000.00 | 190000.00 | 195252.00 | 195252.00 | 190000.00 | Manish Electricals
1.01 | INCOMER (a) 125 Amps, 4 pole MCCB (ICS = 100% ICU), Thermal release range of 100-125 (A), 30 kA (L&T DU125H Cat. No. CM90679OOLO or similar) - 4 Nos. (b) C. T. 100/5 Amps, 5 VA, CL-1 - 6 Nos. (c) LED type indication lamps for RYB & ON/OFF indication for each MCCB with control MCB. - 04 sets. (d) Multifunction meter of Class accuracy 1.0 (Schneider Conzerv 5.1 Hexa Series Product Code EM6436H / L&T MFM 4405 WL440511OOOO or similar) - 2 Nos. (e) Automatic Transfer Switch with Controller (Open Execution), Four Pole, 50 Hz, 415 V with complete protection. (Havells - IHYFCDO125/ ABB or similar) - 1 No. (f) 125 Amps, 4 pole Change over Switch with operating handle (L&T Cat No. CO21250OOOO OR similar) - 1 No. OUTGOINGS (a) 63 Amps, 4 pole MCCB (ICS = 100% ICU), Thermal release range of 50-63 (A), 30 kA (L&T DU100H Cat. No. CM97933OOH2 or similar) - 5 Nos. (b) LED type indication lamps for ON/OFF indication for each MCCB with control MCBs. - 05 Sets. NOTE: All MCCBs shall be provided with rotary operating handle and spreader terminals.
1.02 | Supply, installation, testing and commissioning outdoor feeder pillar box of minimum size 600 x 600 X 450 mm depth, suitable for operation on 415V, 3 phase, 4 wire 50Hz AC supply system, fabricated in totally enclosed, free standing, non-extensible, IP-65 rated design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates, complete with 35 kA rated 250 Amp current capacity Aluminium Bus-bars, hinged front & back door opening & locking arrangement, painted/powder coated with one coat of red oxide & two coats of enamel paint, suitable openings at the bottom for cable entries, earthing bolts etc. The box shall be mounted on MS angle stand to be grouted in 1:2:4 concrete of 100 X 100 X 300 mm depth, providing & laying in position cement concrete (PCC) of specified grade around the feeder panel boxes (PCC Size 1 Mtr X 1 Mtr X 0.15 Mtr) (1:2:4) (1 cement: 2 coarse sand: 4 graded stone aggregate 40mm nominal size) with Suitable HDPE pipe for cable in & out to the boxes, etc. as per technical specifications as required. | 2.00 | Job | 12708.00 | 18000.00 | 36000.00 | 15000.00 | 30000.00 | 30000.00 | Techno Electricals
1.03 | Supply, installation, testing and commissioning of outdoor feeder pillar box of minimum size 600 X 800 X 500 mm depth, free standing type having IP-65 protection, suitable for operation on 415V, 3 phase, 4 wire 50Hz AC supply system, fabricated in totally enclosed and compartmentalized design from CRCA sheet steel of 2 mm thick for frame work and covers, 3mm thick for segmented gland plates, powder coating in approved shade, with TPN Aluminium Alloy bus bars of high conductivity, non- extensible type, rated for 250 Amps with short circuit withstand capacity of 50 kA for 1 Sec., bottom base channel of MS frame of suitable size, common earth bus bar of size 25mm X 5mm at the rear with 2 nos. earth studs, connections from main bus bars to switch gears with required size of copper / aluminium conductors / bus bars, control wiring with 2.5 sqmm PVC insulated copper conductor flexible cable, i/c providing following switch gears etc. as per technical specifications as required. The feeder shall be mounted on MS angle stand to be grounded in 1:2:4 concrete of 100 X 100 X 300 mm depth, providing & laying in position cement concrete (PCC) of specified grade around the feeder panel boxes (PCC Size 1 Mtr X 1.2 Mtr X 0.15 Mtr) (1:2:4) (1 cement: 2 coarse sand: 4 graded stone aggregate 40mm nominal size) with Suitable HDPE pipe for cable in & out (for 3 Cables) to the feeder pillar, etc. as required and as per instructions of engineer-in-charge. | 1.00 | Job | 30699.00 | 24000.00 | 24000.00 | 75252.00 | 75252.00 | 24000.00 | Manish Electricals
1.03 | INCOMER (a) 125 Amps, 4 pole MCCB (ICS = 100% ICU), Thermal release range of 100-125 (A), 30 KA of make L&T DU125H Cat. No. CM90679OOLO or similar) - 2 Nos. NOTE: All MCCBs shall be provided with rotary operating handle and spreader terminals.
1.04 | Supply, installation, testing and commissioning of Type 1+2 Three phase Surge Protection on existing panel on input side to eliminate the direct & indirect lightning surges and switching surges from electrical power supply system. The SPD shall be have combined varistor block with encapsulated spark gap (GDT) protection for L-N and encapsulated spark gap (GDT) protection for N-PE, no following current, with visual fault signalling, voltage protection level of 1.5 kV, according to IEC / EN 61643-11, suitable for DIN rail mounting along with 32A, FP C-Series MCB in an IP-42 polycarbonate enclosure with clear front cover including complete connection with copper flexible cable and shall be as per technical specifications etc. as required. (Make: Finder / 7P.04.8.260.1025 or similar) | 2.00 | Set | 87954.00 | 24000.00 | 48000.00 | 154540.00 | 309080.00 | 48000.00 | Manish Electricals
1.05 | Supplying and fixing of IP30, FP sheet steel MCCB enclosure on surface/ recess along with 125 A, 35kA, 4 pole MCCB (ICS = 100% ICU), Thermal release range of 100-125 (A) with spreader terminals complete with connections, testing and commissioning etc. as required. (Make-L&T / DU125H or similar & Make-L&T / Size II Cat. No. CM91003OOOO or similar) | 1.00 | Job | 8269.00 | 16000.00 | 16000.00 | 18252.00 | 18252.00 | 16000.00 | Manish Electricals
2.00 | SH: II - Supply & Laying of LT Cables
2.01 | Supply of following size Aluminium conductor, XLPE insulated, PVC sheathed (FRLS), armoured power cable for working voltage 1.1 KV grade & as per IS: 7098 (Part- I) 1988 with up to date amendments of approved make & as per technical specifications etc. complete as required.
2.01 | 3.5 core X 300 sq.mm. | 1050.00 | Mtr. | 965.00 | 860.00 | 903000.00 | 787.00 | 826350.00 | 826350.00 | Techno Electricals
2.01 | 3.5 core X 120 sq.mm. | 350.00 | Mtr. | 420.00 | 400.00 | 140000.00 | 465.00 | 162750.00 | 140000.00 | Manish Electricals
2.01 | 4 core x 16 Sq.mm. | 50.00 | Mtr. | 113.00 | 130.00 | 6500.00 | 100.00 | 5000.00 | 5000.00 | Techno Electricals
2.02 | Supplying and laying of 120 mm size (OD-120 mm & ID-103 mm nominal) DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers, end caps etc. conforming to IS 16205, Part 24 complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 1300.00 | Mtr. | 279.00 | 380.00 | 494000.00 | 215.00 | 279500.00 | 279500.00 | Techno Electricals
2.03 | Providing, laying and fixing 100 mm dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep) and re-filling etc. as required. | 12.00 | Mtr. | 1035.00 | 1200.00 | 14400.00 | 1000.00 | 12000.00 | 12000.00 | Techno Electricals
2.04 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC pipe as required.
2.04 | Above 95 sq. mm and upto 185 sq. mm | 300.00 | Mtr. | 55.00 | 40.00 | 12000.00 | 45.00 | 13500.00 | 12000.00 | Manish Electricals
2.04 | Above 185 sq. mm and upto 400 sq. mm | 1000.00 | Mtr. | 97.00 | 45.00 | 45000.00 | 45.00 | 45000.00 | 45000.00 | Manish Electricals, Techno Electricals
2.04 | Up to 35 sq. mm | 50.00 | Mtr. | 26.00 | 20.00 | 1000.00 | 40.00 | 2000.00 | 1000.00 | Manish Electricals
2.05 | Retrieval of existing 1.1 KV grade LT UG cable of size exceeding 185 Sq.mm. and not exceeding 400 sq.mm. laid directly in ground including excavation of earth, sand etc. and without damaging the cable complete as required: | 100.00 | Mtr. | 165.00 | 250.00 | 25000.00 | 95.00 | 9500.00 | 9500.00 | Techno Electricals
2.06 | Extra for Excavation for cable trenches in hard rock/PCC/Bituminous not exceeding 1.5 meters in width and lift up to 1.5 meters, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 meters. | 5.00 | CuM | 584.00 | 800.00 | 4000.00 | 1752.00 | 8760.00 | 4000.00 | Manish Electricals
3.00 | SH: III - Earthing
3.01 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 6043.00 | 7000.00 | 14000.00 | 7525.00 | 15050.00 | 14000.00 | Manish Electricals
3.02 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 11781.00 | 15000.00 | 30000.00 | 10250.00 | 20500.00 | 20500.00 | Techno Electricals
3.03 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtr. | 1126.00 | 800.00 | 16000.00 | 14500.00 | 290000.00 | 16000.00 | Manish Electricals
3.04 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtr. | 451.00 | 250.00 | 5000.00 | 650.00 | 13000.00 | 5000.00 | Manish Electricals
3.05 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 10.00 | Mtr. | 912.00 | 350.00 | 3500.00 | 956.00 | 9560.00 | 3500.00 | Manish Electricals
3.06 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 10.00 | Mtr. | 180.00 | 400.00 | 4000.00 | 185.00 | 1850.00 | 1850.00 | Techno Electricals
3.07 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 1500.00 | Mtr. | 31.00 | 25.00 | 37500.00 | 25.00 | 37500.00 | 37500.00 | Manish Electricals, Techno Electricals
4.00 | SH: IV - Miscellaneous Work
4.01 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
4.01 | 3½ X 120 sq. mm (45mm) | 6.00 | Set | 466.00 | 600.00 | 3600.00 | 450.00 | 2700.00 | 2700.00 | Techno Electricals
4.01 | 3½ X 300 sq. mm (70mm) | 2.00 | Set | 931.00 | 1000.00 | 2000.00 | 500.00 | 1000.00 | 1000.00 | Techno Electricals
4.01 | 3½ X 400 sq. mm (82mm) | 2.00 | Set | 1184.00 | 1200.00 | 2400.00 | 650.00 | 1300.00 | 1300.00 | Techno Electricals
4.01 | 4 core x 16 Sq.mm (28 mm) | 10.00 | Set | 238.00 | 350.00 | 3500.00 | 185.00 | 1850.00 | 1850.00 | Techno Electricals
4.02 | Providing and laying in position cement concrete of 1:2:4 grade (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) excluding the cost of of centering, shuttering - All work up to plinth level. | 1.00 | CuM | 5945.00 | 7000.00 | 7000.00 | 6520.00 | 6520.00 | 6520.00 | Techno Electricals
5.00 | SH: V - SITC of Split ACs
5.01 | Supply of Inverter type, 5 star rated 1.5 TR split air conditioner having inverter rotary / scroll type compressor, 100% copper condenser, with cordless remote control, refrigerant type R-32, suitable for operation on 230 V AC, 50 Hz, 1-Ph power supply, suitable for operation in ambient temperature of 52 Deg.C (minimum) etc. complete as per technical specifications as required. (Make/model: Bluestar/DBTX or Voltas/ 185V JZJ or similar) | 5.00 | Each | 31336.00 | 48000.00 | 240000.00 | 35252.00 | 176260.00 | 176260.00 | Techno Electricals
5.02 | Supply of Inverter type, 5 star rated 2.0 TR split air conditioner having inverter dual / twin rotary / scroll type compressor, 100% copper condenser, with cordless remote control, refrigerant type R-32, suitable for operation on 230 V AC, 50 Hz, 1-Ph power supply, suitable for operation in ambient temperature of 52 Deg.C (minimum) etc. complete as per technical specifications as required. (Make/model: Bluestar/DATX or Voltas/ 245V ADZ or similar). | 2.00 | Each | 47833.00 | 54000.00 | 108000.00 | 42525.00 | 85050.00 | 85050.00 | Techno Electricals
5.03 | Installation, testing & commissioning of inverter type 1.5/2 TR split air conditioner by fixing indoor unit on wall/ceiling/structure and outdoor unit on wall/stand including providing & fixing suitable size duly painted / powder coated M.S. / G.I. equal angle base frame (ODU Stand), providing and fixing suction/discharge refrigerant copper piping with elastomeric nitrile rubber insulation (Up to 4 Mtrs), control cabling (Up to 4 Mtrs) from indoor to outdoor unit, fasteners, charging of refrigerant gas i/c minor civil works and all accessories etc. complete as per technical specifications as required. | 7.00 | Each | 1615.00 | 3000.00 | 21000.00 | 2500.00 | 17500.00 | 17500.00 | Techno Electricals
5.04 | Supply & fixing (Over and above 4 Mtrs included in Item No: 3) of suction/discharge refrigerant copper piping for 1.5/2 TR split AC with elastomeric nitrile rubber insulation between indoor and outdoor units with suitable size of clamp / MS hanger / MS support / MS angle as per site requirement and as per technical specifications as required. | 30.00 | Mtr. | 870.00 | 700.00 | 21000.00 | 725.00 | 21750.00 | 21000.00 | Manish Electricals
5.05 | Supply & fixing 25 mm dia. UPVC drain pipe including cutting, jointing with approved solvent cement compound as per IS 14735, etc complete as required. | 30.00 | Mtr. | 201.00 | 150.00 | 4500.00 | 145.00 | 4350.00 | 4350.00 | Techno Electricals
5.06 | Supply and laying of 3 C x 4 Sq. mm PVC insulated, FRLS PVC sheathed, unarmoured, multi stranded copper cable as per IS : 694 along with refrigerant piping between indoor and outdoor unit of 1.5/2.0 TR Split type AC units etc as required. | 30.00 | Mtr. | 114.00 | 160.00 | 4800.00 | 112.00 | 3360.00 | 3360.00 | Techno Electricals
5.07 | Supply, installation, testing and commissioning of AC timer suitable to control 2 No. 1.5 / 2.0 TR Split ACs, suitable for operation with 230 VAC +/- 15 %, 50Hz AC power supply, output contacts rating of 25 A at 230 V AC with heavy duty connectors rated for 25 Amps for both ACs, cycle time from 4 / 8 hours, with auto / manual mode, test mode etc. as per technical specifications as required. | 2.00 | Each | 3104.00 | 2500.00 | 5000.00 | 4545.00 | 9090.00 | 5000.00 | Manish Electricals
5.08 | Supply, installation, testing and commissioning of 4 KVA, 12 Amp, 170V-270V voltage stabilizer of wall mounting type with Instant Start and Intelligent time delay provisions complete etc. as required. (Make : V-Guard Model : VG400, Make : Everest Model: EW 400 or similar) | 5.00 | Each | 1485.00 | 6000.00 | 30000.00 | 4758.00 | 23790.00 | 23790.00 | Techno Electricals
5.09 | Supply, installation, testing and commissioning of 5 KVA, 15 Amp, 170V-270V voltage stabilizer of wall mounting type with Instant Start and Intelligent time delay provisions complete etc.as required. (Make : V-Guard Model : VG500, Make : Everest Model: EW 500 or similar) | 2.00 | Each | 1692.00 | 7000.00 | 14000.00 | 5525.00 | 11050.00 | 11050.00 | Techno Electricals
6.00 | SH: VI - Fire Detection & Alarm System
6.01 | Supply, Installation, testing & commissioning of fire alarm panel with minimum two loop, Intelligent Analog Addressable Fire Alarm Panel including battery back-up rechargeable battery (Minimum 12 Volts 7 Ah). The panel shall be microprocessor based with its own micro controller, memory, and fire device zone. The system shall be compatible with all kind of security and fire sensors/switches, built in real time clock operation with provision of GSM Auto Dialer facilitation (Inbuilt or externally installed) and shall be capable to auto dial minimum 5 No. mobile / telephone no. in case of any emergency /exigency, built in intelligent battery charger with deep discharge protection. The system shall be suitable for operation on continuous basis (round the clock) on 230 +/- 10%, 50Hz, single phase A.C. supply backed up with 12 V +/-10% D.C. batteries with built in power supply and battery charging circuits, complete, etc. as required. | 1.00 | Each | 72295.00 | 25000.00 | 25000.00 | 55254.00 | 55254.00 | 25000.00 | Manish Electricals
6.02 | Supply, installation, testing & commissioning of UL /EN listed (latest version) Repeater Panel having controls for system reset, accept, mute, silence alarms and self test; RS 485 communication capability; back-lit 80 character LCD display with touch screen or other keypad including suitable enclosure for panel mounting, providing all components & accessories for suitable DC power supply to the panel etc. complete as per technical specifications as required. (Make: Edwards / RLCD-C / Make: Honeywell - Morley IAS ZXr-A or similar) | 1.00 | Job | 45626.00 | 14000.00 | 14000.00 | 52525.00 | 52525.00 | 14000.00 | Manish Electricals
6.03 | Supply, installation, testing & commissioning of UL / EN listed (latest version) Addressable Intelligent multi-criteria detector (Smoke + Heat) with in-built fault isolator / isolator base, with optical sensing chamber, with visible multi-color LED Status indication, suitable for 2 wires loop connection, with all accessories like plug-in common base, base box, etc. to be installed below / above false ceiling, concealed space etc. complete with interconnections to loop cable as per technical specifications as required. (Make: Edwards / SIGA-PHD+IB / Make: Honeywell - Morley IAS - MI-PTSE-S2I or similar) | 12.00 | Each | 2335.00 | 4000.00 | 48000.00 | 3000.00 | 36000.00 | 36000.00 | Techno Electricals
6.04 | Supply, installation, testing & commissioning of UL / EN listed (latest version) Addressable intelligent fixed temperature cum rate-of-rise type Heat Detector with in-built fault isolator / isolator base, with multi-color LED status indication complete with all accessories like plug-in common base, base box, etc. to be installed below / above false ceiling, concealed space etc. complete with interconnections to loop cable as per technical specifications as required. (Make: Edwards / SIGA-HRD+IB / Make: Honeywell - Morley IAS - MI-RHSE-S2I or similar) | 1.00 | Each | 2378.00 | 4000.00 | 4000.00 | 3000.00 | 3000.00 | 3000.00 | Techno Electricals
6.05 | Supply, installation, testing & commissioning of UL / EN listed (latest version) intelligent addressable Manual Call Station / Manual Pull Station (Resettable pull / push type) with inbuilt fault isolator / isolator module, with LED for status indication, suitable for semi flush mounting and indoor use, with double gang outlet box, equipment for key operator test-reset lock, electronic or rotary switches for address setting etc. complete as per technical specifications as required. (Make: Edwards / SIGA-278 with Isolator / Make: Honeywell - Morley IAS - MI-MCP-Flex-I or similar) | 3.00 | Each | 3422.00 | 3000.00 | 9000.00 | 650.00 | 1950.00 | 1950.00 | Techno Electricals
6.06 | Supply, installation, testing & commissioning of UL / EN listed (latest version) loop powered addressable sounder cum strobe with inbuilt fault isolator / isolator module complete with all fixing accessories, interconnections to loop cable etc. complete as per technical specifications as required. (Make: Edwards / G1RF-HDVM with Isolator / Make: Honeywell - Morley IAS - MI-WSS-PR-I or similar) | 2.00 | Each | 3323.00 | 4000.00 | 8000.00 | 7525.00 | 15050.00 | 8000.00 | Manish Electricals
6.07 | Supply, Installation, testing & commissioning of UL / EN listed (Latest Version) LED Remote Indicator for getting fire indications of detectors installed above false ceiling area complete including mounting boxes with all fixing accessories, interconnections to loop cable etc. complete as per technical specifications as required. (Make: Edwards / SIGA-LED / Make: Honeywell - Morley IAS - IRK-2E or similar) | 4.00 | Each | 576.00 | 3000.00 | 12000.00 | 2522.00 | 10088.00 | 10088.00 | Techno Electricals
6.08 | Supply, installation, testing & commissioning of RS-485 to single mode fibre optic signal converter including all accessories, enclosure, connectors, cords, cards etc. to connect the fire alarm panel to repeater panel at Equipment Room through existing OFC network etc. complete as required. (Make: Honeywell / SIGA-CC1 or similar) | 2.00 | Each | 44855.00 | 40000.00 | 80000.00 | 6525.00 | 13050.00 | 13050.00 | Techno Electricals
6.09 | Supply and laying 2 core X 1.5 sq.mm. size Copper conductor, XLPE insulated, PVC sheathed (FRLS), armoured cable as per IS: 7098 (Part- I) 1988 with up to date amendments of approved make & as per technical specifications etc. complete as required. | 100.00 | Mtr. | 103.00 | 160.00 | 16000.00 | 175.00 | 17500.00 | 16000.00 | Manish Electricals
6.10 | Supply of trolley mounted CO2 type fire extinguisher of 6.5 Kgs. Capacity as per IS: 2878 with initial filling of CO2 gas as per IS: 15222 in mild steel body cylinder with powder coated finish, wheel type discharge valve, discharge hose with horn etc. complete as per technical specifications as required. | 6.00 | Each | 11023.00 | 9500.00 | 57000.00 | 5525.00 | 33150.00 | 33150.00 | Techno Electricals
| Total in Figures |  |  |  |  | 2808700.00 |  | 2982793.00
Lowest Amount Quoted BY: Manish Electricals(2808700.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of DVOR Building at Jalgaon Airport. SH- Electrical Works. Tender ID: 2020_AAI_60696_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Manish Electricals | 2808700.00 | L1
| 2 | Techno Electricals | 2982793.00 | L2