## BoQ1
Government eProcurement System Created By: Jyoti Prakash chauhan Created Date/Time: 24-Nov-2020 04:54 PM Tender Title: Construction of Pre-Engineered Airport Terminal and Associated Works at Chitrakoot Airport (Design and build Basis) SH SITC of Sub-Station Equipment and Associated Works Tender ID: 2020_AAI_60770_1
Tender Inviting Authority: <Senior Manager (E-E), Airports Authority of India, Prayagraj Airport, Prayagraj,UP.>
Name of Work: <Construction of Pre-Engineered Airport Terminal and Associted Works at Chitrakoot Airport (Design & build Basis) SH : SITC of Sub-Station Equipment & Associated Works.>
Contract No: AAI/PRG/SMEE/ENIT-06/2020-21
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | Anzen Projects Private Limited(GSTN-06AANCA5052C1ZZ) |  | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION(GSTN-09AOTPS2578C1ZC) |  | ECS ENGINEERING PVT LTD(GSTN-09AABCE5944P1Z1) |  | MEC ENGINEERS(GSTN-09AABFM1296R1ZM)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | HT PANEL BOARD Supply, Installation, Testing & Commissioning of indoor type (IP 4X) floor mounted metal clad, 11 KV Switch Board VCB panel with 3 Nos. VCBs, totally enclosed & fully interlocked, truck mounting, horizontal draw out, horizontal isolation type vacuum breaker as per IS / IEC 62271-100 (2007) for breakers & 200 (2003), for panels / IS3247 as amended up to date, having capacities as mentioned below, free standing extensible on both sides, single break, trip free mechanism, motorised charged and auto/ manually closing breaker suitable for use on 11 KV, 3 Phase, 50Hz A.C. supply with short circuit fault level of 350 MVA, complete with self contained short time current 18.4 kA for 3 sec and cable compartment, rack in and rack out mechanism, air insulated but encapsulated copper bus bars of 630 Amp capacity meeting fault level current , suitable capacity of DC power pack, breaker featured with mechanical ON / OFF indicator with hand trip device, Breaker control TNC switch and all accessories such as shunt trip coil, and auxiliary switch of 4NO+4NC, motorised and manually operated spring assisted closing mechanism, emergency trip push button, interconnections, space heaters, earthing, etc. and equipped with following switchgears and accessories, connections suitable for 3 x120 sq mm, XLPE 11 KV cable (cable entry from bottom), end termination with heat shrinkable jointing materials etc, Separate earthing switch shall be provided for cable earthing .The earthing truck shall be so designed that it is impossible to earth a live wire.
1.10 | INCOMER - consisting of following; 1 Nos. of 630 Amp , 11 KV, 3 Ph, 3P Vaccum Circuit Breaker, having Rated voltage-12 KV,rated Current -630 A, Closing Coil-24 V, DC, triping coil-24 V, DC, Spring Charging Motor-230 V, AC , with test and service limit switch actuator. Incomer having following accessories/Items- 1 No - Multifunction Meter with accuracy class 0.5, LED display of I, V, Hz, Active, Reactive , Apparent Power & Energy, Power factor, %THD , Maximum demand load, (complying with IEC 61557-12) with RS 485 port & Ethernet port and protection MCB and required accessories to complete as per technical specification. 1 No. Cast resin drawout type PTs, 11 KV / 110 V, class 0.5 accuracy,100 VA, burden including Protection HRC fuse for HT metering up to 12 KV on incomer and MCBs on secondary side protction. 3 Nos. Cast resin insulated Dual core dual ratio CTs 60/30/5 A of 15VA burden and accuracy Class -0.5 for metering and class 5P10 for protection. 1 No Digital type Ammeter of suitable rating for three phase wth selector switch- aux. supply -24 1 No Digital type Voltmeter for 3 phase, three wire,0-15 KV wth selector switch. aux. supply -24 1 No.Aux. relays for Anti Pumping Fault indication, 01 No trip circuit supervision relay, Aux. supply-24 DC. Flush mounted 01 No. Master Trip Circuit Relay, aux. supply-24 V DC, Flush mounted RYB indication lamps with back up MCB, Clear lamp for trip circuit / healthy supply & spring charged, 03 set of Breaker ON/OFF/TRIP indicating lamps. 3 Nos. of over current & short circuit 51,51N & one earth fault element with numerical IDMT relay with shunt trip on 24 volts DC, on RS 485 modbus communication consisting 3 element over current relay and earth fault, Over & under voltage,Over & under frequency. with minimum 15 trip history.
1.20 | BUSBAR 630 Amps, TP,12 KV, Copper Bus bar with heat shrinkable insulated sleeves with cast epoxy insulator to withstand full short circuit currents upto 18.4 kA for 3 second. OUTGOINGS- consisting of following; 2 Nos. - 630 Amp , 11 KV, 3 Ph, 3P Vaccum Circuit Breaker, having Rated voltage-12 KV,rated Current -630 A, Closing Coil-24 V, DC, triping coil-24 V, DC, Spring Charging Motor-230 V, AC , with test and service limit switch actuator. Each Outgoing having following accessories/Items- 1 No Digital type Ammeter of suitable rating for three phase with slector switch. 3 Nos. Cast resin insulated Dual core dual ratio CTs 60/ 30/5 A of 15VA burden and accuracy Class -0.5 for metering and class 5P10 for protection. 01 No trip circuit supervision relay, Aux. supply-24 DC. Flush mounted, 01 No. Master Trip Circuit Relay, aux. supply-24 V DC, Flush mounted, 1 No. - 3 elements auxillary relay 24 V DC, Flush mounted for oil temparature, winding temparature and bucholz alarm trip & RYB indication lamps with back up MCB, Clear lamp for trip circuit /healthy supply & spring charged, 03 set of ON/OFF/TRIP indicating lamps. 2 Nos. of over current & short circuit 51,51N & one earth fault element with numerical IDMT relay with shunt trip on 24volts DC, on RS 485 modbus communication consisting 3 element , Relay- auxillary supply-24 DC, Flush mounted, with minimum 15 trip history. All metering & protection devices, interconnections, necessary control wiring and all other accessories shall be provided as per technical specifications & technical particulars. | 1.00 | Set |  | 1850000.00 | 1850000.00 | 1035000.00 | 1221300.00 | 2000000.00 | 2360000.00 | 1041000.00 | 1228380.00 | 1200000.00 | 1416000.00 | 1221300.00 | Anzen Projects Private Limited
2.00 | Transformer Supply, Installation, Testing & Commissioning of 400 KVA 11/0.433 kV, indoor,ONAN cooled, 3 Phase, 50Hz, vector group-Dyn 11, Transformer having impedance 4.5 % copper wound with winding temperature indicator/controller , indoor type Transformer with Losses as per IS 1180 level 2 with uptodate amendments . The transformer shall be provided with OFF load tap changer on HT side with 7.5% to -7.5% in steps of 2.5 % on HT side , having cable end boxes on HV side suitable 3x 95 sqmm XLPE cable of 11kV grade and LT side suitable 2 nos x 3.5 x 300 Sqmm XLPE cable of 1.1KV , supplying and grouting of suitable MS channels with all accessories for mounting arrangement of incommer and confirming to IS 2026 (Part 1 to Part 5) & as per specification attached complete in all respects as required at site.
2.10 | The transformer shall be supplied with following Fitting & Accessories: Transformer Oil Temperature Alarm & Tripping Winding temperature relay unit with Alarm and trip Oil Level Low Alarm with trip Buchholz relay of double float type with high gas pressure alarm & trip suitable for 24 volts DC supply with complete wiring up to Marshalling box & having 2 No. potential free contact for alram, trip & annunciation. The transformers shall have bi-directional rollers, winding temperature indicator, oil temperature indicator and Buchholz relay with wiring up to the marshalling box complete. The transformers shall have first filling of oil, weather proof HT cable box. The transformer shall have suitable disconnecting chamber at the ends with min 8mm thick non-magnetic gland plate , including M. S. channel and suitable size foundation complete with earth terminals / lifting lugs and other standard accessories as required, as per relevant IS to successfully test & commission the distribution transformer as described above and as per technical specification. | 2.00 | Each |  | 650000.00 | 1300000.00 | 977500.00 | 2306900.00 | 900000.00 | 2124000.00 | 1017000.00 | 2400120.00 | 1000000.00 | 2360000.00 | 1300000.00 | Manish Electricals
3.00 | APFC Panel Supplying, installation, testing & commissioning of 150 KVAR APFC CAPACITOR PANEL factory built floor mounted with provision for auto as well as manual operation for power factor correction. Separate compartment for capacitors, 3 Phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, SMC bus bar supports,with short circuit withstand capacity of 35 KA for 1 sec , bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25 mm x 5 mm at the rear with 2 Nos. earth stud, solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination in cable alley with required size of AL conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, i/c providing following switchgears / accessories as per specifications. (Panel shall confirm to IEC 60439 & shall be IP-42 & of Form -3b construction)
3.10 | INCOMER 400 amp 4 Pole Moulded Case circuit breaker (Ics = Icu = 35 KA) -01 Nos APFC relay-12 steps, microprocessor based. 1 no.digital Voltmeter & digital Ammeter of suitable range for 3 phase, 4 wire operation with 3 CTs, selector switches, 2A MCB for controlling- 1 set , Selector switches with Auto/manual/off-complete job BUS BAR TPN aluminium bus bars of minimum 400 Amps capacity with heat shrinkable coloured sleeves and i/c SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 35KA for 1 sec.
3.20 | OUTGOING MCCB, 160A, TP, 35 kA - 2 nos. MCCB, 100A, TP, 35 kA - 3 nos. MCCB, 63A, TP, 35 kA - 4 nos. 2 Nos.Bank of 50 kVAR Mixed dielectric, heavy duty type units. 3 Nos Bank of 10 kVAR Mixed dielectric heavy duty type units. 4 Nos Bank of 5 kVAR Mixed dielectric type heavy duty type units. 9 Sets of Auxilary Control contractors of required rating. 9 Sets of Start/ Stop push buttons. 9 Sets of Indicating lamps (LED type) for capacitor ON (Green) & capacitor OFF (Red) & Trip (AMBER) 9 Sets A/M Selector Switch. 2 Sets of Axial flow fans with thermostat. | 1.00 | Each |  | 380000.00 | 380000.00 | 287500.00 | 339250.00 | 600000.00 | 708000.00 | 365000.00 | 430700.00 | 400000.00 | 472000.00 | 339250.00 | Anzen Projects Private Limited
4.00 | LT PANEL Supplying, installing, testing & commissioning of compartmentalised wall mounted / floor mounted cubicle board made from 2mm thick CRCA sheet dust & vermin proof duly phosphatized & powder coated with channel based frame suitable for operation on three phase and neutral , 415V , 50 Hz A.C. sytem including control wiring with 2.5 sq.mm. size wire, interconnection providing. Lugs, inter-earthing, painting etc. i/c providing & fixing below mentioned accessories: INCOMING : (a) 125 Amp FP MCCB having breaking capacity - 25 KA with Ics=Icu=25 KA,with thermal-magnetic release with Rotary Handle operating Mechanism - 2 No. (b) (0-125 A) Digital Ammeter with selector switch & 100/5 C.T.'s - 2 Set (c) (0-500 V) Digital Voltmeter with selector switch - 2 Set (d) Indication lamp R/Y/B with backup MCB - 2 Set of Three
4.10 | BUSCOUPLER (a) 125 Amp FP MCCB having breaking capacity - 25 KA with Ics=Icu=25 KA, with thermal-magnetic release with Rotary Handle operating Mechanism - 1 No. Panel shall be interlocked electrically & mechanically so that only two MCCB's i.e 1 incomer + buscoupler or both incomers can be switched on at a time. BUS - BAR 200 A TPN Bus bar of high conductivity electrolytic quality aluminium alloy as per specification OUTGOING : (a) 63 Amp FP MCCB having breaking capacity - 25 KA with Ics=Icu=25 KA, with Rotary Handle operating Mechanism - 4 No. with digital ammeter and CTs for each. b) 32 Amp FP C-Curve MCB - 2 No. | 1.00 | Each |  | 245000.00 | 245000.00 | 155250.00 | 183195.00 | 900000.00 | 1062000.00 | 186000.00 | 219480.00 | 190000.00 | 224200.00 | 183195.00 | Anzen Projects Private Limited
5.00 | SITC of double door dust & vermin proof outdoor floor mounted Feeder panel of size 900mm x 700mm x 300mm (minimum) on cement concrete foundations to withstand rough usage and weather. The panel shall be fabricated with 14 SWG M.S. sheet complete with hinged door on front and back with locking arrangement , doors/ covers for individual inside compartments, suitable angle / channels frame stand with legs in the bottom, lifting hooks, including grouting with cement concreate founadation, painting etc. including supplying and fixing of following accessories and making inter connections, earth connection etc. complete as per the specification attached. (a) 63-A , 4-Pole, 25-KA MCCB = 1 No. (Incomer) Icu=Ics (b) 32 A C Series TPN MCB = 4 Nos (Outgoing) (c) C.T. - 1 set , 50/5 AMP, Class - 1.0 (d) Digital type Voltmeter, Ammeter. (e) 100 Amp , 4 Strip suitable length Al Busar - 1Set (f) 2 way 40-A connector = 16 nos. (g) RYB pilot indicating lamps (Cluster LED type) with 5 A MCB with toggle switches-1 set. (h) (0-24) Hrs analog timer with ML 3 contactor-1 No. (i) Inter connection with suitable size copper flexible cable | 1.00 | Each |  | 75000.00 | 75000.00 | 69000.00 | 81420.00 | 700000.00 | 826000.00 | 50000.00 | 59000.00 | 90000.00 | 106200.00 | 59000.00 | ECS ENGINEERING PVT LTD
6.00 | SUPPLY & LAYING OF CABLES & END TERMINATION Supply of 3 Core, following sizes of XLPE insulated PVC sheathed aluminium conductor armoured Power cable of 11 KV grade (11 KV earthed system) conforming to IS: 7098 (part-II) amended up to date. i) 3C x 95 Sq mm | 150.00 | Mtr |  | 650.00 | 97500.00 | 1132.04 | 200370.55 | 350.00 | 61950.00 | 520.00 | 92040.00 | 512.00 | 90624.00 | 61950.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
7.00 | Supply of followin sixes of 1.1 KV grade XLPE insulated PVC sheathed, Alumimium Conductor armoured power cable confirming to IS 7098 (Part-I) 1988 amended upto date : 3.5C x 300 Sq mm | 1900.00 | Mtr |  | 870.00 | 1653000.00 | 990.49 | 2220689.79 | 1050.00 | 2354100.00 | 830.00 | 1860860.00 | 840.00 | 1883280.00 | 1653000.00 | Manish Electricals
8.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of size up to 95 Sq. mm. direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. | 100.00 | Mtr |  | 300.00 | 30000.00 | 345.00 | 40710.00 | 150.00 | 17700.00 | 250.00 | 29500.00 | 240.00 | 28320.00 | 17700.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of size up to 95 Sq. mm. in the existing RCC/HUME/ HDPE/METAL pipe as required. | 30.00 | Mtr |  | 40.00 | 1200.00 | 172.50 | 6106.50 | 150.00 | 5310.00 | 100.00 | 3540.00 | 120.00 | 4248.00 | 1200.00 | Manish Electricals
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing masonry open duct as required. i) Upto 120 sq. mm | 10.00 | Mtr |  | 40.00 | 400.00 | 172.50 | 2035.50 | 150.00 | 1770.00 | 100.00 | 1180.00 | 70.00 | 826.00 | 400.00 | Manish Electricals
11.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. i) Above 185 sq. mm and upto 400 sq. mm | 50.00 | Mtr |  | 40.00 | 2000.00 | 230.00 | 13570.00 | 180.00 | 10620.00 | 100.00 | 5900.00 | 115.00 | 6785.00 | 2000.00 | Manish Electricals
12.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1KV grade of following size direct in ground including excavation, sand cushioning,protective covering and refilling the trench etc as required. i) Above 185 sq. mm and upto 400 sq. mm | 900.00 | Mtr |  | 280.00 | 252000.00 | 345.00 | 366390.00 | 140.00 | 148680.00 | 250.00 | 265500.00 | 220.00 | 233640.00 | 148680.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
13.00 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required. i) Above 185 sq. mm and upto 400 sq. mm | 900.00 | Mtr |  | 250.00 | 225000.00 | 345.00 | 366390.00 | 150.00 | 159300.00 | 175.00 | 185850.00 | 200.00 | 212400.00 | 159300.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
14.00 | Supplying and laying of following size 100 mm dia GI Pipe, B-Class, ISI marked along with all accessories like socket, bend, complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. i)100 mm dia GI Pipe | 36.00 | Mtr |  | 900.00 | 32400.00 | 1324.80 | 56277.50 | 650.00 | 27612.00 | 1370.00 | 58197.60 | 1100.00 | 46728.00 | 27612.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
15.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required. i) Above 185 sq. mm and upto 400 sq. Mm | 50.00 | Mtr |  | 40.00 | 2000.00 | 230.00 | 13570.00 | 120.00 | 7080.00 | 100.00 | 5900.00 | 135.00 | 7965.00 | 2000.00 | Manish Electricals
16.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. i) 3.5C x 300 Sq mm | 4.00 | Each |  | 1200.00 | 4800.00 | 2629.24 | 12410.04 | 1500.00 | 7080.00 | 1275.00 | 6018.00 | 3200.00 | 15104.00 | 4800.00 | Manish Electricals
17.00 | Suppy and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 3 core X 95 sqmm XLPE aluminium conductor cable of 11 KV (UE) grade as required. | 5.00 | Set |  | 15000.00 | 75000.00 | 2213.69 | 13060.79 | 4780.00 | 28202.00 | 5000.00 | 29500.00 | 3575.00 | 21092.50 | 13060.79 | Anzen Projects Private Limited
18.00 | Suppy and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 3 core X 95 sqmm XLPE aluminium conductor cable of 11 KV (UE) grade as required. | 1.00 | Set |  | 18000.00 | 18000.00 | 15000.31 | 17700.37 | 4780.00 | 5640.40 | 6300.00 | 7434.00 | 3715.00 | 4383.70 | 4383.70 | MEC ENGINEERS
19.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. i)3½ X 300 sq. mm | 2.00 | Each |  | 4000.00 | 8000.00 | 6487.84 | 15311.30 | 10000.00 | 23600.00 | 3100.00 | 7316.00 | 3620.00 | 8543.20 | 7316.00 | ECS ENGINEERING PVT LTD
20.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required.
20.10 | i) 63 mm dia (OD-63 mm & ID-51 mm nominal) | 10.00 | Mtr. |  | 160.00 | 1600.00 | 296.12 | 3494.27 | 700.00 | 8260.00 | 200.00 | 2360.00 | 170.00 | 2006.00 | 1600.00 | Manish Electricals
20.20 | i) 90 mm dia (OD-90 mm & ID-76 mm nominal) | 30.00 | Mtr. |  | 220.00 | 6600.00 | 485.30 | 17179.62 | 800.00 | 28320.00 | 300.00 | 10620.00 | 200.00 | 7080.00 | 6600.00 | Manish Electricals
21.00 | Supplying of Rubber hand gloves suitable for 11 KV. | 2.00 | Pair |  | 600.00 | 1200.00 | 1380.00 | 3256.80 | 1000.00 | 2360.00 | 1000.00 | 2360.00 | 650.00 | 1534.00 | 1200.00 | Manish Electricals
22.00 | Supplying and fixing of Shock treatment chart both in Hindi & English and framed with 5mm thick glass as required.(Frame A2 Size). | 2.00 | Each |  | 250.00 | 500.00 | 345.00 | 814.20 | 450.00 | 1062.00 | 2000.00 | 4720.00 | 3000.00 | 7080.00 | 500.00 | Manish Electricals
23.00 | Supply and fixing single line diagram, schematic diagrams etc. of A1 size on suitable Aluminium sheet including lamination etc. as required complete on wall. | 2.00 | Job |  | 3000.00 | 6000.00 | 3450.00 | 8142.00 | 5000.00 | 11800.00 | 2000.00 | 4720.00 | 6000.00 | 14160.00 | 4720.00 | ECS ENGINEERING PVT LTD
24.00 | Supply and fixing of 9 ltr chemical foam type fire extinguisher | 1.00 | Each |  | 6000.00 | 6000.00 | 3680.00 | 4342.40 | 3000.00 | 3540.00 | 5000.00 | 5900.00 | 10000.00 | 11800.00 | 3540.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
25.00 | Providing of set of 04 Nos. 9.5 Ltr. Capacity GI Bucket painted in post office red colour with prior coat of Red Oxide paint and written with white paint "FIRE" and mounted on MS Angle iron frame with bracket of appropriate size and capacity including fillings sand etc. complete as required. | 2.00 | Set |  | 3000.00 | 6000.00 | 5175.00 | 12213.00 | 400.00 | 944.00 | 2100.00 | 4956.00 | 6000.00 | 14160.00 | 944.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
26.00 | Supply of First Aid Box with medicines, accessories as approved by St.John Ambulance Brigade/Indian Red Cross conforming to IS:2217-1963. | 1.00 | Each |  | 400.00 | 400.00 | 4600.00 | 5428.00 | 650.00 | 767.00 | 2000.00 | 2360.00 | 2000.00 | 2360.00 | 400.00 | Manish Electricals
27.00 | Supplying and fixing of flame retardant electrical insulation mat having no adverse effect of mineral oil, high insulation resistance and water proof of nominal size: 2.5mm +/- 10% thick and 1000mm +/-20mm wide Antistatic Electric Insulated Synthetic Mat confirming to IS: 15652: 2006 with upto date amendments suitable for 11 KV installation alongwith adhesive/resin, sealing material and similar type of taping on sealing at all joints and corners as per recommendations etc as required .The Mat shall be ISI marked. Its leakage current at 11 KV shall not be more then 10 mA.The mat shall be welded by hot gas lending with filler martial method by making V grove cut at joints with suitable welding cord of insulation material of matching colour to provide a seamless jointed surface as per IS:8002 | 10.00 | Sq. Mtr |  | 1200.00 | 12000.00 | 1150.00 | 13570.00 | 2800.00 | 33040.00 | 1500.00 | 17700.00 | 4000.00 | 47200.00 | 12000.00 | Manish Electricals
28.00 | Supplying and fixing of nominal 2.0 mm thick Electric Insulated Synthetic Mat of conforming to IS:15652:2006 and meeting the requirements of IS 5216, IS 8437, IEC-479 Pub-1, alongwith suitable adhesive /chemibound, pu-resin, water proofing compound and sealing material as per in service recommendations of Annexure-'A' 'Clause C' of IS:15652 and Suitable for Class - A upto 3.3 KV AC & 240 V DC without HT Trolley movement. | 10.00 | Sq. Mtr |  | 900.00 | 9000.00 | 632.50 | 7463.50 | 2500.00 | 29500.00 | 1200.00 | 14160.00 | 3500.00 | 41300.00 | 7463.50 | Anzen Projects Private Limited
29.00 | Providing and fixing H.T. danger notice plate of 250 mm X 200 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 4.00 | Each |  | 150.00 | 600.00 | 345.00 | 1628.40 | 150.00 | 708.00 | 250.00 | 1180.00 | 450.00 | 2124.00 | 600.00 | Manish Electricals
30.00 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 6.00 | Each |  | 150.00 | 900.00 | 345.00 | 2442.60 | 150.00 | 1062.00 | 250.00 | 1770.00 | 250.00 | 1770.00 | 900.00 | Manish Electricals
31.00 | Supplying and fixing of Wall mounted wooden Key Board of Size 450 x 600 mmx 150 mm depth suitable with 70 key pins etc complete as required. | 1.00 | Each |  | 300.00 | 300.00 | 6900.00 | 8142.00 | 2500.00 | 2950.00 | 3000.00 | 3540.00 | 650.00 | 767.00 | 300.00 | Manish Electricals
32.00 | Providing and fixing of advance technology earth electrode earthing system fabricated from hot deep galvanized pipes ( pipe in pipe technology) & cavity between pipes pressure filled with highly conductive non-corrosive crystalline material complete with chemically modified homogeneous earth enhancing compound (back fill compound 2x25 Kg) to treat the soil for lowering the effective ground impedance for each earth pit to make it maintenance free and to minimize the ground voltage potential rise i/c excavation of earth pit suitable to accommodate earth electrode, prefabricated CC enclose with MS cover plate having locking arrangement all as reqd. & conforming to (IS:3043 : 1987) duly CPRI/ERDA approved all as required & as specified for size : - Outer pipe dia = 80mm Inner pipe dia = 40mm Length of electrode = 3 Mtr | 18.00 | Set |  | 12000.00 | 216000.00 | 14950.00 | 317538.00 | 6500.00 | 138060.00 | 8500.00 | 180540.00 | 10000.00 | 212400.00 | 138060.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
33.00 | Providing and fixing of advance technology earth electrode earthing system fabricated from pure copper (99.9%) pipes (pipe in pipe technology) & cavity between pipes pressure filled with highly conductive non-corrosive crystalline material complete with chemically modified homogeneous earth enhancing compound (back fill compound 2x25 Kg) to treat the soil for lowering the effective ground impedance for each earth pit to make it maintenance free and to minimize the ground voltage potential rise i/c excavation of earth pit suitable to accommodate earth electrode, prefabricated CC enclose with MS cover plate having locking arrangement all as reqd. & conforming to (IS:3043 : 1987) duly CPRI/ERDA approved all as required & as specified for Size : - Outer pipe dia = 80mm Inner pipe dia = 40mm Length of electrode = 3 Mtr | 10.00 | Set |  | 21000.00 | 210000.00 | 30561.25 | 360622.75 | 8500.00 | 100300.00 | 16000.00 | 188800.00 | 16000.00 | 188800.00 | 100300.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
34.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2.00 | Set |  | 7000.00 | 14000.00 | 14375.00 | 33925.00 | 2500.00 | 5900.00 | 6000.00 | 14160.00 | 4500.00 | 10620.00 | 5900.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
35.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 60.00 | Mtr. |  | 700.00 | 42000.00 | 634.80 | 44943.84 | 250.00 | 17700.00 | 875.00 | 61950.00 | 850.00 | 60180.00 | 17700.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
36.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 110.00 | Mtr. |  | 180.00 | 19800.00 | 219.65 | 28510.57 | 250.00 | 32450.00 | 190.00 | 24662.00 | 120.00 | 15576.00 | 15576.00 | MEC ENGINEERS
37.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 60.00 | Mtr. |  | 900.00 | 54000.00 | 1351.37 | 95676.64 | 450.00 | 31860.00 | 1170.00 | 82836.00 | 1110.00 | 78588.00 | 31860.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
38.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 60.00 | Mtr. |  | 450.00 | 27000.00 | 569.36 | 40311.04 | 350.00 | 24780.00 | 570.00 | 40356.00 | 370.00 | 26196.00 | 24780.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
39.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 40.00 | Mtr. |  | 600.00 | 24000.00 | 1002.80 | 47332.16 | 450.00 | 21240.00 | 733.00 | 34597.60 | 850.00 | 40120.00 | 21240.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
40.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 60.00 | Mtr. |  | 160.00 | 9600.00 | 201.25 | 14248.50 | 250.00 | 17700.00 | 155.00 | 10974.00 | 120.00 | 8496.00 | 8496.00 | MEC ENGINEERS
41.00 | Providing and fixing of lightning conductor finial, made of 25mm dia 1000 mm, long G.I. tube, having single prong at top, with 85mm dia 6mm thick G.I. base plate including holes etc. complete as required. | 4.00 | Each |  | 1200.00 | 4800.00 | 10350.00 | 48852.00 | 4500.00 | 21240.00 | 2000.00 | 9440.00 | 562.00 | 2652.64 | 2652.64 | MEC ENGINEERS
42.00 | Providing and fixing GI tape 20mm x 3mm thick on parapet or surface of wall for lightning conductor as required. (for horizontal run). | 20.00 | Mtr |  | 425.00 | 8500.00 | 94.30 | 2225.48 | 85.00 | 2006.00 | 94.00 | 2218.40 | 132.00 | 3115.20 | 2006.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
43.00 | Providing and fixing G.I. tape 20mm x 3mm thick on parapet or surface of wall for lightning conductor as required. (For vertical run.) | 60.00 | Mtr |  | 560.00 | 33600.00 | 94.30 | 6676.44 | 85.00 | 6018.00 | 100.00 | 7080.00 | 210.00 | 14868.00 | 6018.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
44.00 | Providing and fixing testing joint, made of 20mm x 3mm thick G.I. strip, 125mm long with 4 Nos. of G.I. bolts, nuts, check nuts and spring washers etc. complete as required. | 4.00 | Each |  | 600.00 | 2400.00 | 1725.00 | 8142.00 | 200.00 | 944.00 | 100.00 | 472.00 | 122.00 | 575.84 | 472.00 | ECS ENGINEERING PVT LTD
45.00 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the finial or any other metallic object) by riveting / nut bolting/ sweating and soldering etc as required. | 4.00 | Each |  | 350.00 | 1400.00 | 345.00 | 1628.40 | 200.00 | 944.00 | 100.00 | 472.00 | 112.00 | 528.64 | 472.00 | ECS ENGINEERING PVT LTD
46.00 | Supply,installation,testing & commissioning of fully autonomous, CPRI tested early streamer emission air terminal (ESEAT) with (gain in triggering time) of minimum 30 µs, radius of protection 55 meters in level II protection zone when installed on 5 meter mast ( 2 metre SS mounting mast) & 3mtr GI mast along with other accessories for installing ESELC on the roof top of the Building for the protection structure from direct lightning strikes etc. complete as required. Make :- ABB, OPR 30 ESE or Equivalent AAI approved make. | 1.00 | Job |  | 120000.00 | 120000.00 | 212750.00 | 251045.00 | 45000.00 | 53100.00 | 130000.00 | 153400.00 | 100000.00 | 118000.00 | 53100.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
47.00 | Supply and laying of 70 sq. mm copper flexible cable for down conductor including suitable clamps and other accessories from air terminal to the earth pit as per site requirement. | 15.00 | Mtr |  | 750.00 | 11250.00 | 754.68 | 13357.77 | 95.00 | 1681.50 | 720.00 | 12744.00 | 700.00 | 12390.00 | 1681.50 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
48.00 | Supply of lightning transient event counter resettable 6 digit LCD display with in built lithium battery in IP67 rating enclosure with transparent lid, mounting arrangements etc., as required. | 1.00 | Each |  | 35000.00 | 35000.00 | 57500.00 | 67850.00 | 50000.00 | 59000.00 | 12000.00 | 14160.00 | 18000.00 | 21240.00 | 14160.00 | ECS ENGINEERING PVT LTD
49.00 | S.I.T.C of following sizes Single Sided / Double Sided openable glow sign board of thickness 70mm minimum for single sided and 100mm for double sided board. Signage shall be made out of 1.44mm thick aluminum extruded profiles with concealed hinged profile system, extrusions with anodizing / epoxy powder coating of approved shade & colour. The text (in two language) / signage matter shall be electro cut computerized automated self-adhesive vinyl graphics of 3M black out film and yellow message to be created by using 3M yellow 3630-015 translucent film, to be transferred on front side of clear cast acrylic sheet of 5 mm thick of A-cast make of malaysia, acrylic sheet to be pasted with 3M VHB (Very High Bond) double side adhesive tape in extruded aluminum section and easy for graphic changes, (single sided shall have 1.5mm thick Aluminum sheet for back). The illumination source shall be of LED's (CREE / Nichia / Sharp/ Philips (Lumade) / Osram/ Edison) with suitable individual current regulator & driver suitable for operation on 150-270V AC, 50Hz supply and LED shall be fixed inside the frame to obtain uniform illumination, Lumen output – 100 lumen per watt, mean life (burning hours)-50000 hrs burning life with 80% output, along with required internal wiring, connectors, earthing the body etc. Signage board shall be suitable for ceiling /wall/side mounting. Complete job, as required, as per specifications & approved drawing and direction of Engineer-in-charge.
49.10 | 1700mm x 400mm x 70mm thick – Single Sided | 12.00 | Each |  | 28000.00 | 336000.00 | 8762.38 | 124075.32 | 500.00 | 7080.00 | 9500.00 | 134520.00 | 4500.00 | 63720.00 | 7080.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
49.20 | 1700mm x 400mm x 100mm thick – Double Sided | 1.00 | Each |  | 28000.00 | 28000.00 | 8762.38 | 10339.61 | 650.00 | 767.00 | 11500.00 | 13570.00 | 5000.00 | 5900.00 | 767.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
49.30 | 400mm x 400mmx70mm thick– Single Sided | 12.00 | Each |  | 7000.00 | 84000.00 | 2325.56 | 32929.93 | 500.00 | 7080.00 | 6000.00 | 84960.00 | 4500.00 | 63720.00 | 7080.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
50.00 | Supply, Installation, Testing and Commissioning of Hydro Pneumatic Pump System (01 Working + 01 Standby ) veritical in-line multi stage booster centrifugal SS-316 pump motor sets of size 1.5 HP (1.1KW) with Flow 9000 LPH at Head 25 Mtrs (Each Pump) sutiable for Operation on 415 V, 50 Hz, 3 Phase AC Supply with 100 Ltr. .Pneumatic balancing tank, mounting skid, foot valve, GI Suction & discharge pipes, fittings, cast brass/virigin brass valves, CI Strainers suction head, etc. each pump shall have TEFC 2900 RPM 3 Phase electric motor includes pressure switches, VFD based control panel with starters, protection relays, cable, interlocking with level and pressure switches, suction, delivery piping all connections etc. complete as required. (Make : Crompton Greaves, Kirloskar, Wilo) | 1.00 | set |  | 550000.00 | 550000.00 | 138000.00 | 162840.00 | 50000.00 | 59000.00 | 75000.00 | 88500.00 | 408000.00 | 481440.00 | 59000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
51.00 | Providing laying, testing & commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. on surface / ground by providing MS support and painting with two coats of synthetic enamel paint of required shade, complete as required as per site condition & direction of EIC. sizes-150 mm dia. i) 150 mm Dia. | 650.00 | Mtr |  | 1400.00 | 910000.00 | 2560.00 | 1963520.00 | 350.00 | 268450.00 | 1750.00 | 1342250.00 | 1500.00 | 1150500.00 | 268450.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
52.00 | Providing laying, testing & commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the trench etc. of following sizes complete as required. i)150 mm Dia. | 100.00 | Mtr |  | 1400.00 | 140000.00 | 2600.00 | 306800.00 | 350.00 | 41300.00 | 1800.00 | 212400.00 | 1446.00 | 170628.00 | 41300.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
53.00 | Supplying and fixing, testing & commissioning of double flanged butterfly valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat ISI marked complete with nuts, bolts, washers, gaskets, conforming relavent IS 780 of following sizes as required. (a) 150 mm dia | 2.00 | Each |  | 9000.00 | 18000.00 | 9200.00 | 21712.00 | 450.00 | 1062.00 | 8000.00 | 18880.00 | 9200.00 | 21712.00 | 1062.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
54.00 | Providing, installation, testing and commissioning of dual plate non-return valve of following sizes confirming to IS : 5312 (ISI marked)complete with rubber gasket, GI bolts, nuts, washers etc. as required. (a) 150 mm dia | 2.00 | Each |  | 8000.00 | 16000.00 | 9200.00 | 21712.00 | 450.00 | 1062.00 | 5000.00 | 11800.00 | 16480.00 | 38892.80 | 1062.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
55.00 | SITC of 1 HP, single phase,2800 rpm sewage submersible cutter pump set suitable for operation on 230 V, 1-phase, 50 Hz, A.C. power supply with discharge range 300-50 LPS, head range 6-16 mtr. including providing & fixing 50 mm outlet dia B-class GI pipe up to 15 mtr. etc. complete as required & as per the direction of EIC. (Make : Crompton CCPM12 or equivalent AAI approved make list) | 2.00 | Each |  | 15000.00 | 30000.00 | 115000.00 | 271400.00 | 16000.00 | 37760.00 | 36000.00 | 84960.00 | 125000.00 | 295000.00 | 30000.00 | Manish Electricals
56.00 | S.I.T.C. of following sizes aircurtains suitable for mounting on height upto 10 feet & having stainless steel construction, cross flow type impellers, A.B.S. Plastic/S.S. grills & with continuous rating single phase motor etc. complete as per site requirement. (Make: Techno Mech/Russel/Approved equivalent) a)2000mm | 4.00 | Each |  | 18000.00 | 72000.00 | 28750.00 | 135700.00 | 20000.00 | 94400.00 | 32000.00 | 151040.00 | 25000.00 | 118000.00 | 72000.00 | Manish Electricals
57.00 | SITC of fully automatic wall mounted hand drier with stainless steel brushed finished casing, brushless motor heater assembly with high and low temperature cut off having 1150-1800 Watt heating capacities,minimum air speed of 13m/sec including all accessories with adjustable sensing between 10 to 30 cm and suitable for operation on 230 Volt +/- 10V, 50 Hz single phase AC supply etc complete as required and as per specifications. | 10.00 | Each |  | 15000.00 | 150000.00 | 14950.00 | 176410.00 | 15000.00 | 177000.00 | 6500.00 | 76700.00 | 30000.00 | 354000.00 | 76700.00 | ECS ENGINEERING PVT LTD
58.00 | Supply, installation, Testing and Commissioning of 5 KVA Capacity, 1 phase in / 1 Phase out online UPS with PWM IGBT technology pure sine wave output.suitable to operate at 230V, 50Hz, 1 Phase AC supply and delivering 1phase output and necessary safety protection. The job also includes SITC of 12V, SMF batteries to give a backup time of minimum 30 minutes along with MS battery rack, connectors, wiring between battery bank and UPS with insulated copper conductor of required size as per site requirement etc. as required. UPS & Batteries should be As per AAI Approved makes and Warranty on UPS and Battries should be for 02 Years. | 1.00 | JOB |  | 70000.00 | 70000.00 | 176180.00 | 207892.40 | 30000.00 | 35400.00 | 124000.00 | 146320.00 | 110000.00 | 129800.00 | 35400.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
59.00 | Supply, installation, testing and commissioning of frangible & illuminated wind direction indicator confirming to ICAO Annex 14, volume I and suitable for operation on 230 V, 50 Hz, single phase AC supply and consist of following complete as required. a) 4.5 Meter height FRP frangible pole/mast. The frangibility shall confirm to ICAO Annex 14 & Aerodrome design manual Part-VI/FAA. b) The color of pole/mast shall be red/white. c) Four nos, LED lamps along with Lamps mounting arrangement for outdoor conditions. d) One no. LED Aviation obstruction light having aluminium cast body and red polycarbonate dome. Internal wiring, provision for remote control operation. Providing and laying suitable cement concrete foundation for installation of WDI as per OEM recommendations & as per direction of EIC. | 1.00 | JOB |  | 280000.00 | 280000.00 | 92000.00 | 108560.00 | 20000.00 | 23600.00 | 175000.00 | 206500.00 | 465000.00 | 548700.00 | 23600.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
60.00 | Supply,Installation, testing and commissioning of Rotating Aerodrome Beacon on the top of ATC building complete with light weight aluminium enclosure, heavy duty gear motor for 24/36 flashes per minute with 12 RPM motor equipped with 1000 Watt lamp suitable for operation on 220/240 volt, 50 Hz, single phase AC power supply meeting latest ICAO Annexture-14 requirements all as required. | 1.00 | JOB |  | 640000.00 | 640000.00 | 644000.00 | 759920.00 | 20000.00 | 23600.00 | 600000.00 | 708000.00 | 760000.00 | 896800.00 | 23600.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
61.00 | SITC of landing direction indicator consisting of three Aluminum limb having length of 4000 mm supported by 50 mm dia aliminum pipe & frangible coupling with flagges, LED lamp fixture along with glass dome (IP65), with control box having 2 contactos , led indicatos complete with wiring, suitable to operate for 230V ac,50 Hz supply with accessories ,meeting latest ICAO Annexture-14 requirements all as required as per attached technical specification. | 1.00 | JOB |  | 260000.00 | 260000.00 | 172500.00 | 203550.00 | 10000.00 | 11800.00 | 200000.00 | 236000.00 | 212000.00 | 250160.00 | 11800.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
62.00 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m, including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, within a lead of 50 m :All kinds of soil Pipes, cables etc, not exceeding 80 mm dia. | 100.00 | Mtr |  | 400.00 | 40000.00 | 115.00 | 13570.00 | 200.00 | 23600.00 | 150.00 | 17700.00 | 500.00 | 59000.00 | 13570.00 | Anzen Projects Private Limited
63.00 | Excavating trenches of required width for pipes, cables, etc, including excavation for sockets, depth upto 1.5 m, including getting out the excavated materials, returning the soil as required in layers not exceeding 20 cm in depth, including consolidating each deposited layers by ramming, watering etc., stacking serviceable material for measurements and disposal of unserviceable material as directed, within a lead of 50 m :Ordinary rock Pipes, cables etc. not exceeding 80 mm dia | 737.00 | Mtr |  | 350.00 | 257950.00 | 30.00 | 26089.80 | 160.00 | 139145.60 | 250.00 | 217415.00 | 500.00 | 434830.00 | 26089.80 | Anzen Projects Private Limited
64.00 | Providing and fixing G.I. pipes complete with G.I. fittings including trenching and refilling etc. External work 50 mm dia nominal bore. | 837.00 | Mtr |  | 450.00 | 376650.00 | 300.00 | 296298.00 | 80.00 | 79012.80 | 648.00 | 640003.68 | 550.00 | 543213.00 | 79012.80 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
| Total in Figures |  |  |  |  | 11394350.00 |  | 13790978.79 |  | 11629000.30 |  | 12203142.28 |  | 13736042.52
Lowest Amount Quoted BY: Manish Electricals(11394350.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of Pre-Engineered Airport Terminal and Associated Works at Chitrakoot Airport (Design and build Basis) SH SITC of Sub-Station Equipment and Associated Works Tender ID: 2020_AAI_60770_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Manish Electricals | 11394350.00 | L1
| 2 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION | 11629000.30 | L2
| 3 | ECS ENGINEERING PVT LTD | 12203142.28 | L3
| 4 | MEC ENGINEERS | 13736042.52 | L4
| 5 | Anzen Projects Private Limited | 13790978.79 | L5