## BoQ1
Government eProcurement System Created By: Ashvin Kumar Singh Created Date/Time: 20-Nov-2020 12:14 PM Tender Title: Construction of 4 nos. Self-Supported Steel Roof Structures for Cargo building at Chandigarh International Airport Ltd., Mohali. S.H. Electrical Works Tender ID: 2020_AAI_61338_1
Tender Inviting Authority: Asstt. General Manager (Engg- Elect.), Chandigarh International Airport Ltd.(CHIAL), Mohali (PB)
Name of Work: Construction of 4 nos. Self-Supported Steel Roof Structures for Cargo building at Chandigarh International Airport Ltd., Mohali. S.H: Electrical Works.
Contract No: 0172-2242404, 0172-2242434
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ARNAV ENGINEERING CONSULTANCY SERVICES(GSTN-07ABKFA7102Q1Z4)
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer) as required. 8 way (4 + 24), Double door | 4.00 | EA | 100.00 | 5843.00 | 23372.00 | 23372.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
2.00 | Supplying and fixing following rating, four pole, 415 V, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63A | 6.00 | EA | 100.00 | 634.00 | 3804.00 | 3804.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
3.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Triple pole and neutral 32 Amp = 9 Nos. | 9.00 | EA | 10.00 | 825.00 | 7425.00 | 7425.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
4.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole 6 Amp = 12 Nos 16 Amp= 16 Nos | 28.00 | EA | 100.00 | 151.00 | 4228.00 | 4228.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
5.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required. 4 X 2.5 sq. mm + 2 X 2.5 sq. mm earth wire | 120.00 | Metre | 100.00 | 257.00 | 30840.00 | 30840.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
6.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.. 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 120.00 | Metre | 100.00 | 173.00 | 20760.00 | 20760.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
7.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 36.00 | Point | 100.00 | 899.00 | 32364.00 | 32364.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
8.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc as required. Group C | 68.00 | Point | 10.00 | 527.00 | 35836.00 | 35836.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
9.00 | Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/recessed steel conduit alongwith 2 Nos. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 200.00 | Metre | 100.00 | 297.00 | 59400.00 | 59400.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
10.00 | Wiring for light/ power plug with 2X4 sq. mm FR PVC insulated copper conductor single core cable in surface/ recessed steel conduit along with 1 No 4 sq. mm FR PVC insulated copper conductor single core cable for loop earthing as required. | 200.00 | Metre | 100.00 | 200.00 | 40000.00 | 40000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
11.00 | Supplying and fixing metal box of 180mm X 100mm X 60mm deep (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including providing and fixing 6 pin 5/6 & 15/16 A socket outlet and 15/16 A piano type switch, connections, painting etc. as required. | 20.00 | EA | 100.00 | 307.00 | 6140.00 | 6140.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
12.00 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required. Telephone socket outlet | 20.00 | EA | 100.00 | 57.00 | 1140.00 | 1140.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
13.00 | Supply and fixing of following RJ-45 connectivity Simplex Faceplate with RJ-45 Gangbox, information outlet with shutter compliant to TIA 568A/B with colour coding complete. | 20.00 | EA | 10.00 | 183.00 | 3660.00 | 3660.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
14.00 | Supply, Installation, Testing and Commisssioning of Wall mounted Fan suitable for operation on 220V, 50 HZ, single phase AC Supply with Aerodynamically designed semi transparent PP blades having higher air delivery, pull cord switch for speed regulation and oscillation control & minimal noise levels including all accessories as required. Sweep (400mm) | 16.00 | Job | 100.00 | 1843.00 | 29488.00 | 29488.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
15.00 | Supply Installation, Testing and Commisssioning of following sizes of heavy duty exhaust fan suitable for operation on 220V, 50 HZ, single phase AC Supply with anti corroisive treatment and attractive metallic finish, minimal noise levels including all accessories as per IS standard complete as required and suitable for installation at angle/support structure as specified. Sweep: (300 mm), 900 rpm | 8.00 | Job | 100.00 | 2409.00 | 19272.00 | 19272.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
16.00 | Supply, Installation, Testing and Commissioning of 100 W High bay LED light fixture (dia=26cm) of approved make having THD less than 10% with high pressure die cast housing having IP65 including all accessories as per relevent IS standard complete as required and suitable for installation at beam/angle/truss/support of Double height area of Cargo shed, as specified, similar to MAke: BAJAJ & Model:BGHBM 100W LED XE or equivalent. | 32.00 | Job | 100.00 | 8070.00 | 258240.00 | 258240.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
17.00 | Supply, Installastion, Testing & Comissioning of following fluorescent light fixtures with electronics ballast having THD less than 10% , with lamp(s) & complete with all accessories as required & specifed. 1 x 28 watt T5 Surface/pendent mounting T5 lamp luminaire PVC body channel with acrylicrecess mounted slim linear fluorescent light fixture complete with all accessories as required similar to Bajaj BTIP 128 ACR N 1x28W T5 or approved equivalent | 40.00 | Job | 100.00 | 785.00 | 31400.00 | 31400.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
18.00 | Dismantling, Shifting and re-installation of 1.5/2 TR (3 Star) air cooled split airconditioning unit consist of outdoor unit, indoor unit, interconnecting insulated copper referigerant piping 3 mtr (appox), corded remote control, interconnecting power & control cables 3 mtr (aaprox) and refrigerant charging complete with all accessories i/c MS stand for outdoor unit or equivalent as required. | 2.00 | Job | 100.00 | 1855.00 | 3710.00 | 3710.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
19.00 | Supply of following size of 1.1KV grade multicore stranded aluminium conductor XLPE insulated & PVC sheathed armoured cable as per IS: 7098 (Part-1) 1988 complete as required & as per enclosed specification. (3.5 core, 35 Sq.mm. ) | 300.00 | Metre | 100.00 | 142.00 | 42600.00 | 42600.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
20.00 | Supply of following size of 1.1KV grade multicore stranded aluminium conductor XLPE insulated & PVC sheathed armoured cable as per IS: 7098 (Part-1) 1988 complete as required & as per enclosed specification. (4 x 10 Sqmm) | 100.00 | Metre | 100.00 | 83.00 | 8300.00 | 8300.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
21.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 120 mm dia (OD-120 mm & ID-103 mm nominal) | 50.00 | Metre | 100.00 | 268.00 | 13400.00 | 13400.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
22.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 200 mm dia (OD-200 mm & ID-175 mm nominal) | 50.00 | Metre | 100.00 | 461.00 | 23050.00 | 23050.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
23.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. 20 mm | 125.00 | Metre | 10.00 | 110.00 | 13750.00 | 13750.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
24.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. 25 mm | 150.00 | Metre | 100.00 | 124.00 | 18600.00 | 18600.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
25.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Above 35 sq. mm and upto 95 sq. mm | 70.00 | Metre | 100.00 | 35.00 | 2450.00 | 2450.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
26.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. Above 35 sq. mm and upto 95 sq. mm | 100.00 | Metre | 100.00 | 259.00 | 25900.00 | 25900.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
27.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Upto 35 sq. mm | 400.00 | Metre | 100.00 | 23.00 | 9200.00 | 9200.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
28.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 400 sq. mm (82mm) | 2.00 | EA | 10.00 | 915.00 | 1830.00 | 1830.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
29.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 95 sq. mm (45mm) | 2.00 | EA | 100.00 | 360.00 | 720.00 | 720.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
30.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 X 35 sq. mm (32 mm) | 12.00 | EA | 100.00 | 228.00 | 2736.00 | 2736.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
31.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 10 sq. mm (25mm) | 1.00 | EA | 100.00 | 167.00 | 167.00 | 167.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
32.00 | Supplying and drawing following pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. 2 pair | 400.00 | Metre | 100.00 | 15.00 | 6000.00 | 6000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
33.00 | Supplying and drawing following pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, armored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. 10 pair | 400.00 | Metre | 100.00 | 101.00 | 40400.00 | 40400.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
34.00 | Supply and fixing telephone juntion box including tag block, cover plate fabricated out of 1.6 mm thick GI sheet suitable for housing following pair of krone type connectors complete as required. 10 pair | 5.00 | Set | 100.00 | 516.00 | 2580.00 | 2580.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
35.00 | Supply and fixing telephone juntion box including tag block, cover plate fabricated out of 1.6 mm thick GI sheet suitable for housing following pair of krone type connectors complete as required. 50 pair | 1.00 | Set | 100.00 | 1168.00 | 1168.00 | 1168.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
36.00 | Supplying and drawing of UTP 4 pair CAT 6 LAN Cable in the existing surface/ recessed Steel/ PVC conduit as required. 4 pair UTP CAT 6- 1 run of Cable | 400.00 | Metre | 100.00 | 37.00 | 14800.00 | 14800.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
37.00 | Dismantling,shifting and erection of 9 Mtr.Long OCTAGONAL street light pole & bracket with all accessories including installation of LED pole fixture & its connection from connector of pole to fittig by 3C X 2.5 sqmm wire, casting of cement concrete foundation of M-25 grade as per approved foundation drawing suitable for type of pole metioned Above including excavation of pit of required size, allignment of anchor plate, foundation bolts (supplied with pole to match with pole base plate),i/c providing and fixing of DWC pipe of size 50 mm OD & 38 mm ID as per IS 14930 part -II in the foundation pit for loop-in-loop-out cables to the pole complete as required and as specified. Pole with single Arm | 10.00 | Job | 10.00 | 7424.00 | 74240.00 | 74240.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
38.00 | Design, Supply, installation, testing & commissioning of MV Out door type, floor mounted, compartmentalized, cubicle type panel board as per technical specificaton with minimum IP-65 protection fabricated out of 2 mm thick cold rold sheet steel, free standing & totally enclosed, dust proof/vermin proof with cable entries (bottom) and cable alleys as per site conditions. The board shall be suitable for operation 3 phase, 4 Wire, 50Hz, A.C Supply and with aluminium busbars and following switchgear, instrumentation, protective devices and complete with connections, interconnections, earthing, painting (powder coated) and marking etc., complete as required with electical and mechnical interlocking. The panel shall mounted by suitable size MS angle frame with PCC and cement, concrete mortar as per site requirement. Incomers : - 400 Amp FP moulded case Circuit Breaker (35KA Ics=100% Icu) with Microprocessor Based with adjustable Overload, Short Circuit and In-Built Earth Fault Protection microprocessor release with O/L & S/C protection & Rotary handle - 2no. - Set of phase (R,Y,B) LED indication lamps protected by MCBs. - 96 mm x 96 mm square digital voltmeter with builtin voltage selector switch protected by MCB's. - 96 mm x 96 mm square digital ammeter with builtin ammeter selector switch with CT's (400/5A class-1). -144 mm x144 mm square trivector meter (meter controller) equivalent to schneider (conzerv) cat. No. EM 3460 series class 1 with RS 485 port protected by mcb. BUSCOUPLER (1No.) - 400 Amp FP moulded case Circuit Breaker (35KA Ics=100% Icu) with Microprocessor Based with adjustable Overload, Short Circuit and In-Built Earth Fault Protection microprocessor release with O/L & S/C protection & Rotary handle and ON / OFF LED indicating lamps protected by MCBs. BUSBAR - 600Amp TPN aluminium busbars - 2 set Outgoings: (a) -02 nos. 100A TP MCCB (35KA Ics=100% Icu) with thermal magnetic release with variable O/L & S/C protection & Rotary handle, LED type 'ON' indication with MCB protection alongwith:- b) 06 nos. 63A TP MCCB (35KA Ics=100% Icu) with thermal magnetic release with O/L & S/C protection & Rotary handle, LED type 'ON' indication with MCB protection alongwith. (c)- Street light and Highmast feeder consisting of: 1 no.- 63A TPN MCCB, (25KA Ics=100% Icu) with thermal magnetic release with O/L & S/C protection & Rotary handle, LED type 'ON' indication with MCB protection alongwith:- - 3 pole 16 amp. power contactor , Timer switch (Daily dial type) DIN mounting & Toggle switch (for by pass). | 1.00 | Job | 100.00 | 225931.00 | 225931.00 | 225931.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
39.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 100.00 | 4670.00 | 9340.00 | 9340.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
40.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 80.00 | Metre | 100.00 | 156.00 | 12480.00 | 12480.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
41.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 15.00 | Metre | 100.00 | 100.00 | 1500.00 | 1500.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
42.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 870.00 | Metre | 10.00 | 28.00 | 24360.00 | 24360.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
43.00 | FIRE EXTINGUISHER Supply of ISI marked portable fire extinguishers of following type complete as per enclosed specification and fixed / install as per site condition : Co2 type 4.5 kg capacity as per IS-15683:2006 | 4.00 | EA | 100.00 | 5734.00 | 22936.00 | 22936.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
44.00 | Supply of ISI marked portable fire extinguishers of following type complete as per nclosed specification and fixed / install as per site condition : Water type of 9 liters capacity as per IS- 15683:2006 | 4.00 | EA | 100.00 | 2744.00 | 10976.00 | 10976.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
45.00 | Supply of ISI marked portable fire extinguishers of following type complete as per enclosed specification and fixed / install as per site condition : Stored Pressure ABC Powder (MAP Base), of 10kg : IS- 15683 CE marked : MAP 90% as per IS 14609 | 8.00 | EA | 100.00 | 3136.00 | 25088.00 | 25088.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
46.00 | FIRE HYDRANT Supply & fixing of Single headed external yard hydrant comprising of 100mm dia. stand pipe with bend , flange, 63mm dia. Gun Metal landing valve (ISI marked) conforming to IS-5290 (Type -B) with blank Gun-Metal cap & chain, cast iron wheel, complete as required and as per enclosed specification. | 4.00 | EA | 100.00 | 6007.00 | 24028.00 | 24028.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
47.00 | Providing & fixing 63 mm dia Gun Metal short Branch pipe with 20mm (nominal internal diameter) in size Gun Metal nozzle conforming to IS:903 suitable for instantaneous connection complete to inter-connect hose pipe, coupling etc. as required and as per enclosed specification. | 4.00 | EA | 10.00 | 2223.00 | 8892.00 | 8892.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
48.00 | Providing & fixing of MS Hose cabinet outdoor type of size 0.750Mx 0.600Mx 0.250M made of 2mm thick MS sheet with 6mm thick glazed glass doors i/c necessary locking arrangement suitable to accomodate 2nos 15m long hoses, one number branch pipe, etc. and mounted on wall or with raised brick platform. The cabinet shall be painted with red colour shade No. 536 of IS: 5 externally & white internally complete in all respects for external hydrant and as per enclosed specification | 4.00 | EA | 100.00 | 6325.00 | 25300.00 | 25300.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
49.00 | Providing & fixing 63mm dia., 15mtr. long RRL hose pipe (ISI Marked) with 63mm dia. male and female Gun-Metal couplings duly binded with GI wire, rivets etc. conforming to IS- 636 (Type-A) complete as required & as per enclosed specification. | 8.00 | EA | 100.00 | 3960.00 | 31680.00 | 31680.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
50.00 | Providing, laying, jointing, testing and commissioning of following sizes of MS heavy (Class C) pipes conforming to IS-1239 including cutting , threading welding etc. with all accessories like all fittings (standard MS fitting with welded joint shall be used on the pipes) including tees, elbows, reducers, union, flanges, rubber gaskets, nut, bolts and washer, two coats of Synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. All pipe includes cost of supporting/fixing on floor / wall /ceiling with clamps, hangers (using anchor fasteners), MS angles/ channels of suitable size/specification. a) 150 mm | 170.00 | Metre | 100.00 | 1735.00 | 294950.00 | 294950.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
51.00 | Providing, fixing and jointing including testing C- class heavy duty mild steel pipes conforming to IS-1239 upto 150 mm dia. & IS-3589 for sizes greater than 150 mm dia, including cutting, welding, fittings viz bends, tees, reducers, flanges, nut-bolts, gasket complete and laying in ground including excavation, providing PCC block support at interval and giving suitable treatment for corrosion by way of min. 4mm thick corrosion protection tape which shall be wrapped comprising of coal tar/ asphalt component supported on fabric of organic/ inorganic fibre as per IS-10221, re-filling the trench etc.as required and as per enclosed specification. a) 150 mm dia | 30.00 | Metre | 100.00 | 2035.00 | 61050.00 | 61050.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
52.00 | Providing the services of impact Hilti machine/Breaker and Diamond cutter for cutting of pavment of Grade M-40 of minimum size 9m X 0.5m X 0.5m with operators including making good the damage with same Grade of pavement and removal of dismantled material from site. | 1.00 | Job | 100.00 | 19669.00 | 19669.00 | 19669.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
53.00 | FIRE ALARM SYSTEM Supply, installation, testing and commisssioning of UL listed (latest version) Conventional Type Fire Detection & Alarm panel of following loops in network connected to sensors, sounders, manual pull station and operating complete with all necessary hardware and software. Panel shall be completely networkable field programmable, and shall be complete with Central Processing Unit (CPU), Display interface assembly ( DIA), Loop interface board (LIB), Serial interface board (SIB) 30 key keypad, 160 Character LCD display with LCD/LED Backlite, main power supply, 24volts DC maintenance free battery and battery charger suitable 24 hrs normal working and it should be capable of operating for 2hrs during an emegency condition etc. | 1.00 | Job | 10.00 | 38101.00 | 38101.00 | 38101.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
54.00 | Supply, installation, testing & commissioning of UL Listed (latest version) Non motorised reflective optical Beam detector with built-in automatic gain control compensates for signal deterioration from dust buildup, complete as required & as per enclosed specification. | 4.00 | Job | 100.00 | 46493.00 | 185972.00 | 185972.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
55.00 | SITC of UL Listed (latest version) Wall Mounted Hooter-cum- strobe with minimum 90dB output and with required power supply converter (230VAC to 12/24 VDC) etc. as required. | 4.00 | Job | 100.00 | 2399.00 | 9596.00 | 9596.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
56.00 | SITC of the following UL Listed (latest version) conventional Fire Detection & Alarm system detectors & devices complete with connections, etc. as required. conventional multicriteria detector {Smoke + heat (fixed and rate of rise) } complete as required. | 6.00 | Job | 100.00 | 1600.00 | 9600.00 | 9600.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
57.00 | SITC of the following UL Listed (latest version) conventional Fire Detection & Alarm system detectors & devices complete with connections, etc. as required. UL Listed (latest version) Conventional Manual Pull station (not break glass type) complete as required. | 5.00 | Job | 100.00 | 3500.00 | 17500.00 | 17500.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
58.00 | SITC of UL Listed (latest version) Response Indicator (LED in polycorbonate housing) etc. as required. | 6.00 | Job | 10.00 | 275.00 | 1650.00 | 1650.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
59.00 | Supply & laying (surface or in existing conduit) of Fire Survival Unarmoured Cable (300/500V) etc. as required. 2 x 1.5 Sq.mm. | 500.00 | Metre | 100.00 | 150.00 | 75000.00 | 75000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
| Total in Figures |  |  |  |  | 2048569.00
Lowest Amount Quoted BY: ARNAV ENGINEERING CONSULTANCY SERVICES(2048569.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of 4 nos. Self-Supported Steel Roof Structures for Cargo building at Chandigarh International Airport Ltd., Mohali. S.H. Electrical Works Tender ID: 2020_AAI_61338_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ARNAV ENGINEERING CONSULTANCY SERVICES | 2048569.00 | L1