## BoQ1
Government eProcurement System Created By: PRASHANT FULMARE Created Date/Time: 24-Nov-2020 11:38 AM Tender Title: Replacement of 2 Nos. 320KVA DG sets for GLF installation at S.V. Airport, Raipur. Tender ID: 2020_AAI_61735_1
Tender Inviting Authority: Asst. Gen. Manager (E-E), Airports Authority of India, S.V. Airport, Raipur
Name of Work: Replacement of 2 Nos 320KVA DG sets for GLF installation at S.V. Airport, Raipur.
Contract No: 2020_AAI_61735
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO.(GSTN-24AAEFD3355K1ZI) |  | ECS ENGINEERING PVT LTD(GSTN-09AABCE5944P1Z1) |  | VIJAYPOWER GENERATORS LIMITED(GSTN-07AAACV0191N1Z4) |  | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ) |  | Balaji Engineering(GSTN-33ADGPV2628A1ZV) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | DIESEL GENERATOR SETS
2.00 | Providing, Installing, Testing and Commissiong of 'Silent Type' Diesel Generating set alongwith having Prime Power Rating of 320 KVA, 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz, 3 phase system & for 0.85 Load Factor and consisting of the followings: | 2.00 | Set | 2367303.75 | 2043000.00 | 4086000.00 | 2159000.00 | 4318000.00 | 1815000.00 | 3630000.00 | 1885000.00 | 3770000.00 | 2200000.00 | 4400000.00 | 1965000.00 | 3930000.00 | 2350000.00 | 4700000.00 | 3630000.00 | VIJAYPOWER GENERATORS LIMITED
3.00 | (a) Diesel Engine: Diesel engine 4 stroke water cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 45 Degree C, 50% RH & at 335 Meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continous operation. The engine will be fitted complete with all the required accessories.
4.00 | (b) Engine mounted Instrument Panel fitted with and having digital display for following: (i) Start-stop switch with key (ii) Water temperature indication (iii) Lubrication oil pressure indication (iv) Lubrication oil temperature indication (v) Battery charging indication (vi) RPM indication (vii) Over speed indication (viii) Low lub. Oil trip indication (ix) Engine Hours indication
5.00 | (c) Alternator Synchronous alternator rated at 320 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 45 Degree C, 50% RH & at 335 Meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR conforming to IS: 4722/BS 2613 suitable for tropical conditions and with class-F/H insulation.
6.00 | (d) Base Frame & Foundation: Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on suitable cement concrete foundation and vibration isolation arrangement as per recommendations of manufacturer. (Foundation as per Technical specifications /manufacturer's recommendations to be provided)
7.00 | (e) Fuel Tank: Daily service fuel tank of 990 L capacity capacity fabricated out of 3 mm thick M.S./CRCA sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class 'C' pipes of suitable dia. Complete with valves, level indications & accessories as required as per specifications.
8.00 | (f) Exhaust System: Dry exhaust mainfold with hospital exhaust silencer and catalytic convertor.
9.00 | (g) Starting System: 24V DC starting system comprising of starter motors: voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries (OR) as per OEM standard complete as required.
10.00 | (h) Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications.
11.00 | AMF PANEL Fabricating, Installing, Testing & Commissioning of automatic mains failure control including auto by-pass panel, suitable for 320 KVA silent type DG set complete with relays, timers, set of CTs for metering & protection and energy analyser to indicate currents, phase and line voltages, frequency, power factor, KWH, KVARH & provision for overload, short circuit, restricted earth fault, under frequency, control cabling from AMF panel to diesel engine and elsewhere if required, all complete and inter locking including the following: | 2.00 | Set | 527621.85 | 510000.00 | 1020000.00 | 400000.00 | 800000.00 | 550000.00 | 1100000.00 | 595000.00 | 1190000.00 | 300000.00 | 600000.00 | 325000.00 | 650000.00 | 225000.00 | 450000.00 | 450000.00 | Manish Electricals
12.00 | (a) 2 nos. 4 Pole, 630 A, 50 KA, Ics=100% Icu, Microprocessorbased MCCB (with O/L, S/C & E/F protection)
13.00 | (b) Auto/Manual/Test/Off selector switch
14.00 | (c) 2 Nos. over voltage relay, 2 Nos. reverse power relay and 2 Nos. under voltage relay.
15.00 | (d) 3 Sets of current transformers 15 P 10 accuracy for protection and 15 VA class-I for metering
16.00 | (e) Energy analyser unit to indicate current, voltage, frequency, power factor and KWH
17.00 | (f) Indicating lamps for load on mains and load on set
18.00 | (g) Fuse for instruments
19.00 | (h) Battery charger, complete with transformer/ rectifier, D.C. voltmeter and ammeter, selector switch for trickle, off and boost and current adjustment.
20.00 | (i) Main supply failure monitor
21.00 | (j) Supply failure timer
22.00 | (k) Restoration timer
23.00 | (l) Control unit with three impulse automatic engine start/stop and failure to start lockout.
24.00 | (m) Impulse counter with locking and reset facility.
25.00 | (n) ON/OFF/Control circuit switch with indicator
26.00 | (o) Audio/Video annunciation for
27.00 | (i) High water temperature
28.00 | (ii) Low lubricating oil pressure
29.00 | (iii) Engine over speed
30.00 | (iv) Engine fails to start
31.00 | (v) Full load/maximum load warning
32.00 | MOBILE DG SET Supply of fuel efficient silent type trolley mounted DG set having prime power rating of 25 KVA, 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz, 3 phase system & for 0.85 load factor complete with acoustic enclosure. The DG set should be air cooled and shall have integrated fuel tank of capacity 75-100 Ltr. The DG set must be equipped with manual control panel and maintenance free battery and must confirm to relevant CPCB norms and consisting of electronic speed governor, in-built silencer inside the canopy. The Trolley for mounting DG sets should be capable to sustain the weight of DG set and its accessories, having 4 nos tubeless or solid tyred wheels of suitable size with guard, equipped with pulling arrangement (eye hook arrangement with movement of front wheels in left & right direction), additional 1.5 meter length tow bar with locking arrangements. The trolley should be painted with one coat of red oxide and two coats of synthetic enamel paint etc. as per the instruction of Engineer-in- charge and shall meet the other technical specifications mentioned in contract document. | 1.00 | Set | 612189.90 | 485000.00 | 485000.00 | 344000.00 | 344000.00 | 500000.00 | 500000.00 | 507547.08 | 507547.08 | 500000.00 | 500000.00 | 335000.00 | 335000.00 | 535000.00 | 535000.00 | 335000.00 | Awasthi Electric Works
33.00 | Supplying and fixing exhaust gas piping of 150 mm dia. welded black MS, B Class pipe conforming to IS:1239 (part-I, 2004) cut to required lengths and installed with necessary bends, supports and clamps, anti-vibration mountings, SS Expansion Joints, insulation of exhaust system with mineral wool/Rock wool of 50 mm thick, wiremesh & aluminum cladding etc. suitable for 320 KVA DG Set etc. complete as required as per specifications. | 12.00 | Mtrs | 3216.15 | 2700.00 | 32400.00 | 2400.00 | 28800.00 | 4000.00 | 48000.00 | 1441.66 | 17299.92 | 2000.00 | 24000.00 | 5000.00 | 60000.00 | 2000.00 | 24000.00 | 17299.92 | Mona Generator Services Pvt. Ltd.
34.00 | Dismantling of Exisitng 320 KVA open type DG sets along with AMF panels terminations, cable connections, Diesel Tanks including shifting to store or as directed by E-I-C complete as required. | 2.00 | Job | 11830.35 | 45000.00 | 90000.00 | 15000.00 | 30000.00 | 15000.00 | 30000.00 | 25000.00 | 50000.00 | 5000.00 | 10000.00 | 15000.00 | 30000.00 | 50000.00 | 100000.00 | 10000.00 | Balaji Engineering
35.00 | Supply of 30 W (nominal capacity) LED integral Flood Light type light fitting having pressure die cast housing with toughened glass, individual LEDs with secondary optics, IP 66, inbuilt convertor, accessories etc and suitable for use on 230 volts, 50 Hz, single phase, A.C. supply as required. (Make:- Havells, Model - JETACOMPECTOFL30WLED757TG or equivalent). | 6.00 | Each | 2863.35 | 4000.00 | 24000.00 | 2600.00 | 15600.00 | 5500.00 | 33000.00 | 2400.00 | 14400.00 | 3000.00 | 18000.00 | 1650.00 | 9900.00 | 6500.00 | 39000.00 | 9900.00 | Awasthi Electric Works
36.00 | Installation, testing and commissioning of wall bracket /ceiling fittings of all sizes and shapes containing upto two GLS/CFL/ LED lamps per fitting/wall fan, complete with all accessories including connections etc. as required. | 6.00 | Each | 92.40 | 700.00 | 4200.00 | 300.00 | 1800.00 | 1800.00 | 10800.00 | 800.00 | 4800.00 | 100.00 | 600.00 | 100.00 | 600.00 | 200.00 | 1200.00 | 600.00 | Balaji Engineering, Awasthi Electric Works
37.00 | Supply of following sizes LT power cable of 1.1 KV grade of following sizes aluminum conductor XLPE insulated PVC sheathed armored cable confirming to IS 5554 & 7098/1/1988 with upto date amendment as required. | 270.00 | Mtrs | 1256.85 | 1000.00 | 270000.00 | 853.00 | 230310.00 | 990.00 | 267300.00 | 975.00 | 263250.00 | 800.00 | 216000.00 | 960.00 | 259200.00 | 850.00 | 229500.00 | 216000.00 | Balaji Engineering
38.00 | (a) 3.5 x 300 sq.mm. Al Aromured XLPE cable
39.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL / HDPE pipe as required. | 90.00 | Mtrs | 101.85 | 40.00 | 3600.00 | 150.00 | 13500.00 | 100.00 | 9000.00 | 112.00 | 10080.00 | 50.00 | 4500.00 | 100.00 | 9000.00 | 90.00 | 8100.00 | 3600.00 | DOSHI ELECTRIC ENGG. CO.
40.00 | (a) Above 185 sq. mm and upto 400 sq. mm
41.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. | 90.00 | Mtrs | 87.15 | 40.00 | 3600.00 | 150.00 | 13500.00 | 100.00 | 9000.00 | 96.00 | 8640.00 | 50.00 | 4500.00 | 70.00 | 6300.00 | 90.00 | 8100.00 | 3600.00 | DOSHI ELECTRIC ENGG. CO.
42.00 | (a) Above 185 sq. mm and upto 400 sq. mm
43.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/XLPE aluminiumonductor cable of 1.1 KV grade as required. | 24.00 | Nos. | 1076.25 | 800.00 | 19200.00 | 1400.00 | 33600.00 | 900.00 | 21600.00 | 960.00 | 23040.00 | 750.00 | 18000.00 | 950.00 | 22800.00 | 1200.00 | 28800.00 | 18000.00 | Balaji Engineering
44.00 | (a) 3.5 X 300 sq. mm (70 mm)
45.00 | EARTHING SYSTEM
46.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 2.00 | Set | 4360.65 | 5000.00 | 10000.00 | 7000.00 | 14000.00 | 7000.00 | 14000.00 | 7000.00 | 14000.00 | 7500.00 | 15000.00 | 4890.00 | 9780.00 | 7000.00 | 14000.00 | 9780.00 | Awasthi Electric Works
47.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 4.00 | Set | 9200.10 | 16000.00 | 64000.00 | 13000.00 | 52000.00 | 12000.00 | 48000.00 | 11500.00 | 46000.00 | 15000.00 | 60000.00 | 10500.00 | 42000.00 | 18000.00 | 72000.00 | 42000.00 | Awasthi Electric Works
48.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Meter | 1125.60 | 1100.00 | 33000.00 | 1300.00 | 39000.00 | 1400.00 | 42000.00 | 1200.00 | 36000.00 | 750.00 | 22500.00 | 1150.00 | 34500.00 | 700.00 | 21000.00 | 21000.00 | Manish Electricals
49.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Meter | 527.10 | 400.00 | 8000.00 | 460.00 | 9200.00 | 390.00 | 7800.00 | 470.00 | 9400.00 | 300.00 | 6000.00 | 450.00 | 9000.00 | 450.00 | 9000.00 | 6000.00 | Balaji Engineering
50.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 20.00 | Meter | 838.95 | 700.00 | 14000.00 | 900.00 | 18000.00 | 900.00 | 18000.00 | 1000.00 | 20000.00 | 750.00 | 15000.00 | 950.00 | 19000.00 | 600.00 | 12000.00 | 12000.00 | Manish Electricals
51.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 80.00 | Meter | 194.25 | 100.00 | 8000.00 | 150.00 | 12000.00 | 180.00 | 14400.00 | 165.00 | 13200.00 | 150.00 | 12000.00 | 160.00 | 12800.00 | 190.00 | 15200.00 | 8000.00 | DOSHI ELECTRIC ENGG. CO.
52.00 | SH-II: MISCELLANEOUS CIVIL WORKS
53.00 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required. 250 mm dia | 30.00 | Meter | 638.40 | 350.00 | 10500.00 | 900.00 | 27000.00 | 900.00 | 27000.00 | 1550.00 | 46500.00 | 300.00 | 9000.00 | 715.00 | 21450.00 | 450.00 | 13500.00 | 9000.00 | Balaji Engineering
54.00 | Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-incharge. Ordinary rock | 80.00 | Cum | 404.25 | 200.00 | 16000.00 | 500.00 | 40000.00 | 350.00 | 28000.00 | 1050.00 | 84000.00 | 300.00 | 24000.00 | 335.00 | 26800.00 | 200.00 | 16000.00 | 16000.00 | DOSHI ELECTRIC ENGG. CO., Manish Electricals
55.00 | Earth work in excavation by mechanical means (Hydraulic excavator) /manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. | 35.00 | Cum | 254.10 | 100.00 | 3500.00 | 600.00 | 21000.00 | 350.00 | 12250.00 | 1250.00 | 43750.00 | 300.00 | 10500.00 | 425.00 | 14875.00 | 200.00 | 7000.00 | 3500.00 | DOSHI ELECTRIC ENGG. CO.
56.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | 20.00 | Cum | 3608.85 | 3800.00 | 76000.00 | 5600.00 | 112000.00 | 4500.00 | 90000.00 | 7500.00 | 150000.00 | 4000.00 | 80000.00 | 5300.00 | 106000.00 | 3500.00 | 70000.00 | 70000.00 | Manish Electricals
57.00 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level : 1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size). | 8.00 | Cum | 5171.25 | 5000.00 | 40000.00 | 7300.00 | 58400.00 | 5500.00 | 44000.00 | 7000.00 | 56000.00 | 7000.00 | 56000.00 | 7200.00 | 57600.00 | 4000.00 | 32000.00 | 32000.00 | Manish Electricals
58.00 | STEEL REINFORCEMENT: Thermo-Mechanically Treated bars of grade Fe-500D or more. | 1170.00 | Kg | 86.10 | 80.00 | 93600.00 | 75.00 | 87750.00 | 120.00 | 140400.00 | 90.00 | 105300.00 | 80.00 | 93600.00 | 75.00 | 87750.00 | 60.00 | 70200.00 | 70200.00 | Manish Electricals
59.00 | Brick work with common fly ash F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : Cement mortar 1:6 (1 cement : 6 coarse sand) | 11.00 | Cum | 6333.60 | 6000.00 | 66000.00 | 6000.00 | 66000.00 | 6500.00 | 71500.00 | 6200.00 | 68200.00 | 6000.00 | 66000.00 | 7200.00 | 79200.00 | 3500.00 | 38500.00 | 38500.00 | Manish Electricals
60.00 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. Hot finished welded type tubes | 1000.00 | Kg | 130.20 | 80.00 | 80000.00 | 80.00 | 80000.00 | 120.00 | 120000.00 | 115.00 | 115000.00 | 90.00 | 90000.00 | 125.00 | 125000.00 | 70.00 | 70000.00 | 70000.00 | Manish Electricals
61.00 | Providing and fixing mild steel round holding down bolts with nuts and washer plates complete. | 100.00 | Kg | 75.60 | 90.00 | 9000.00 | 110.00 | 11000.00 | 120.00 | 12000.00 | 95.00 | 9500.00 | 100.00 | 10000.00 | 79.00 | 7900.00 | 150.00 | 15000.00 | 7900.00 | Awasthi Electric Works
62.00 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 157.00 | Kg | 93.45 | 95.00 | 14915.00 | 95.00 | 14915.00 | 120.00 | 18840.00 | 230.00 | 36110.00 | 100.00 | 15700.00 | 95.00 | 14915.00 | 90.00 | 14130.00 | 14130.00 | Manish Electricals
63.00 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-charge) 0.50 mm (+ 0.05 %) total coated thickness with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineerin-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. | 110.00 | Sqm | 1195.95 | 610.00 | 67100.00 | 600.00 | 66000.00 | 900.00 | 99000.00 | 500.00 | 55000.00 | 400.00 | 44000.00 | 560.00 | 61600.00 | 550.00 | 60500.00 | 44000.00 | Balaji Engineering
64.00 | Providing and laying damp-proof course 40mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand (zone-III): 4 graded stone aggregate 12.5mm nominal size) | 11.00 | Sqm | 332.85 | 200.00 | 2200.00 | 6300.00 | 69300.00 | 6500.00 | 71500.00 | 500.00 | 5500.00 | 250.00 | 2750.00 | 330.00 | 3630.00 | 3000.00 | 33000.00 | 2200.00 | DOSHI ELECTRIC ENGG. CO.
65.00 | CEMENT PLASTER (IN FINE SAND) 12 mm cement plaster of mix : 1:6 (1 cement: 6 fine sand) | 90.00 | Sqm | 211.05 | 500.00 | 45000.00 | 204.00 | 18360.00 | 550.00 | 49500.00 | 300.00 | 27000.00 | 250.00 | 22500.00 | 3.50 | 315.00 | 210.00 | 18900.00 | 315.00 | Awasthi Electric Works
66.00 | EXTERIOR FINISHING Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) | 90.00 | Sqm | 171.15 | 150.00 | 13500.00 | 320.00 | 28800.00 | 190.00 | 17100.00 | 450.00 | 40500.00 | 100.00 | 9000.00 | 156.00 | 14040.00 | 120.00 | 10800.00 | 9000.00 | Balaji Engineering
67.00 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work | 40.00 | Sqm | 116.55 | 200.00 | 8000.00 | 85.00 | 3400.00 | 270.00 | 10800.00 | 325.00 | 13000.00 | 100.00 | 4000.00 | 115.00 | 4600.00 | 180.00 | 7200.00 | 3400.00 | ECS ENGINEERING PVT LTD
68.00 | Providing and fixing precoated galvanised steel sheet roofing accessories 0.50 mm (+ 0.05 %) total coated thickness, Zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns using self drilling/ self tapping screws complete:
69.00 | Ridges plain (500 - 600mm) | 10.00 | Meter | 375.90 | 200.00 | 2000.00 | 725.00 | 7250.00 | 800.00 | 8000.00 | 1000.00 | 10000.00 | 250.00 | 2500.00 | 395.00 | 3950.00 | 500.00 | 5000.00 | 2000.00 | DOSHI ELECTRIC ENGG. CO.
70.00 | Gutter (600 mm over all girth) | 20.00 | Meter | 939.75 | 300.00 | 6000.00 | 725.00 | 14500.00 | 550.00 | 11000.00 | 1000.00 | 20000.00 | 250.00 | 5000.00 | 960.00 | 19200.00 | 900.00 | 18000.00 | 5000.00 | Balaji Engineering
71.00 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion, (i) Single socketed pipes.
72.00 | 75 mm diameter | 14.00 | Meter | 176.40 | 300.00 | 4200.00 | 300.00 | 4200.00 | 300.00 | 4200.00 | 170.00 | 2380.00 | 300.00 | 4200.00 | 192.00 | 2688.00 | 150.00 | 2100.00 | 2100.00 | Manish Electricals
73.00 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion, (i) Single socketed pipes.
74.00 | (a) Coupler - 75 mm | 4.00 | Each | 71.40 | 100.00 | 400.00 | 300.00 | 1200.00 | 175.00 | 700.00 | 120.00 | 480.00 | 100.00 | 400.00 | 191.00 | 764.00 | 200.00 | 800.00 | 400.00 | DOSHI ELECTRIC ENGG. CO., Balaji Engineering
75.00 | (b) Bend 87.5° - 75 mm | 4.00 | Each | 82.95 | 150.00 | 600.00 | 300.00 | 1200.00 | 150.00 | 600.00 | 145.00 | 580.00 | 100.00 | 400.00 | 85.00 | 340.00 | 150.00 | 600.00 | 340.00 | Awasthi Electric Works
76.00 | (c) Shoe (Plain) - 75 mm | 4.00 | Each | 72.45 | 200.00 | 800.00 | 300.00 | 1200.00 | 175.00 | 700.00 | 125.00 | 500.00 | 100.00 | 400.00 | 75.00 | 300.00 | 100.00 | 400.00 | 300.00 | Awasthi Electric Works
77.00 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. All kinds of soil | 14.00 | Cum | 201.60 | 100.00 | 1400.00 | 500.00 | 7000.00 | 450.00 | 6300.00 | 600.00 | 8400.00 | 100.00 | 1400.00 | 208.00 | 2912.00 | 700.00 | 9800.00 | 1400.00 | DOSHI ELECTRIC ENGG. CO., Balaji Engineering
78.00 | Providing and laying factory made chamfered edge Cement Concrete paver blocks In foot path, park & lawns driveway or light & traffic parking etc. of required strength, thickness & size/ shape, made by table vibratory method using PU mould, laid in required colour & pattern over 50mm thick compacted bed of course sand, compacting and proper embedding/laying of inter locking paver blocks into the sand bedding layer through vibratory compaction by using plate vibrator, filling the joints with sand and cutting of paver blocks as per required size and pattern, finishing and sweeping extra sand, all complete as per manufacturer's specifications & direction of Engineerin-Charge. 80mm thick Cement concrete paver block of M-30 grade with approved colour, design & pattern. Centring and shuttering including strutting, propping etc. and removel of form for: | 160.00 | Sqm | 795.90 | 1200.00 | 192000.00 | 750.00 | 120000.00 | 900.00 | 144000.00 | 800.00 | 128000.00 | 500.00 | 80000.00 | 850.00 | 136000.00 | 350.00 | 56000.00 | 56000.00 | Manish Electricals
79.00 | Foundations, Footings, bases of columns etc. for mass concrete. | 70.00 | Sqm | 237.30 | 450.00 | 31500.00 | 225.00 | 15750.00 | 700.00 | 49000.00 | 315.00 | 22050.00 | 1000.00 | 70000.00 | 250.00 | 17500.00 | 150.00 | 10500.00 | 10500.00 | Manish Electricals
80.00 | Lintels, beams, plinth beams, girdrs, bressumers and cantilevers. | 30.00 | Sqm | 483.00 | 600.00 | 18000.00 | 470.00 | 14100.00 | 900.00 | 27000.00 | 570.00 | 17100.00 | 1000.00 | 30000.00 | 500.00 | 15000.00 | 200.00 | 6000.00 | 6000.00 | Manish Electricals
81.00 | Columns, Pillars, Piers, Abutments, Posts and Struts. | 10.00 | Sqm | 625.80 | 650.00 | 6500.00 | 470.00 | 4700.00 | 1000.00 | 10000.00 | 750.00 | 7500.00 | 1000.00 | 10000.00 | 650.00 | 6500.00 | 200.00 | 2000.00 | 2000.00 | Manish Electricals
| Total in Figures |  |  |  |  | 6983715.00 |  | 6868335.00 |  | 6876290.00 |  | 7070007.00 |  | 6667450.00 |  | 6270709.00 |  | 6854830.00
Lowest Amount Quoted BY: Awasthi Electric Works(6270709.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of 2 Nos. 320KVA DG sets for GLF installation at S.V. Airport, Raipur. Tender ID: 2020_AAI_61735_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works | 6270709.00 | L1
| 2 | Balaji Engineering | 6667450.00 | L2
| 3 | Manish Electricals | 6854830.00 | L3
| 4 | ECS ENGINEERING PVT LTD | 6868335.00 | L4
| 5 | VIJAYPOWER GENERATORS LIMITED | 6876290.00 | L5
| 6 | DOSHI ELECTRIC ENGG. CO. | 6983715.00 | L6
| 7 | Mona Generator Services Pvt. Ltd. | 7070007.00 | L7