## BoQ1
Government eProcurement System Created By: PRASHANT FULMARE Created Date/Time: 22-Dec-2020 03:53 PM Tender Title: Extension of runway at 24 beginning, expansion of apron suitable for C category of aircraft and other associated works at S.V. Airport, Raipur. SH Electrical works for Trans-Installation of Glide Path. Tender ID: 2020_AAI_62081_1
Tender Inviting Authority: Asst. Gen. Manager (E-E), Airports Authority of India, S.V. Airport, Raipur
Name of Work: Extension of runway at 24 beginning, expansion of apron suitable for C-category of aircraft and other associated works at S.V. Airport, Raipur. SH:- Electrical works for Trans-Installation of Glide Path.
Contract No: 2020_AAI_62081
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | Yash Energy Pvt. Ltd(GSTN-24AAACY3771H1ZA) |  | JAI ENTERPRISES(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I: Internal Electrical Works
2.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in Fire Retardant uPVC trunking (as per IS 14927-Part 2), with modular switch, modular plate, suitable PVC box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required.
3.00 | (a) Group C | 23.00 | Each | 1075.90 | 1000.00 | 23000.00 | 644.00 | 14812.00 | 550.00 | 12650.00 | 12650.00 | JAI ENTERPRISES
4.00 | Wiring for light/ power plug with 4X2.5 sq. mm FRLS PVC insulated copper conductor single core cable in Fire Retardant uPVC trunking (as per IS 14927-Part 2) alongwith 2 Nos. 2.5 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 30.00 | Meter | 306.34 | 290.00 | 8700.00 | 169.00 | 5070.00 | 240.00 | 7200.00 | 5070.00 | Yash Energy Pvt. Ltd
5.00 | Wiring for light/ power plug with 2X2.5 sq. mm FRLS PVC insulated copper conductor single core cable in Fire Retardant uPVC trunking (as per IS 14927-Part 2) alongwith 1 No. 2.5 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 60.00 | Meter | 202.46 | 135.00 | 8100.00 | 92.00 | 5520.00 | 320.00 | 19200.00 | 5520.00 | Yash Energy Pvt. Ltd
6.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
7.00 | (a) 3 x 2.5 sq. mm | 180.00 | Meter | 111.30 | 85.00 | 15300.00 | 92.00 | 16560.00 | 110.00 | 19800.00 | 15300.00 | Awasthi Electric Works
8.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, singlecore cable in Fire Retardant uPVC trunking (as per IS 14927-Part 2) as required.
9.00 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 50.00 | Meter | 202.46 | 190.00 | 9500.00 | 92.00 | 4600.00 | 150.00 | 7500.00 | 4600.00 | Yash Energy Pvt. Ltd
10.00 | Supplying and fixing suitable size PVC Modular box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 8.00 | Each | 721.86 | 490.00 | 3920.00 | 696.00 | 5568.00 | 200.00 | 1600.00 | 1600.00 | JAI ENTERPRISES
11.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
12.00 | 15/16 A switch | 12.00 | Each | 237.44 | 100.00 | 1200.00 | 141.00 | 1692.00 | 200.00 | 2400.00 | 1200.00 | Awasthi Electric Works
13.00 | 6 pin 15/16 A socket outlet | 12.00 | Each | 285.14 | 115.00 | 1380.00 | 210.00 | 2520.00 | 200.00 | 2400.00 | 1380.00 | Awasthi Electric Works
14.00 | Supplying and fixing brass batten/ angle holder including connection etc. as required. | 2.00 | Each | 108.12 | 80.00 | 160.00 | 133.00 | 266.00 | 18.00 | 36.00 | 36.00 | JAI ENTERPRISES
15.00 | Supply of 9 W LED Inverter/ rechargeable bulb With Auto-Charge Technology having Emergency time backup of not less than 4 Hours at min. of 50% illumination, suitable for 230 V, 50 Hz Single phase supply complete as required. | 2.00 | Each | 489.72 | 690.00 | 1380.00 | 460.00 | 920.00 | 1500.00 | 3000.00 | 920.00 | Yash Energy Pvt. Ltd
16.00 | Supply of 400 mm sweep wall fan having Aerodynamically designed, Balanced Blade, thermal overload protection, Jerk free oscillation (60o) & smooth running, 1400 RPM suitable for use on 230 volts, 50 Hz, single phase, A.C. supply etc. complete as required. | 2.00 | Each | 2315.04 | 2250.00 | 4500.00 | 2299.00 | 4598.00 | 1200.00 | 2400.00 | 2400.00 | JAI ENTERPRISES
17.00 | Supply of 1400 RPM, 400 mm dia. Jerk free oscillation & smooth running pedastal fan with aerodynamically desined blades etc. complete as required, suitable for 230 volts, 50 Hz, single phase, A.C. supply. | 2.00 | Each | 1836.98 | 3150.00 | 6300.00 | 2783.00 | 5566.00 | 3000.00 | 6000.00 | 5566.00 | Yash Energy Pvt. Ltd
18.00 | Supply of single phase, 225 mm dia. sweep Heavy Exhaust fan having thermal overload protecton, with Louver and shutter/safety Guard from foreign objects, etc. complete as required suitable for use on 230 volts, 50 Hz, single phase, A.C. supply. | 1.00 | Each | 1477.64 | 3500.00 | 3500.00 | 2629.00 | 2629.00 | 3500.00 | 3500.00 | 2629.00 | Yash Energy Pvt. Ltd
19.00 | Supply of indoor surface mounting 20 W (nominal capacity), LED light fitting efficacy of not less than 100 lumens, complete with LED tube rod, accessories etc and suitable for use on 230 volts, 50 Hz, single phase, A.C. supply as required. | 7.00 | Each | 591.48 | 600.00 | 4200.00 | 1561.00 | 10927.00 | 400.00 | 2800.00 | 2800.00 | JAI ENTERPRISES
20.00 | Supply of indoor surface mounting 9 W (nominal capacity), LED light fitting efficacy of not less than 100 lumens, complete with LED tube rod, accessories etc and suitable for use on 230 volts, 50 Hz, single phase, A.C. supply as required. | 6.00 | Each | 470.64 | 450.00 | 2700.00 | 853.00 | 5118.00 | 1200.00 | 7200.00 | 2700.00 | Awasthi Electric Works
21.00 | Supply of 25 W (nominal capacity) LED integral Flood Light type light fitting having pressure die cast housing with toughened glass, individual LEDs with secondary optics, IP 66, inbuilt convertor, accessories etc and suitable for use on 230 volts, 50 Hz, single phase, A.C. supply as required. | 5.00 | Each | 2124.24 | 2000.00 | 10000.00 | 1513.00 | 7565.00 | 800.00 | 4000.00 | 4000.00 | JAI ENTERPRISES
22.00 | Supply of rechargeable portable type LED Emergency light with min 6 W output and having battery of suitable capcity to provide backup of min 3 Hrs. etc. complete as required. | 4.00 | Each | 9849.52 | 2350.00 | 9400.00 | 932.00 | 3728.00 | 2100.00 | 8400.00 | 3728.00 | Yash Energy Pvt. Ltd
23.00 | Installation, testing and commissioning of wall bracket /ceiling fittings of all sizes and shapes containing upto two GLS/CFL/ LED lamps per fitting/wall fan, complete with all accessories including connections etc. as required. | 20.00 | Each | 92.22 | 150.00 | 3000.00 | 250.00 | 5000.00 | 200.00 | 4000.00 | 3000.00 | Awasthi Electric Works
24.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
25.00 | (a) Upto 450 mm sweep | 1.00 | Each | 340.26 | 250.00 | 250.00 | 350.00 | 350.00 | 100.00 | 100.00 | 100.00 | JAI ENTERPRISES
26.00 | Supplying and fixing 3 pin 16 A Switch with socket in IP 66 enclosure suitable for outdoor installation on surface including connections etc. as required. | 3.00 | Each | 2745.40 | 700.00 | 2100.00 | 1118.00 | 3354.00 | 1200.00 | 3600.00 | 2100.00 | Awasthi Electric Works
27.00 | Providing & fixing (80 X 50) mm size UPVC cable trunking on surface including necessary couplers, joint cover, angles etc. along with all other accessories as required. | 70.00 | Meter | 872.38 | 725.00 | 50750.00 | 428.00 | 29960.00 | 220.00 | 15400.00 | 15400.00 | JAI ENTERPRISES
28.00 | Supply and fixing of 4 Module clip on supports suitble for fixing of switch, power Socket outlets including finishing plate etc. complete as required. | 12.00 | Each | 256.52 | 150.00 | 1800.00 | 262.00 | 3144.00 | 380.00 | 4560.00 | 1800.00 | Awasthi Electric Works
29.00 | SH-II: Distribution Boards & MCBs
30.00 | Supplying and fixing following way, single pole and neutral, sheet steel, glazed door, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
31.00 | (a) 6 way , Double door | 2.00 | Each | 2103.04 | 910.00 | 1820.00 | 1324.00 | 2648.00 | 3000.00 | 6000.00 | 1820.00 | Awasthi Electric Works
32.00 | (b) 8 way , Double door | 4.00 | Each | 2266.28 | 1036.00 | 4144.00 | 1445.00 | 5780.00 | 7000.00 | 28000.00 | 4144.00 | Awasthi Electric Works
33.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
34.00 | (a) 6 way (4 + 18), Double door | 1.00 | Each | 4153.08 | 2750.00 | 2750.00 | 3823.00 | 3823.00 | 12000.00 | 12000.00 | 2750.00 | Awasthi Electric Works
35.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
36.00 | (a) Single pole | 30.00 | Each | 312.70 | 145.00 | 4350.00 | 219.00 | 6570.00 | 140.00 | 4200.00 | 4200.00 | JAI ENTERPRISES
37.00 | (b) Double pole | 8.00 | Each | 977.32 | 450.00 | 3600.00 | 594.00 | 4752.00 | 220.00 | 1760.00 | 1760.00 | JAI ENTERPRISES
38.00 | Supplying and fixing of 63 amps rating, 415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
39.00 | (a) Four Pole | 1.00 | Each | 2385.00 | 1350.00 | 1350.00 | 1630.00 | 1630.00 | 1200.00 | 1200.00 | 1200.00 | JAI ENTERPRISES
40.00 | Supplying and fixing of 25A rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 3.00 | Each | 2788.86 | 1890.00 | 5670.00 | 1946.00 | 5838.00 | 3000.00 | 9000.00 | 5670.00 | Awasthi Electric Works
41.00 | SH-III: LT Panel & SPDs
42.00 | Design, fabrication, supply, installation, testing and commissioning of vermin & dust proof, front operated cubicle type floor mounted, OUTDOOR double door type LT panel board made out of 2.0 mm thick for body & doors and all partitions shall be of 1.6 mm thick CRCA sheet, totally enclosed type, IP 54 ,duly rust inhibited, stove enameled, powder coated paint , fully compartmentalized complete with double hinged front door with lockable arrangement with name plates, heavy duty rubber gaskets, removable gland plates made out of 3 mm thick sheet steel, 02nos earth stud, MS angle iron channel, internal wiring with 1.5sqmm FR copper wires/cable, connection, interconnection including necessary civil works(if required) like PCC, brick work etc. complete as required. | 1.00 | Job | 200766.12 | 225000.00 | 225000.00 | 186500.00 | 186500.00 | 180000.00 | 180000.00 | 180000.00 | JAI ENTERPRISES
43.00 | Incomer
44.00 | 3 Nos. 160 A, four pole Thermal Magnetic release variable range, Moulded Case Circuit Breaker with extended rotary handle and all accessories including providing spreader terminals and auxiliary contacts (Ics=100% Icu value 25 KA ).
45.00 | a) 9 Nos. Phase indication LED lamps with 2Amp MCB, 03 Sets ON/OFF' indicating light with 2A MCB, 03 Nos Multifunction meter, class 0.5 with LCD Display shown V, A, Hz & PF.
46.00 | Bus Bar
47.00 | 200 Amps FP bus bar of high conductivity electrolytic quality aluminium alloy.
48.00 | Changeover
49.00 | 2 Nos. 160 A, Manual Change over with extended rotary handle and all accessories including providing spreader terminals etc. complate as required.
50.00 | Out Going
51.00 | 4 Nos. 100 A, four pole Thermal Magnetic release variable range, Moulded Case Circuit Breaker with extended rotary handle and all accessories including providing spreader terminals and auxiliary contacts (Ics=100% Icu value 25 KA).
52.00 | Note: Output of each changeover should be distributed to 2 Nos O/Gs with suitable subsections/compartments for MCCBs, bubars, metering, cable alleys etc.
53.00 | Supply, installation, testing and commissioning of dust, damp and vermin proof cubicle free floor, indoor type factory built sheet steel enclosed modular bolted construction, suitable for operation on 415 ±10% volts, 50 Hz AC 3 phase 4 wire supply system fabricated out of CRCA sheet steel of 2.0 mm thick for frame work and 2.0 mm thick for doors/ covers, 3mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports, bottom base channel of section not less than ISMC 75mm, entire panel shall have a common copper earth bar of suitable size with 2 nos earth studs, including control wiring with 1.5 sqmm. PVC insulated FRLS copper conductor Single Core cable for voltage & 2.5 sq.mm for current circuits, cable alleys, cable gland plates, danger notice plates, etc. necessary metering protections & indications and mounted with the following switch gears. | 1.00 | Each | 295887.34 | 230000.00 | 230000.00 | 428500.00 | 428500.00 | 180000.00 | 180000.00 | 180000.00 | JAI ENTERPRISES
54.00 | INCOMER i) 2 No. 100 Amps. 4P , MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equiped with extendable rotary Handle and extendable terminals with the following: a) 6 Nos. Phase indication LED lamps with 2Amp MCB, 02 Sets ON/OFF' indicating light with 2A MCB, 02 Nos Multifunction meter, class 0.5 with LCD Display shown V, A, Hz & PF.
55.00 | AUTO TRANSFER SWITCH i) 1 No. 4 pole, 100 Amps. Open execution type with complete protection.
56.00 | BUS-BAR : TPN aluminium main bus bars of minimum of 300 Amp capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bars supports at required intervals complete.
57.00 | OUT GOING: i) 3 No. 63 Amps. 4P, MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equiped with extendable Rotary handle. ii) 1 No. 100Amps. 4P, MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equiped with extendable Rotary handle with the following: 4 Set of ON‐OFF indication lamps (LED type) with 2 Amp control MCBs. iii) 04 Nos 32 A, 10 kA, DP MCB
58.00 | Power Quality Analyser & DATA LOGGER: Microprocessor based Multi channel Power Quality Analyzer and Data Logger device for electrical parameters measuring and monitoring on the data logger display as well as data archiving (storage) having inbuilt real time clock with power from a lithium-type battery
59.00 | LAPTOP FOR DATA RECORD: 64 bit, Window 10 loaded with user friendly programs, 15" screen Laptop with all accesssories having Intel Core i5 (10th Gen) or equivalent processor, HDD (1TB), RAM (8 GB), Graphic Card (1 GB) including wireless optical mouse etc. complete as required (HP Pavilion - 15-cs3006tx or equivalent)
60.00 | The panel shall have suitable DIN bar provision for fixing the Surge Protection Device of min. 4 modules
61.00 | Supply and installation of pre-wired Primary protection (Class B / Type 2) surge protection device (SPD) having 100KA , 10/350 micro seconds neutral to earth, 50 KA, 10/350 micro seconds line to neutral with limiting voltage less than 1.5 KV on the mains power entry point at the incomers. The enclosure shall have IP:65 weather proof polycarbonate PVC box with cable gland. The three phase SPD shall have the followings. i) Line protected : Line-Neutral and Neutral to earth + Line to Line +Line to Ground (4 modes). ii) Nominal Operating Voltage : 220/240 V AC iii) Input power Frequency : 47-60 Hz iv) Protection : Transverse and common mode v) Response Time : <100 ns vi) Surge rating : 10/350 us pulse response vii) Voltage Protection Level : < 1.5 KV viii) Approval and Testing : Listed with UL-1449-3/IEC - 61643 - 62305 as applicable. | 1.00 | Each | 25840.68 | 19000.00 | 19000.00 | 38082.00 | 38082.00 | 18000.00 | 18000.00 | 18000.00 | JAI ENTERPRISES
62.00 | Supply and installation of pre-wired Secondary protection (Class C / Type 3) surge protection device (SPD) this protection to be provided at UPS output in each phase and neutral. The protection device shall be a combination of multi stage modular MOV device to attenuate surge and noise. The LC filter shall attenuate surge voltage to limit peak surge to less than 900 Volt. The filter shall attenuate noise and power system harmonics by minimum 30 DB. The enclosure shall have IP:65 weather proof polycarbonate PVC box with cable gland. The Single phase SPD shall have the followings. i) Line protected : Line-Neutral, Line - Earth and Neutral to Earth. ii) Nominal Operating Voltage : 240 V AC (Phase to Neutral) iii) Voltage Drop : < 3 V at full load iv) Efficiency : 99% v) Response Time : <25 ns vi) Protection Modes : Transverse and Common mode vii) Filter Configuration : LC, transverse and common modes viii) Protection Stages : MOV, LPF SPD ix) Surge Rating : 40 KA, 8/20 us x) Voltage Protection Level : < 0.9 KV xi) Approvals and Testing : UL- 1449-3/ IEC 61643/ 62305 as applicable | 4.00 | Each | 22326.78 | 5800.00 | 23200.00 | 7173.00 | 28692.00 | 18000.00 | 72000.00 | 23200.00 | Awasthi Electric Works
63.00 | Providing & Fixing in position 1000 mm wide, Electrical Insulating Mat as per IS 15652:2006, 2 mm thick, suitable upto 3.3 KV, fire retardant, no effect of acids, alkalies and transformer oils, moiture proof, high tensile strength and texture fininsh/ cloth impression (Anti slip marking on top) etc. complete as required. | 2.00 | Sqm | 1144.80 | 900.00 | 1800.00 | 968.00 | 1936.00 | 900.00 | 1800.00 | 1800.00 | Awasthi Electric Works, JAI ENTERPRISES
64.00 | SH-IV: CABLE LAYING WORK
65.00 | Supply of aluminium conductor XLPE insulated, PVC sheathed, armoured power cable of 1.1 KV grade conforming to IS-7098 Part 1(1988) amended up to date.
66.00 | (a) 3.5 X 150 Sq mm | 3413.00 | Meter | 482.30 | 490.00 | 1672370.00 | 478.00 | 1631414.00 | 620.00 | 2116060.00 | 1631414.00 | Yash Energy Pvt. Ltd
67.00 | (b) 4 X 16 Sq mm | 20.00 | Meter | 100.70 | 125.00 | 2500.00 | 148.00 | 2960.00 | 260.00 | 5200.00 | 2500.00 | Awasthi Electric Works
68.00 | Supply of copper conductor XLPE insulated, PVC sheathed, FRLSZH at outer Sheath armoured power cable of 1.1 KV grade conforming to IS-7098 Part 1(1988) amended up to date.
69.00 | (a) 3 x 10 Sqmm | 60.00 | Meter | 310.58 | 349.00 | 20940.00 | 310.00 | 18600.00 | 420.00 | 25200.00 | 18600.00 | Yash Energy Pvt. Ltd
70.00 | (b) 3 x 2.5 sq mm | 130.00 | Meter | 103.88 | 130.00 | 16900.00 | 109.00 | 14170.00 | 180.00 | 23400.00 | 14170.00 | Yash Energy Pvt. Ltd
71.00 | (c) 2 x 1.5 Sqmm | 50.00 | Meter | 62.54 | 65.00 | 3250.00 | 88.00 | 4400.00 | 150.00 | 7500.00 | 3250.00 | Awasthi Electric Works
72.00 | Excavation for cable trenches in soft soil, depth upto 1.2 m including dressing of sides lift upto 1.5 m, including getting out the excavated soil, refilling with sand and or good soil after laying of cable/ pipe etc in layers of 20 cm, ramming, watering and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 430.00 | Cum | 489.72 | 190.00 | 81700.00 | 400.00 | 172000.00 | 200.00 | 86000.00 | 81700.00 | Awasthi Electric Works
73.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 20.00 | Cum | 903.12 | 450.00 | 9000.00 | 500.00 | 10000.00 | 220.00 | 4400.00 | 4400.00 | JAI ENTERPRISES
74.00 | Filling available excavated earth (excluding rock) in trenches, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 metres. | 20.00 | Cum | 190.80 | 100.00 | 2000.00 | 500.00 | 10000.00 | 250.00 | 5000.00 | 2000.00 | Awasthi Electric Works
75.00 | Providing and laying in position cement concrete 1:3:6 (1 cement : 2 coarse sand : 6 graded stone aggregate 40 mm nominal size) in road crossing/side wall of drain including form work etc as required. | 2.00 | Cum | 4157.32 | 6000.00 | 12000.00 | 7000.00 | 14000.00 | 220.00 | 440.00 | 440.00 | JAI ENTERPRISES
76.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) etc., complete as required.
77.00 | (a) 90 mm dia (OD-90 mm & ID-76 mm nominal) | 3220.00 | Meter | 129.32 | 110.00 | 354200.00 | 165.00 | 531300.00 | 220.00 | 708400.00 | 354200.00 | Awasthi Electric Works
78.00 | (b) 50 mm dia (OD -50mm & ID 40 mm nominal) | 80.00 | Meter | 74.20 | 50.00 | 4000.00 | 117.00 | 9360.00 | 230.00 | 18400.00 | 4000.00 | Awasthi Electric Works
79.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required.
80.00 | (a) 100 mm dia. | 30.00 | Meter | 1155.40 | 900.00 | 27000.00 | 1145.00 | 34350.00 | 290.00 | 8700.00 | 8700.00 | JAI ENTERPRISES
81.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required.
82.00 | (a) Upto 35 Sqmm | 20.00 | Meter | 28.62 | 35.00 | 700.00 | 30.00 | 600.00 | 60.00 | 1200.00 | 600.00 | Yash Energy Pvt. Ltd
83.00 | (b) Above 95 sq. mm and upto 185 sq. mm | 3250.00 | Meter | 58.30 | 40.00 | 130000.00 | 50.00 | 162500.00 | 60.00 | 195000.00 | 130000.00 | Awasthi Electric Works
84.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
85.00 | (a) 3.5 x 150 Sqmm | 6.00 | Each | 4604.64 | 1800.00 | 10800.00 | 2728.00 | 16368.00 | 2800.00 | 16800.00 | 10800.00 | Awasthi Electric Works
86.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
87.00 | (a) 3 X 2.5 sq. mm (12/16 mm) | 4.00 | Each | 183.38 | 250.00 | 1000.00 | 179.00 | 716.00 | 50.00 | 200.00 | 200.00 | JAI ENTERPRISES
88.00 | (b) 3 X 10 sq. mm (22mm) | 16.00 | Each | 203.52 | 250.00 | 4000.00 | 261.00 | 4176.00 | 100.00 | 1600.00 | 1600.00 | JAI ENTERPRISES
89.00 | (c) 4 X 16 sq. mm (28mm) | 2.00 | Each | 248.04 | 250.00 | 500.00 | 438.00 | 876.00 | 150.00 | 300.00 | 300.00 | JAI ENTERPRISES
90.00 | (d) 3.5 X 150 sq. mm (50 mm) | 7.00 | Each | 974.14 | 350.00 | 2450.00 | 1167.00 | 8169.00 | 300.00 | 2100.00 | 2100.00 | JAI ENTERPRISES
91.00 | SH V: EARTHING WORKS
92.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 2.00 | Each | 5354.06 | 5500.00 | 11000.00 | 10470.00 | 20940.00 | 4700.00 | 9400.00 | 9400.00 | JAI ENTERPRISES
93.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Meter | 488.66 | 480.00 | 9600.00 | 134.00 | 2680.00 | 250.00 | 5000.00 | 2680.00 | Yash Energy Pvt. Ltd
94.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 30.00 | Meter | 200.34 | 145.00 | 4350.00 | 122.00 | 3660.00 | 150.00 | 4500.00 | 3660.00 | Yash Energy Pvt. Ltd
95.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required | 10.00 | Each | 393.26 | 450.00 | 4500.00 | 1210.00 | 12100.00 | 400.00 | 4000.00 | 4000.00 | JAI ENTERPRISES
96.00 | Lightning Conductor
97.00 | Providing and fixing of lightning finial, made of 25 mm dia 300 mm long, copper tube, having single prong at top, with 85 mm dia 3mm thick copper base plate including holes etc. complete as required. | 3.00 | Each | 935.98 | 2150.00 | 6450.00 | 3025.00 | 9075.00 | 1800.00 | 5400.00 | 5400.00 | JAI ENTERPRISES
98.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 3.00 | Each | 10172.82 | 10500.00 | 31500.00 | 17625.00 | 52875.00 | 3500.00 | 10500.00 | 10500.00 | JAI ENTERPRISES
99.00 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the final or any other metallic object) by riveting / nut bolting/ sweating and soldering etc. as required. | 3.00 | Each | 91.16 | 330.00 | 990.00 | 500.00 | 1500.00 | 120.00 | 360.00 | 360.00 | JAI ENTERPRISES
100.00 | Providing and fixing copper tape 20mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required. (For horizontal run) | 35.00 | Meter | 449.44 | 395.00 | 13825.00 | 548.00 | 19180.00 | 150.00 | 5250.00 | 5250.00 | JAI ENTERPRISES
101.00 | Providing and fixing copper tape 20mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required. (For Vertical run) | 15.00 | Meter | 504.56 | 410.00 | 6150.00 | 548.00 | 8220.00 | 120.00 | 1800.00 | 1800.00 | JAI ENTERPRISES
102.00 | Providing and fixing testing joint, made of 20 mm X 3 mm thick Copper strip, 125 mm long, with 4 nos. of G.l. bolts, nuts, chuck nuts and spring washers etc. complete as required. | 3.00 | Each | 133.56 | 260.00 | 780.00 | 282.00 | 846.00 | 80.00 | 240.00 | 240.00 | JAI ENTERPRISES
103.00 | Providing and laying copper tape 32 mm X 6 mm from earth electrode in ground as required. | 20.00 | Meter | 1007.00 | 1250.00 | 25000.00 | 1408.00 | 28160.00 | 100.00 | 2000.00 | 2000.00 | JAI ENTERPRISES
104.00 | SH-VI: AIR CONDITIONING WORKS
105.00 | Supply of 1.5 TR highly energy efficient, hi-wall mounted Split type inverter Air-conditioner with high ISEER, 5 star rating, dual inverter compressor, cordless remote, suitable for operation on 230 Volts +/- 10%, 50 Hz, single phase A.C. supply, having copper condenser coil, capable of performing cooling, dehumidifying, air circulating, filtering and ventilation complete etc. as required. | 5.00 | Nos | 49496.70 | 42000.00 | 210000.00 | 35937.00 | 179685.00 | 35000.00 | 175000.00 | 175000.00 | JAI ENTERPRISES
106.00 | Installation, Testing & commissioning of A/C units as mentioned in item no-1 which includes mounting of indoor & outdoor unit including providing MS stand/ PCC platform at their respective location along with laying of refrigerant pipeline with insulation & flexible PVC covering pipe up to standard length supplied with the unit , connecting both the units , leak testing of entire system, connecting both indoor and outdoor units with three core PVC insulated flexible copper cable supplied with the unit , top up of refrigerant (if required), minor civil repairing work as per site requirement complete as required. | 5.00 | Job | 1494.60 | 2500.00 | 12500.00 | 2500.00 | 12500.00 | 1000.00 | 5000.00 | 5000.00 | JAI ENTERPRISES
107.00 | Supplying and fixing 20/16 A, 240 V, IP 40, SPN AC Distribution Box/socket outlet, with 2 pole and earth, High grade Thermoplastic enclosed plug top alongwith 20/16 A "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 5.00 | Nos | 1753.24 | 830.00 | 4150.00 | 1593.00 | 7965.00 | 1200.00 | 6000.00 | 4150.00 | Awasthi Electric Works
108.00 | Supply of bubble top Hot and Cold water dispenser with three faucets (normal, hot and cold) having capacity not less than 15 litre, with non CFC Refrigerant and 02 Nos duly filled 20 L Water Bottles/Cans etc. as required. | 1.00 | Each | 9149.92 | 9500.00 | 9500.00 | 19150.00 | 19150.00 | 1500.00 | 1500.00 | 1500.00 | JAI ENTERPRISES
109.00 | SH-VII: FADS & FIRE EXTINGUISHERS
110.00 | Supply and Installation of Microprocessor based 2 Zone non-expandable conventional fire alarm panel, should be equiped of 2 Zone capacity to take maximum 20 detections per Zone, reset function inbuilt and alarm & Fault Display by individual LEDs for each detector group. 240 volts AC power supply, automatic battery charges, 2 Nos. X 12 volt sealed maintenance free batteries sufficient for 12 hours normal working. | 1.00 | Each | 21200.00 | 13000.00 | 13000.00 | 11680.00 | 11680.00 | 8000.00 | 8000.00 | 8000.00 | JAI ENTERPRISES
111.00 | Supply and Installation of 2 Channel Wireless auto dialer (GSM based) voice message. 40 (20+20) seconds voice recording. 9 nos. of tel./mobile 16 digit each. View numbers & user setting any time. Standard telephone key pads. Work with all types of GSM network. Easy menu based programming. 1 levels of password protected. Approved by various consultants. | 1.00 | Each | 10600.00 | 11500.00 | 11500.00 | 20150.00 | 20150.00 | 1500.00 | 1500.00 | 1500.00 | JAI ENTERPRISES
112.00 | Supply and Installation of Conventional Type smoke Detector with LED indication, with mounting base complete etc. as required. | 4.00 | Each | 2120.00 | 1050.00 | 4200.00 | 2278.00 | 9112.00 | 1200.00 | 4800.00 | 4200.00 | Awasthi Electric Works
113.00 | Supply and Installation of Conventional Hooter complete etc. as required. | 1.00 | Each | 1908.00 | 1290.00 | 1290.00 | 1310.00 | 1310.00 | 800.00 | 800.00 | 800.00 | JAI ENTERPRISES
114.00 | Supply and Installation of manual call points complete etc. as required. | 1.00 | Each | 1590.00 | 890.00 | 890.00 | 1310.00 | 1310.00 | 800.00 | 800.00 | 800.00 | JAI ENTERPRISES
115.00 | SITC of Response indicator complete etc. as required. | 2.00 | Each | 318.00 | 250.00 | 500.00 | 826.00 | 1652.00 | 500.00 | 1000.00 | 500.00 | Awasthi Electric Works
116.00 | Supply of carbon dioxide (CO2) type fire extinguishers confi rming to IS 2878 : 1976 and cylinders fully charged of following capacity including providing suitable M.S. Stand. (a) 4.5 KG | 4.00 | Each | 16620.80 | 7000.00 | 28000.00 | 7865.00 | 31460.00 | 900.00 | 3600.00 | 3600.00 | JAI ENTERPRISES
| Total in Figures |  |  |  |  | 3458809.00 |  | 3955387.00 |  | 4134056.00
Lowest Amount Quoted BY: Awasthi Electric Works(3458809.00)

## BOQ Summary
BOQ Summary Details Tender Title: Extension of runway at 24 beginning, expansion of apron suitable for C category of aircraft and other associated works at S.V. Airport, Raipur. SH Electrical works for Trans-Installation of Glide Path. Tender ID: 2020_AAI_62081_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works | 3458809.00 | L1
| 2 | Yash Energy Pvt. Ltd | 3955387.00 | L2
| 3 | JAI ENTERPRISES | 4134056.00 | L3