## BoQ1
Government eProcurement System Created By: Samir Naskar Created Date/Time: 04-Dec-2020 06:04 PM Tender Title: Consruction of 6 High Dependency Units and 2 Intesive Care Units Hospital near LBSI Airport, Varanasi, SH Provision of Sub Station equipments and associated works etc. Tender ID: 2020_AAI_62190_1
Tender Inviting Authority: Sr. Manager (Engg.-E), LBSI Airport Varanasi.
Name of work: Construction of 6 High Dependency Units (HDU) and 2 Intensive Care Units (ICU) Hospital near LBSI Airport Varanasi. (SH:Provision of Sub Station equipments & associated works etc.)
Contract No: 2020_AAI_ 62190_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | m/s anil kumar singh(GSTN-09AVFPS4608C1ZL) |  | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | MEC ENGINEERS(GSTN-09AABFM1296R1ZM) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply ,installation,testing and commissiong of indoor type LT panel (PTTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , Incomer and outgoing should be of four pole MCCB with rotary handle, panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMERS:250 A,4P, 35 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. OUTGOINGS:125 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -2 Nos. 63 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -8 Nos. 32 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -3 Nos. 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-01 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Aluminium bus bar but not less than 300 Amps. | 1.00 | Each |  | 226700.00 | 226700.00 | 400000.00 | 400000.00 | 388000.00 | 388000.00 | 220000.00 | 220000.00 | 220000.00 | Awasthi Electric Works
2.00 | Supply ,installation,testing and commissiong of indoor type LT panel (TTA), made out of 2 mm CRCA sheet steel, totally enclosed, minimum IP 42 protection, free standing, floor mounting, dust and vermin proof ,compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with breaker control switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required, suitable electrical and mechanical interlocking as required between incomers and bus couplers , Incomer and outgoing should be of four pole MCCB with rotary handle, panel should have continous GI earth strip of suitable size throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom or top entry of cables as required including supply & installation of all items as below and as per detailed specifications. Works includes loading & unloading, Positioning,Testing, Commissioning of panel & necessary minor civil works e.g. providing C-C channel etc. complete as per site requirement and as per Instruction of E-I-C. INCOMERS:320 A,4P, 36 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. OUTGOINGS:250 A,4P, 36 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -1 Nos. 63 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -2 Nos. 32 A,4P, 25 kA,MCCB with thermal magnetic release O/L , S/C (Ics=Icu=100 %) -2 Nos. 1 Lot of control wiring & 1 Set of designation plates. Multifunction Meter: Digital Multifunction Meter with all normal electrical parameter (V,A,f) i/c KWh & MD etc.-01 No Indicating lamp : RYB,ON/OFF/TRIP LED type Indicating Lamps for all Incomers & Outgoings. - 01 set BUS BARS: Suitable size TPN Aluminium bus bar but not less than 400 Amps. | 1.00 | Each |  | 240900.00 | 240900.00 | 500000.00 | 500000.00 | 300000.00 | 300000.00 | 170000.00 | 170000.00 | 170000.00 | Awasthi Electric Works
3.00 | Supply ,installation,testing and commissiong of 250 KVA ,11KV/433Volt,3 phase ,50 Hz ,Dyn 11,outdoor ONAN type,copper wound transformer with off load tap changing arrangement with taping +5% to -10% in steps of 2.5%, having cable end boxes on HV side suitable for 11kv grade arrangement and XPLE aluminium armoured cable on LV side complete with all aceessories i/c first fill of filtered dehydrated oil and confirming to IS 1180 (Level-2) with up to date amendments & as per specification attached complete in all respects as required at site. | 1.00 | Each |  | 561400.00 | 561400.00 | 550000.00 | 550000.00 | 548000.00 | 548000.00 | 649000.00 | 649000.00 | 548000.00 | MEC ENGINEERS
4.00 | 11 KV H.T. (I/C-01 No. & O/G- 01 No.) BREAKER SWITCH BOARD PANEL SITC of indoor cubicle type floor mounted metal clad 11KV VCB Panel Board with 11 KV, 350MVA , 630A, HT VCB (One incomer & One outgoing VCB),totally enclosed & fully interlocked, horizontal draw out, horizontal / vertical Isolation type breaker as per IEC 62271-100 for breaker & 62271-200 for panels and of capacity as mentioned below, single break, trip free mechanism, motor / manually charged and auto / manual closing breaker suitable for use on 11KV 3 phase 50 Hz AC supply complete with self contained, fully interlocked, rack in and rackout mechanism, air insulated but encapsulated copper bus bars of 630 Amp capacity, Breaker featured with mechanical ON/OFF indication with hand trip device,DC power pack, spring released coil, shunt trip coil and auxiliary switchs and equipped with switchgears mentioned below. Panel Board shall be provided with Earthing troley for incoming side / Busbar / outgoing breakers earthing, Panel Board shall be fabricated, made out of 2 mm thick CRCA sheet steel, totally enclosed, IP 4X, free standing, floor mounting, dust and vermin proof ,indoor, compartmentalized, powder coated painting including internally wired / interconnected with suitable provision for end termination with heat shrinkable jointing material etc as required (Note cost of end termination not included in this item) (VCBs shall be SCADA compatible & shall have feature for control & monitoring by SCADA system/ BMS in future.(Cost of SCADA system not included in this item). Incomer (a) 630A,Minimum18.3kA, 11KV, 3 phase, 50 Hz Vacuum Circuit Breaker(VCB),Icu=Ics=Icw=100% and withstand capacity of 3 seconds -1 No. (b) 3 phase 11 KV/110 V Volts PT, class 1.0 accuracy and 100 VA burden with 1 No Voltmeter (0-15 KV), Digital type, selector switch for voltmeter and protection fuses for HT metering upto 15 KV on incomer (Voltmeter shall have communication features for monitoring by BMS) - 1set (c ) 3 CTs 30/5A of 15 VA burden and accuracy class 1.0 for metering and class 5P10 for protection-1 set (d ) Multi function meter to display F, PF, kW, kVA, kVAR, kWh, kVAh, kVARh, THD, Phase angles, Power demand parameters, suitable for operation on 110V a.c supply, with RS-485 interface for integration to BMS- 1 No (e) Microprocessor based numerical relay for Over current and Earth fault protection -1 No. (f) 0-50 Amps Ammeter, digital type with selector switch for ammeters. (ammeter shall have communication features for monitoring by BMS) -1 No. (g) Phase indicating lamps with HRC fuses/MCB-1 Set (h) Indicating lamps to indicate OPEN, CLOSE, TRIP, SPRING CHARGED, TRIP CIRCUIT HEALTHY-1 set (i) 630 Amps TP Copper Busbar-1 set (j) Test terminal block-1 No (k) Copper bus bar of suitable size for earthing-1 set (l) Master trip relay & trip circuit healthy supervision relay.-1 set (m) Provision for padlocking the incomer VCBs in 'OFF' position.-1 No. Outgoing (a) 630A,Minimum 18.3kA, 11KV, 3 phase, 50 Hz Vacuum Circuit Breaker(VCB),Icu=Ics=Icw=100% and withstand capacity of 3 seconds -1 No. (b) 3 CTs 30/5A of 15 VA burden and accuracy class 1.0 for metering and class 5P10 for protection - 1 Set. (c) Microprocessor based numerical relay for O/C and E/F protection- 1 No (d) 0-50 Amp, digital type ammeter with selector switch (ammeter shall have communication features for monitoring by BMS)- 1 No. (e) indicating lamps to indicate OPEN, CLOSE, TRIP, SPRING CHARGED, TRIP CIRCUIT HEALTHY- 1 set (f) Master trip relay & trip circuit healthy supervision relay-1 set (g) Annunciator (having minimum 8 windows) and alarm bell/ hooter - 1 No. (h) Protection arrangements with necessary auxiliary relays for connecting the WTI of Transformer- 1 set NOTE:-All metering and protection devices, interconnections, necessary control wiring and all other accessories shall be provided as per SLD or as required as per specifications and technical particulars and as per instruction of E-I-C. | 1.00 | Each |  | 879509.00 | 879509.00 | 800000.00 | 800000.00 | 800000.00 | 800000.00 | 889000.00 | 889000.00 | 800000.00 | jaydeep agency corporation, MEC ENGINEERS
5.00 | Supply of 11 KV grade (11 KV Earthed System) XLPE insulated , PVC sheathed, Aluminium Conductor,Armoured Power cable of size 3X70 sq mm, Conforming to IS: 7098 (Part - II) amended upto date. | 170.00 | Meter |  | 700.00 | 119000.00 | 500.00 | 85000.00 | 445.00 | 75650.00 | 549.00 | 93330.00 | 75650.00 | MEC ENGINEERS
6.00 | Supply of 4 x 10 sq.mm XLPE insulated & PVC sheathed armoured aluminium conductor cable of , 1.1KV grade conforming to I.S : 7098 (Part-I ) with upto date ammendments. | 280.00 | Meter |  | 120.00 | 33600.00 | 80.00 | 22400.00 | 82.00 | 22960.00 | 97.00 | 27160.00 | 22400.00 | jaydeep agency corporation
7.00 | Supply of 4 x 25 sq.mm XLPE insulated & PVC sheathed armoured aluminium conductor cable of , 1.1KV grade conforming to I.S : 7098 (Part-I ) with upto date ammendments. | 150.00 | Meter |  | 200.00 | 30000.00 | 200.00 | 30000.00 | 126.00 | 18900.00 | 158.00 | 23700.00 | 18900.00 | MEC ENGINEERS
8.00 | Supply of 3.5 x 35 sq.mm XLPE insulated & PVC sheathed armoured aluminium conductor cable of , 1.1KV grade conforming to I.S : 7098 (Part-I ) with upto date ammendments. | 400.00 | Meter |  | 230.00 | 92000.00 | 225.00 | 90000.00 | 145.00 | 58000.00 | 182.00 | 72800.00 | 58000.00 | MEC ENGINEERS
9.00 | Supply of 3.5 x 95 sq.mm XLPE insulated & PVC sheathed armoured aluminium conductor cable of , 1.1KV grade conforming to I.S : 7098 (Part-I ) with upto date ammendments. | 140.00 | Meter |  | 475.00 | 66500.00 | 320.00 | 44800.00 | 305.00 | 42700.00 | 385.00 | 53900.00 | 42700.00 | MEC ENGINEERS
10.00 | Supply of 3.5 x 120 sq.mm XLPE insulated & PVC sheathed armoured aluminium conductor cable of , 1.1KV grade conforming to I.S : 7098 (Part-I ) with upto date ammendments. | 80.00 | Meter |  | 600.00 | 48000.00 | 400.00 | 32000.00 | 385.00 | 30800.00 | 490.00 | 39200.00 | 30800.00 | MEC ENGINEERS
11.00 | Supply of 40 mm outer dia PN-6, PE80, ISI Marked HDPE Pipe conforming to IS 4984:2016 with up to date ammendments complete as required. | 275.00 | Meter |  | 80.00 | 22000.00 | 80.00 | 22000.00 | 36.00 | 9900.00 | 46.00 | 12650.00 | 9900.00 | MEC ENGINEERS
12.00 | Supply of 63 mm outer dia PN-6, PE80, ISI Marked HDPE Pipe conforming to IS 4984:2016 with up to date ammendments complete as required. | 400.00 | Meter |  | 150.00 | 60000.00 | 120.00 | 48000.00 | 86.00 | 34400.00 | 110.00 | 44000.00 | 34400.00 | MEC ENGINEERS
13.00 | Supply of 110 mm outer dia PN-6, PE80, ISI Marked HDPE Pipe conforming to IS 4984:2016 with up to date ammendments complete as required. | 390.00 | Meter |  | 410.00 | 159900.00 | 200.00 | 78000.00 | 246.00 | 95940.00 | 320.00 | 124800.00 | 78000.00 | jaydeep agency corporation
14.00 | Laying of 40/63mm dia HDPE/MS Pipe direct in under ground at depth of 75 cm below ground level including soil excavation and refilling the trench etc. as required. | 675.00 | Meter |  | 120.00 | 81000.00 | 55.00 | 37125.00 | 180.00 | 121500.00 | 115.00 | 77625.00 | 37125.00 | jaydeep agency corporation
15.00 | Laying of 110 mm dia HDPE/MS Pipe direct in under ground at depth of 75 cm below ground level including soil excavation and refilling the trench etc. as required. | 220.00 | Meter |  | 120.00 | 26400.00 | 60.00 | 13200.00 | 180.00 | 39600.00 | 115.00 | 25300.00 | 13200.00 | jaydeep agency corporation
16.00 | Laying of 110 mm dia HDPE/MS Pipe direct in under ground at depth of 120 cm below ground level including soil excavation and refilling the trench etc. as required. | 170.00 | Meter |  | 190.00 | 32300.00 | 80.00 | 13600.00 | 200.00 | 34000.00 | 120.00 | 20400.00 | 13600.00 | jaydeep agency corporation
17.00 | Laying of one number PVC insulated and PVC sheathed XLPE power cable of 1.1 kV grade cable of size upto 35 sq mm in the existing RCC/ HUME/ METAL / HDPE pipe as required. | 675.00 | Meter |  | 30.00 | 20250.00 | 20.00 | 13500.00 | 80.00 | 54000.00 | 30.00 | 20250.00 | 13500.00 | jaydeep agency corporation
18.00 | Laying of one number PVC insulated and PVC sheathed XLPE power cable of 1.1 kV grade cable of size above 35 sq mm and upto 95 sq mm in the existing RCC/ HUME/ METAL / HDPE pipe as required. | 310.00 | Meter |  | 50.00 | 15500.00 | 25.00 | 7750.00 | 80.00 | 24800.00 | 50.00 | 15500.00 | 7750.00 | jaydeep agency corporation
19.00 | Laying of one number PVC insulated and PVC sheathed XLPE power cable of 1.1 kV grade cable of size above 95 sq mm and upto 185 sq mm in the existing RCC/ HUME/ METAL / HDPE pipe as required. | 80.00 | Meter |  | 60.00 | 4800.00 | 30.00 | 2400.00 | 80.00 | 6400.00 | 60.00 | 4800.00 | 2400.00 | jaydeep agency corporation
20.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade Upto 35 sq. mm (clamped with 1mm thick saddle) on wall surface as required. | 155.00 | Meter |  | 35.00 | 5425.00 | 25.00 | 3875.00 | 60.00 | 9300.00 | 45.00 | 6975.00 | 3875.00 | jaydeep agency corporation
21.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4X10 Sqmm XLPE armoured aluminium conductor cable of 1.1 KVgrade as required. | 14.00 | Each |  | 200.00 | 2800.00 | 100.00 | 1400.00 | 450.00 | 6300.00 | 200.00 | 2800.00 | 1400.00 | jaydeep agency corporation
22.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4X25 Sqmm XLPE armoured aluminium conductor cable of 1.1 KVgrade as required. | 4.00 | Each |  | 220.00 | 880.00 | 110.00 | 440.00 | 450.00 | 1800.00 | 245.00 | 980.00 | 440.00 | jaydeep agency corporation
23.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5X35 Sqmm XLPE armoured aluminium conductor cable of 1.1 KVgrade as required. | 2.00 | Each |  | 260.00 | 520.00 | 120.00 | 240.00 | 600.00 | 1200.00 | 290.00 | 580.00 | 240.00 | jaydeep agency corporation
24.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5X95 Sqmm XLPE armoured aluminium conductor cable of 1.1 KVgrade as required. | 12.00 | Each |  | 400.00 | 4800.00 | 150.00 | 1800.00 | 750.00 | 9000.00 | 450.00 | 5400.00 | 1800.00 | jaydeep agency corporation
25.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5X120 Sqmm XLPE armoured aluminium conductor cable of 1.1 KVgrade as required. | 2.00 | Each |  | 410.00 | 820.00 | 220.00 | 440.00 | 1000.00 | 2000.00 | 470.00 | 940.00 | 440.00 | jaydeep agency corporation
26.00 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for 3.5 X 120 sq. mm of PVC insulated and PVC sheathed /XLPE aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Each |  | 1380.00 | 2760.00 | 750.00 | 1500.00 | 445.00 | 890.00 | 1800.00 | 3600.00 | 890.00 | MEC ENGINEERS
27.00 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 70 sq mm of 3 core, XLPE aluminium conductor cable of 11 KV grade as required. | 2.00 | Each |  | 11250.00 | 22500.00 | 2800.00 | 5600.00 | 4500.00 | 9000.00 | 2000.00 | 4000.00 | 4000.00 | Awasthi Electric Works
28.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 70 sq mm of 3 core, XLPE aluminium conductor cable of 11 KV grade as required. | 2.00 | Each |  | 6600.00 | 13200.00 | 2300.00 | 4600.00 | 4500.00 | 9000.00 | 1750.00 | 3500.00 | 3500.00 | Awasthi Electric Works
29.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 10.00 | Each |  | 5500.00 | 55000.00 | 3900.00 | 39000.00 | 8000.00 | 80000.00 | 4500.00 | 45000.00 | 39000.00 | jaydeep agency corporation
30.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 30.00 | Mtr. |  | 100.00 | 3000.00 | 120.00 | 3600.00 | 125.00 | 3750.00 | 125.00 | 3750.00 | 3000.00 | m/s anil kumar singh
31.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required | 50.00 | Mtr. |  | 380.00 | 19000.00 | 390.00 | 19500.00 | 400.00 | 20000.00 | 450.00 | 22500.00 | 19000.00 | m/s anil kumar singh
32.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | Mtr. |  | 160.00 | 8000.00 | 120.00 | 6000.00 | 120.00 | 6000.00 | 180.00 | 9000.00 | 6000.00 | jaydeep agency corporation, MEC ENGINEERS
33.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Each |  | 10400.00 | 41600.00 | 6800.00 | 27200.00 | 11000.00 | 44000.00 | 10500.00 | 42000.00 | 27200.00 | jaydeep agency corporation
34.00 | Supplying and laying 25 mm X 5 mm Copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 20.00 | Mtr. |  | 650.00 | 13000.00 | 750.00 | 15000.00 | 860.00 | 17200.00 | 850.00 | 17000.00 | 13000.00 | m/s anil kumar singh
35.00 | Providing and fixing 25 mm X 5 mm Copper strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required | 20.00 | Mtr. |  | 950.00 | 19000.00 | 980.00 | 19600.00 | 1130.00 | 22600.00 | 1150.00 | 23000.00 | 19000.00 | m/s anil kumar singh
36.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 830.00 | Mtr. |  | 50.00 | 41500.00 | 20.00 | 16600.00 | 22.00 | 18260.00 | 18.00 | 14940.00 | 14940.00 | Awasthi Electric Works
37.00 | Supply, Installation, Testing and Commissioning of ‘Silent Type’ Diesel Generating set alongwith having Prime Power Rating of 180 KVA, 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz, 3 phase system & for 0.85 Load Factor and consisting of the followings: Diesel Engine : Diesel engine 4 stroke water cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 40 Degree C, 50% RH & at 1000 Meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted complete with all the required accessories. Engine mounted Instrument Panel fitted with and having digital display for following: (i) Start-stop switch with key (ii) Water temperature indication (iii) Lubrication oil pressure indication (iv) Lubrication oil temperature indication (v) Battery charging indication (vi) RPM indication (vii) Over speed indication (viii) Low lub. Oil trip indication (ix) Engine Hours indication Alternator: Synchronous alternator rated at 180 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 1000 Meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR conforming to IS: 4722/BS 2613 suitable for tropical conditions and with class- F/H insulation. Base Frame & Foundation : Both the engine and alternator shall be mounted on suitable base frame made of MS fabricated base frame with AVM pads. which shall be installed on existing cement concrete foundation and vibration isolation arrangement as per recommendations of manufacturer. Fuel line work : Daily service inbuilt fuel tank of OEM recommended capacity fabricated out of 2 mm thick M.S. sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class ‘C’ pipes of suitable dia. complete with valves, level indications & accessories as required as per specifications and as per OEM recommendations. Exhaust System : Dry exhaust mainfold with hospital exhaust silencer and catalytic convertor. Starting System : 12/24V DC starting system comprising of starter motors, voltage regulator and arrangement for initial excitation complete with suitable nos of batteries and its capacity as per OEM recommendation. Acoustic Enclosure: Accoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifi cations. | 1.00 | Each |  | 1233500.00 | 1233500.00 | 1111000.00 | 1111000.00 | 1400000.00 | 1400000.00 | 1245000.00 | 1245000.00 | 1111000.00 | jaydeep agency corporation
38.00 | Design, Supply, Installation, Testing and Commissioning of 315 Amp,36 kA capacity indoor and cubicle type AMF panel suitable for 180 KVA DG Set , made out of 2 mm CRCA sheet steel, totally enclosed, IP 42 protection, free standing, floor mounting, dust and vermin proof, compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system , interconnections with suitable size of copper lead/ solid aluminium strips, control circuit with switch , digital type ammeter and voltmeter,LED type indicating lamps, CT's as required and having 02 nos 315 AMP FP MCCB, 35kA (MP Based OC, S/C & E/F protection) for Main & DG Incomers with 315A FP Power Contactors and 01 No. Manual ON Load Changeover for bypass in event failure of AMF i/c required numbers of AMF relay, over current and earth fault relay,over and under voltage relay, alternator and main voltage monitor relay, engine start and engine cranking relay. Panel should have continous suitable size GI earth strip throughout the length of panel with earth terminations at both the ends ,cable alleys suitable for bottom entry of cables including supply & installation of all items as trequired and as per tender technical specification . Works includes required minor civil works like providing C- chanel etc as required at site. Loading & unloading, Positioning, Testing and Commissioning of panel complete as per site requirement and as per Instruction of E-I-C. | 1.00 | Each |  | 510000.00 | 510000.00 | 320000.00 | 320000.00 | 450000.00 | 450000.00 | 210000.00 | 210000.00 | 210000.00 | Awasthi Electric Works
39.00 | Providing and laying in position cement concrete 1:2:4 (1cement: 2 coarse sand :4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required. | 8.00 | Cum |  | 6600.00 | 52800.00 | 2450.00 | 19600.00 | 10000.00 | 80000.00 | 5500.00 | 44000.00 | 19600.00 | jaydeep agency corporation
40.00 | Supply and fixing of minimum 125mm dia. size ,Class C MS Piping with 50mm thick mineralwool/glasswool/Rockwool insulation (of 46 kg per cubic meter density) around the exhaust pipes of 180 KVA DG set including cladding with aluminium sheet of 0.60mm thick for exhaust including providing suitable bends, reducers & supporting arrangement at suitable intervals for attaching the pipe to existing RCC /steel structure, painting etc. as required. | 10.00 | Rm |  | 6500.00 | 65000.00 | 1850.00 | 18500.00 | 5000.00 | 50000.00 | 5200.00 | 52000.00 | 18500.00 | jaydeep agency corporation
41.00 | Providing & fixing for MS support structure for exhaust fume pipes from DG Sets (Exhaust pipe to be measured and paid for separately) for bottom support along horizontal and vertical runs upto the height (as per CPCB norms) including cutting, welding etc and applying two coats of red oxide and two coats of synthetic enamelled paint of colour and shade as directed by E-I-C. The design of the support structure shall be done by the contractor and shall be suitable to the exhaust pipe height as per CPCB norms approved , also to get the approval from the E-I-C. before execution etc. as required. Work include all necessary civil work. | 200.00 | Kg |  | 150.00 | 30000.00 | 85.00 | 17000.00 | 150.00 | 30000.00 | 240.00 | 48000.00 | 17000.00 | jaydeep agency corporation
42.00 | Design, detailed engineering Manufacturing, supply,Installation,testing and commisioning of Grid connected roof top solar PV power Plant of the required capacity as per tender specifications i/c transportation,insurance,transit insurance,required civil work for foundation etc, storage of materials,statutory clearances &approvals etc and any other items or accessories required for successful commissioning of power plant. | 50000.00 | Wp |  | 25.00 | 1250000.00 | 45.00 | 2250000.00 | 50.00 | 2500000.00 | 41.00 | 2050000.00 | 1250000.00 | m/s anil kumar singh
43.00 | Supply ,installation testing and commisiong of double pole structure on STP of 11 mtr long alongwith 11 KV disc/pin insulator, suitable MS channel, 11 KV TPMO set , 11KV fuse set, painting , grouting etc complete as required including dismantling of existing structure. | 1.00 | Set |  | 175000.00 | 175000.00 | 120000.00 | 120000.00 | 200000.00 | 200000.00 | 34000.00 | 34000.00 | 34000.00 | Awasthi Electric Works
| Total in Figures |  |  |  |  | 6289864.00 |  | 6812270.00 |  | 7675850.00 |  | 6472380.00
Lowest Amount Quoted BY: m/s anil kumar singh(6289864.00)

## BOQ Summary
BOQ Summary Details Tender Title: Consruction of 6 High Dependency Units and 2 Intesive Care Units Hospital near LBSI Airport, Varanasi, SH Provision of Sub Station equipments and associated works etc. Tender ID: 2020_AAI_62190_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | m/s anil kumar singh | 6289864.00 | L1
| 2 | Awasthi Electric Works | 6472380.00 | L2
| 3 | jaydeep agency corporation | 6812270.00 | L3
| 4 | MEC ENGINEERS | 7675850.00 | L4