## BoQ1
Government eProcurement System Created By: THIRUNAVUKKARASU M Created Date/Time: 21-Dec-2020 03:45 PM Tender Title: Replacement of 3X100 TR Chiller Plant, Chilled Water Pumps and Associated Works at RHQ-Admin Block, Chennai Airport Tender ID: 2020_AAI_62346_1
Tender Inviting Authority: Asst. General Manager (Engg-Electrical), AAI, RHQ SR, Chennai Airport, Chennai - 600027
Name of Work:Replacement of 3 x 100 TR Chiller plant , Chilled water pumps & Associated works at RHQ - Admin Block, Chennai Airport.
Contract No: 2020_AAI_62346_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Item Code | Pneumatic Engineers Pvt. Ltd.(GSTN-07AACCP0422A2Z8) |  | VOLTAS LIMITED(GSTN-33AAACV2809DIZT) |  | ETA ENGINEERING PVT LTD(GSTN-33AAACE0808P1ZQ) |  | YUDEK ENGINEERING P LTD(GSTN-NA) |  | OZONE AIR CONDITIONING AND CONSULTANCY(GSTN-NA) |  | VK BUILDING SERVICES PVT.LTD.(GSTN-NA)
[5 empty] | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | L1 Rate Without Tax | L1 Bidder Without Tax | L1 Rate With Tax | L1 Bidder With Tax
1.00 | Supply,Installation, Testing and commissioning of not less than 100 TR actual capacity Air cooled Screw Chiller with hermetic /semi hermetic Screw compressor, flooded type evaporator, air cooled condenser with all accessories, interconnecting hard drawn copper refringent piping and aluminium fins, Star Delta starter or soft starter, power & control cabling between starter and the compressor motor i/c suitable capacity of 4 Pole MCCB for incomming power cable Termination etc., Micro processor based control panel & complete with all safety controls, automatic capacity controls, first charge of refrigerant Gas R134a with Oil, required platforms with railings for maintenance etc & if required the existing RCC foundation to be modified and vibration isolators to be provided etc., The chillers are to be installed on the First floor and shall be suitable for 3 phase, 415 V, 50Hz AC supply etc complete as req. Note: The price shall include pre shipping inspection/ testing at the works of the manufacturer, freight, insurance, port clearance if any, loading/ unloading, installation, testing and commissioning etc. the chiller plant to be installed in the existing foundation if required minor modification to be made by the agency, levelling of machines, installation as per OEM recommendations, testing of all safeties and interlocks etc as required for commissioning of plant and after summer and monsoon season tests, etc. | 3.00 | Jobs | Item No.1 | 6000000.00 | 7080000.00 | 6409440.00 | 7563139.00 | 6181998.00 | 7294758.00 | 6153000.00 | 7260540.00 | 6627813.00 | 7820819.00 | 8215161.00 | 9693890.00 | 6000000.00 | Pneumatic Engineers Pvt. Ltd. | 7080000.00 | Pneumatic Engineers Pvt. Ltd.
2.00 | Supply, installation, testing and commissioning of End Suction Back Pull Out Centrifugal pumpset with 50mm EPS insulation suitable of the following capacity for re circulation of chilled water for the central air conditioning system. The pump motor shall be continuous duty , factory mounted on common base with pump and suitable for 415 volts, 50 cycles, 3 phase AC power supply. The shaft shall be out of alloy steel construction, the impeller shall be of bronze contruction and the casing shall be of cast iron construction complete in all respects as required by the standard specifications. Note: The price shall include for providing of suitable star delta starter, modification of existing foundation, providing of anti vibration Isolation pads etc as required as per OEM recommendations. Flow rate : 300 US GPM & 30 Mtrs. Head. | 3.00 | Jobs | Item No.2 | 390000.00 | 460200.00 | 413970.00 | 488485.00 | 551976.00 | 651332.00 | 312000.00 | 368160.00 | 544806.00 | 642871.00 | 512967.00 | 605301.00 | 312000.00 | YUDEK ENGINEERING P LTD | 368160.00 | YUDEK ENGINEERING P LTD
3.00 | Supply, installation, testing and commissioning of following nominal size of chilled water piping of MS "C" class Heavy duty pipes with 50mm EPS insulation provided complete with all fittings and accessories like Bends, Tees, reducers, exp. Joints supports, clamps, etc complete as required and as per speification (For pipes of dia. up to 200 mm IS 1239 (1) & above, IS 3589)
3.10 | 100 mm dia | 40.00 | Meter | Item No.3 (a) | 88000.00 | 103840.00 | 101200.00 | 119416.00 | 135800.00 | 160244.00 | 98120.00 | 115782.00 | 67000.00 | 79060.00 | 89320.00 | 105398.00 | 67000.00 | OZONE AIR CONDITIONING AND CONSULTANCY | 79060.00 | OZONE AIR CONDITIONING AND CONSULTANCY
3.20 | 80 mm dia | 40.00 | Meter | Item No.3 (b) | 76000.00 | 89680.00 | 78800.00 | 92984.00 | 111240.00 | 131263.00 | 85080.00 | 100394.00 | 50560.00 | 59661.00 | 69120.00 | 81562.00 | 50560.00 | OZONE AIR CONDITIONING AND CONSULTANCY | 59661.00 | OZONE AIR CONDITIONING AND CONSULTANCY
4.00 | Supply, Installation, Testing and commissioning of PN 16 rating of 100 mm dia CI Butterfly valves SS Disc duly insulated with 50 mm EPS insulation in chilled water lines complete with nuts, bolts, gaskets, adequate supports etc conforming to specifications provided. | 12.00 | Nos | Item No.4 | 72000.00 | 84960.00 | 65760.00 | 77597.00 | 117420.00 | 138556.00 | 152340.00 | 179761.00 | 68148.00 | 80415.00 | 65700.00 | 77526.00 | 65700.00 | VK BUILDING SERVICES PVT.LTD. | 77526.00 | VK BUILDING SERVICES PVT.LTD.
5.00 | Supply, Installation, Testing and commissioning of PN 16 rating of 80 mm dia CI Butterfly valves duly insulated with 50 mm EPS insulation in chilled water lines complete with nuts, bolts, gaskets, adequate supports etc conforming to specifications provided. | 16.00 | Nos | Item No.5 | 80000.00 | 94400.00 | 70240.00 | 82883.00 | 105664.00 | 124684.00 | 173792.00 | 205075.00 | 66704.00 | 78711.00 | 69072.00 | 81505.00 | 66704.00 | OZONE AIR CONDITIONING AND CONSULTANCY | 78711.00 | OZONE AIR CONDITIONING AND CONSULTANCY
6.00 | Supply, Installation, Testing and commissioning of PN 16 rating of 100 mm dia Non return valves duly insulated with 50 mm EPS insulation in of chilled water lines, complete with companion flanges, nuts, bolts, gaskets, adequate supports etc conforming to specifications provided. | 3.00 | Nos | Item No.6 | 18000.00 | 21240.00 | 16650.00 | 19647.00 | 34107.00 | 40246.00 | 17541.00 | 20698.00 | 17256.00 | 20362.00 | 18876.00 | 22274.00 | 16650.00 | VOLTAS LIMITED | 19647.00 | VOLTAS LIMITED
7.00 | Supply, Installation, Testing and commissioning of PN 16 rating of 100 mm dia Balancing valves, insulated with 50 mm EPS insulation of chilled water lines , complete with companion flanges, nuts, bolts, gaskets, adequate supports etc conforming to specifications provided. | 3.00 | Nos | Item No.7 | 45000.00 | 53100.00 | 35790.00 | 42232.00 | 68301.00 | 80595.00 | 37839.00 | 44650.00 | 42411.00 | 50045.00 | 47283.00 | 55794.00 | 35790.00 | VOLTAS LIMITED | 42232.00 | VOLTAS LIMITED
8.00 | Supply, Installation, Testing and commissioning of PN 16 rating of 100 mm dia CI Y-strainer in position duly insulated with EPS in chilled water lines with companion flanges, nuts, bolts, gaskets, adequate supports etc as per specification provided etc complete as req. | 3.00 | Nos | Item No.8 | 13500.00 | 15930.00 | 29340.00 | 34621.00 | 39504.00 | 46615.00 | 16200.00 | 19116.00 | 21057.00 | 24847.00 | 21294.00 | 25127.00 | 13500.00 | Pneumatic Engineers Pvt. Ltd. | 15930.00 | Pneumatic Engineers Pvt. Ltd.
9.00 | SITC of 65 mm dia of 3-way modulating control valve with actuator assembly, etc. at all AHUs. | 8.00 | Nos | Item No.9 | 560000.00 | 660800.00 | 266880.00 | 314918.00 | 401400.00 | 473652.00 | 237600.00 | 280368.00 | 278480.00 | 328606.00 | 282344.00 | 333166.00 | 237600.00 | YUDEK ENGINEERING P LTD | 280368.00 | YUDEK ENGINEERING P LTD
10.00 | Supply, Installation, Testing and commissioning of industrial type 100 mm dia dial type Thermometers conforming to technical spec. in the chilled water lines. | 22.00 | Nos | Item No.10 | 70400.00 | 83072.00 | 31900.00 | 37642.00 | 47058.00 | 55528.00 | 20460.00 | 24143.00 | 45188.00 | 53322.00 | 38302.00 | 45196.00 | 20460.00 | YUDEK ENGINEERING P LTD | 24143.00 | YUDEK ENGINEERING P LTD
11.00 | Supply, Installation, Testing and commissioning of 100 mm dia dial type pressure gauges with gate valves conforming to technical specifications provided in the chilled water lines etc complete as req. | 28.00 | Nos | Item No.11 | 33600.00 | 39648.00 | 43680.00 | 51542.00 | 70616.00 | 83327.00 | 35000.00 | 41300.00 | 61796.00 | 72919.00 | 64400.00 | 75992.00 | 33600.00 | Pneumatic Engineers Pvt. Ltd. | 39648.00 | Pneumatic Engineers Pvt. Ltd.
12.00 | Supply, Installation, Testing and commissioning of Water flow switch with all required connections as complete with companion flanges, nuts, bolts, gaskets, adequate supports etc per specification etc complete as req. | 3.00 | Nos | Item No.12 | 7500.00 | 8850.00 | 18450.00 | 21771.00 | 8052.00 | 9501.00 | 6300.00 | 7434.00 | 9711.00 | 11459.00 | 7644.00 | 9020.00 | 6300.00 | YUDEK ENGINEERING P LTD | 7434.00 | YUDEK ENGINEERING P LTD
13.00 | Painting of chilled water line Green colour water proof cement paint with arrows and condenser water lines Dark blue water proof cement paint with white arrows etc complete as required. | 40.00 | Meters | Item No.13 | 8000.00 | 9440.00 | 1200.00 | 1416.00 | 28360.00 | 33465.00 | 14000.00 | 16520.00 | 9480.00 | 11186.00 | 12560.00 | 14821.00 | 1200.00 | VOLTAS LIMITED | 1416.00 | VOLTAS LIMITED
14.00 | Supply, Installation, Testing & Commissioning of indoor AHU VFD starter Panel with star delta by pass, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, wall / floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with busbars extendable on both sides, including internal wiring with suitable size wires, rotary handle, spreader etc. The panel shall be as per the requirements and recommendations of AHU & VFD Manufacturer's standards with suitable capacity of cooling fan, suitable to connect fire alarm system and all type of dampers and as per CPRI specification or type tested Panel manufacturer as per IEC 61439-1&2 with all accessories etc. complete in all respects as required by the standard specifications. (a) INCOMER 1 No. 63A, FP, 25kA, MCCB with Thermal Magnetic release, Ics=Icu, having adjustable over load, short circuit protection.
14.10 | (b) BUSBARS 1 Set of 100 AmpTPN aluminium busbars © INSTRUMENTS 1 No Three phase Digital voltmeter, Acc. Class 1 1 No Three phase Digital ammeter, Acc. Class 1 1 Set of phase indicating lamps, LED type, RYB with 3 Nos. SP MCB control. 1 Set of 60/5A, Class 1.0, 10VA, Cast Resin CT for metering. (d) OUTGOING 2 No. 40A, TPN, 10kA, C Curve, MCB 2 Nos. 16A, SPN, 10kA, C curve MCB. 01 set - Power contactors, by-pass selction switch, timers etc as required for star delta starter 1 No of Normal duty VFD drive of suitable rating for 3 phase, 50Hz AHU motor. (approx 7.5kW/10 HP). Note:Motor kw is only indicative.Any difference in motor rating(higher/lower) shall be selected accordingly with prior approval from from Engineer-in-Charge without any cost implication. 220/24 volts transformer.Wiring for micro-switch smoke sensor and electric actuator for stopping the fan when smoke/fire damper closes (For AHUs provided with fire damper).Control wiring for thermostat.Auto / Manual start / stop selector switch shall beprovided for each equipment in the panel to facilitateremote operation from Central Indication Light Panel. Panels shall have adequate space for mountingtransformers and other accessories related to controlsystem. | 8.00 | Job | Item No.14 | 880000.00 | 1038400.00 | 671520.00 | 792394.00 | 772808.00 | 911913.00 | 664000.00 | 783520.00 | 1049584.00 | 1238509.00 | 818152.00 | 965419.00 | 664000.00 | YUDEK ENGINEERING P LTD | 783520.00 | YUDEK ENGINEERING P LTD
15.00 | Supplying and making End termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1 KV grade as required.
15.10 | 3.5 X 185sqmm | 6.00 | Set | Item No.15 | 6000.00 | 7080.00 | 16140.00 | 19045.00 | 5154.00 | 6082.00 | 18000.00 | 21240.00 | 11460.00 | 13523.00 | 6918.00 | 8163.00 | 5154.00 | ETA ENGINEERING PVT LTD | 6082.00 | ETA ENGINEERING PVT LTD
15.20 | 4 X 16 sqmm | 14.00 | Set | Item No.16 | 5600.00 | 6608.00 | 12600.00 | 14868.00 | 2464.00 | 2908.00 | 35000.00 | 41300.00 | 5376.00 | 6344.00 | 7350.00 | 8673.00 | 2464.00 | ETA ENGINEERING PVT LTD | 2908.00 | ETA ENGINEERING PVT LTD
16.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 10.00 | Meter | Item No.17 | 1500.00 | 1770.00 | 2600.00 | 3068.00 | 1430.00 | 1687.00 | 1950.00 | 2301.00 | 1240.00 | 1463.00 | 2070.00 | 2443.00 | 1240.00 | OZONE AIR CONDITIONING AND CONSULTANCY | 1463.00 | OZONE AIR CONDITIONING AND CONSULTANCY
17.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 30.00 | Meter | Item No.18 | 1500.00 | 1770.00 | 1500.00 | 1770.00 | 1890.00 | 2230.00 | 4500.00 | 5310.00 | 450.00 | 531.00 | 990.00 | 1168.00 | 450.00 | OZONE AIR CONDITIONING AND CONSULTANCY | 531.00 | OZONE AIR CONDITIONING AND CONSULTANCY
18.00 | Supply, installation, testing and commissioning of air curtains of length 1.0Mtr at corridor entry doors with all necessary supports with limit switch etc required . The impeller shall Aluminium construction with curve blades to minimise the air cutting noise below 66 dB. ( Make: Almonard Model:AHV-SMART/DELUX or equivalent approved make) | 2.00 | Each | Item No.19 | 32000.00 | 37760.00 | 48420.00 | 57136.00 | 46084.00 | 54379.00 | 48000.00 | 56640.00 | 51480.00 | 60746.00 | 59834.00 | 70604.00 | 32000.00 | Pneumatic Engineers Pvt. Ltd. | 37760.00 | Pneumatic Engineers Pvt. Ltd.
19.00 | Dismantling & shifting of existing 3 Nos x 100 TR chiller plant with soft starter 3 nos, chiller pumps, pipes upto head main header lines and supporting materails etc complete to the AAI store complete etc as required. | 1.00 | Job | Item No.20 | 60000.00 | 70800.00 | 170470.00 | 201155.00 | 269230.00 | 317691.00 | 127077.00 | 149951.00 | 69999.00 | 82599.00 | 149118.00 | 175959.00 | 60000.00 | Pneumatic Engineers Pvt. Ltd. | 70800.00 | Pneumatic Engineers Pvt. Ltd.
| Total in Figures |  |  |  | 8448600.00 | 9969348.00 | 8506550.00 | 10037729.00 | 9000556.00 | 10620656.00 | 8257799.00 | 9744203.00 | 9099999.00 | 10737998.00 | 10558475.00 | 12459001.00

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of 3X100 TR Chiller Plant, Chilled Water Pumps and Associated Works at RHQ-Admin Block, Chennai Airport Tender ID: 2020_AAI_62346_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | YUDEK ENGINEERING P LTD | 9744203.00 | L1
| 2 | Pneumatic Engineers Pvt. Ltd. | 9969348.00 | L2
| 3 | VOLTAS LIMITED | 10037729.00 | L3
| 4 | ETA ENGINEERING PVT LTD | 10620656.00 | L4
| 5 | OZONE AIR CONDITIONING AND CONSULTANCY | 10737998.00 | L5
| 6 | VK BUILDING SERVICES PVT.LTD. | 12459001.00 | L6