## BoQ1
Government eProcurement System Created By: RISHI RAJ BAGRE Created Date/Time: 01-Jan-2021 11:25 AM Tender Title: Replacement of 01 No. Cooling Tower at DABH Airport, Indore. Tender ID: 2020_AAI_62544_1
Tender Inviting Authority: <AGM (Engg.-E)-II, AAI, DABH Airport, Indore.>
Name of Work: <Replacement of 01 no. Cooling Tower at D.A.B.H Airport, Indore>
Contract No: <AAI/ID/Engg.(E)/ENIT-8/2020-21>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Extreme Comfort Engineers Pvt Ltd(GSTN-23AACCE9112C1Z9) |  | ADVANCE COOLING TOWERS PRIVATE(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.01 | SITC of FRP Induced draft Cooling Towers (CTI certified) complete with FRP basin, casing, distribution system, fills, louvers, ladder, fan, motor, supports for fan & motor, brass strainers, , control cabling / wiring, all accessories as per specifications and any other item required to make the system complete. Water Inlet / Outlet Temp: 99 / 89 Deg. F Design ambient wet bulb temperature: 82 Deg. F Water Flow Rate: 1050 USGPM Type: INDUCED DRAUGHT COUNTER FLOW Tower Structure: Casing : FRP,Basin : FRP LOUVERS : FRP Fan motor : Energy efficient (IE3) FAN ENCLOSER : IP 55 Power Supply : 415V, 3 Phase, 50 Hz Fill support/Bird screen/distribution support :Hot dipped Galvanized frame Drift eliminators : PVC Hardware : Stainless Steel Ladder: HDG STEEL | 1.00 | Job | 100.00 | 635000.00 | 635000.00 | 485000.00 | 485000.00 | 485000.00 | ADVANCE COOLING TOWERS PRIVATE
1.02 | Dismantling of existing Cooling Towers and shifting of dismantled cooling towers items to electrical store at NITB, DABH Airport, Indore. | 1.00 | Job | 100.00 | 30000.00 | 30000.00 | 30000.00 | 30000.00 | 30000.00 | ADVANCE COOLING TOWERS PRIVATE, Extreme Comfort Engineers Pvt Ltd
1.03 | Supply of Following Sizes, Manual Gear Operated Heavy Duty Butterfly Valve, Body - Cast Iron - IS 210, FG 220, PN -16, Type - Wafer Type, Disc - S.G. Iron, Shaft - AISI 410, Body Liner - Integrally moulded nitrile, with epoxy powder coated, compatible with the existing HVAC system, complete as required. (a) 250 mm Dia, for Cooling Tower Tank Outlets | 3.00 | Each | 10.00 | 20500.00 | 61500.00 | 8500.00 | 25500.00 | 25500.00 | ADVANCE COOLING TOWERS PRIVATE
1.04 | Supply of Following Sizes, Manual Gear Operated Heavy Duty Butterfly Valve, Body - Cast Iron - IS 210, FG 220, PN -16, Type - Wafer Type, Disc - S.G. Iron, Shaft - AISI 410, Body Liner - Integrally moulded nitrile, with epoxy powder coated, compatible with the existing HVAC system, complete as required. (b) 350 mm Dia, for Condensor Pot Strainer | 2.00 | Each | 10.00 | 31500.00 | 63000.00 | 18045.00 | 36090.00 | 36090.00 | ADVANCE COOLING TOWERS PRIVATE
1.05 | Supply of 250mm Dia, Motorised Heavy Duty Butterfly Valve of Cooling Towers Spray Line, Body - Cast Iron - IS 210, FG 220, PN -16, Type - Wafer Type, Disc - C.F 8 / SS 304, Shaft - AISI 410, Body Liner - Integrally moulded nitrile, with epoxy powder coated, BMS Compatible with intelligent Control, Quarter Turn Actuators complete as required. | 3.00 | Each | 10.00 | 55000.00 | 165000.00 | 31280.00 | 93840.00 | 93840.00 | ADVANCE COOLING TOWERS PRIVATE
1.06 | Installation,Testing and Commissioning of new Butterfly Valves i/c Dismantling of existing defective/malfunctioning Butterfly valves of cooling tower outlets and Condenser pot stariner and shifting of dismantled items to electrical store at NITB, DABH Airport, Indore. | 8.00 | Job | 10.00 | 5000.00 | 40000.00 | 10500.00 | 84000.00 | 40000.00 | Extreme Comfort Engineers Pvt Ltd
| Total in Figures |  |  |  |  | 994500.00 |  | 754430.00
Lowest Amount Quoted BY: ADVANCE COOLING TOWERS PRIVATE(754430.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of 01 No. Cooling Tower at DABH Airport, Indore. Tender ID: 2020_AAI_62544_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ADVANCE COOLING TOWERS PRIVATE | 754430.00 | L1
| 2 | Extreme Comfort Engineers Pvt Ltd | 994500.00 | L2