## BoQ1
Government eProcurement System Created By: Siddhartha Sankar Majumder Created Date/Time: 08-Jan-2021 02:00 PM Tender Title: Construction of New Integrated Terminal Building and Associated works at Agartala Airport, Agartala, Tripura. SH Miscellaneous Electrical Works Tender ID: 2020_AAI_62548_1
Tender Inviting Authority: Asst. General Manager (Engg-Elect)-Project, M.B.B. Airport, Agartala, Tripura- 799009
Name of Work: Construction of New Integrated Terminal Building and Associated works at Agartala Airport, Agartala, Tripura. SITC of Tyre Killers, Bollards, Boom Barriers and Sliding Gates etc.
Contract No: AAI/AGT/Engg(E-E)/Security/2020-21
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOLKS ENERGIE PVT LTD(GSTN-07AADCV9396C1ZZ) |  | COOL TECH ENGINEERS(GSTN-08AAFFC7397B1ZD) |  | BOSE ENGINEERING AND MARKETING COMPANY(GSTN-19AHMPB0264G1ZJ)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply Installation Testing & Commissioning of 11 Tr. Floor Mounted, Bottom discharge, Air Cooled DX type CRAC units for Server room application, equipped with most advanced & industry technology, guaranteeing precise control of server room. Suitable for 415 Volts, 50 Hz, 3 Phase Power Supply. The units shall be selected on the basis of following parameters: i) 39 kW of minimum Gross Sensible Cooling Capacity @ 10300 CMH. ii) 24 Deg C/50% RH of return air. iii) Supply air in between 12-16 Deg C. iv) 40 Deg C of Design Ambient temperature the Indoor unit shall comprise of Variable capacity Digital Scroll Compressor, Fiberglass corrosion resistant EC fans, Evaporator DX Cooling Coil with hydrophilic coating, Microprocessor controllers, Refrigerant shall be enviromental friendly refrigerant R410A,Thermostatic/electronic Expansion valves, Driers, EU4 Filter, Suction and Discharge piping, Internal power and Control wiring, Crankcaseheaters, Infrared Humidifier,stainless steel drain pan,Liquid Receiver,Pressure relief saftey valve,Liquid line solenoid valve,Vibration Isolator ,Heaters, HP/LP Cut outs, Power and Control contactors,Clogged filter alarm & water leak detectors and Other Electrical accessories The Outdoor Condenser unit shall comprises of air cooled Condenser with variable speed fans, outdoor unit motor should have IP-54 protection, Condenser cooling coil (Copper coil with aluminum fins), Fan speed controller, Isolator switch,Auto sequencing of the unit for equal run time should be integral part of the micro-processor,each unit shall have inbuilt software to facilate BMS connectivity through RS485 Modbus Protocol including earthing,MS stand for Indoor & Outdoor units and minor civil work etc. Complete as per OEMs specifications. | 2.00 | Each |  | 835000.00 | 1670000.00 | 800000.00 | 1600000.00 | 925000.00 | 1850000.00 | 1600000.00 | COOL TECH ENGINEERS
2.00 | Supply,installation,testing and commissioning of one pair of insulated Hard Drawn Copper Pipe Refrigerant piping (liquid & suction) duly complete with all fittings and finished with two coated of enamel paint of approved colour code. Refrigerant piping shall be insulated with 19mm thick closed cell elastomeric nitrile rubber insulation in tubing form including refrigerant as per site requirement etc. Complete as required. | 50.00 | Mtr. |  | 1600.00 | 80000.00 | 1600.00 | 80000.00 | 2100.00 | 105000.00 | 80000.00 | VOLKS ENERGIE PVT LTD, COOL TECH ENGINEERS
3.00 | Supply & Installation of suitable size of GI Ladder Tray for Copper Pipe & Condenser Power Cables etc.Complete as required. | 50.00 | Mtr. |  | 290.00 | 14500.00 | 400.00 | 20000.00 | 500.00 | 25000.00 | 14500.00 | VOLKS ENERGIE PVT LTD
4.00 | Supply & Installation of GI Tray Cover of width Cable Tray (for Exposed Horizontal running at floor level) etc. Complete as required. | 20.00 | Mtr. |  | 280.00 | 5600.00 | 400.00 | 8000.00 | 500.00 | 10000.00 | 5600.00 | VOLKS ENERGIE PVT LTD
5.00 | Supply & Installation suitable size of GI Piping along with all fittings for Humidifier Inlet with 9mm thick nitrile rubber indulation for PACs etc. Complete as required. | 50.00 | Mtr. |  | 190.00 | 9500.00 | 400.00 | 20000.00 | 700.00 | 35000.00 | 9500.00 | VOLKS ENERGIE PVT LTD
6.00 | Supply & Installation of suitable size of GI condensate drain pipe with 9mm thick nitrile rubber indulation for PACs etc. Complete as required. | 50.00 | Mtr. |  | 150.00 | 7500.00 | 350.00 | 17500.00 | 700.00 | 35000.00 | 7500.00 | VOLKS ENERGIE PVT LTD
7.00 | Supply & Installation of Extended Piping Kit (including additional Oil) as per site etc. Complete as required. | 2.00 | Each |  | 13000.00 | 26000.00 | 5000.00 | 10000.00 | 9000.00 | 18000.00 | 10000.00 | COOL TECH ENGINEERS
8.00 | Supply, installation, testing & commissioning of extruded Aluminium Powder coated supply air floor grills of Heavy gauge high quality extruded Aluminium profile with aluminium blade, VCD's, suitable for mounting in false floor of size 600 x 600mm etc. inluding minor civil work etc. Complete as required. | 8.00 | Each |  | 3500.00 | 28000.00 | 7500.00 | 60000.00 | 9000.00 | 72000.00 | 28000.00 | VOLKS ENERGIE PVT LTD
9.00 | Supply, installation, testing & commissioning of 16mm thick Closed Cell Nitrile Rubber Insulation for Server room floor including minor civil work etc. Complete as required. | 40.00 | SQM |  | 480.00 | 19200.00 | 500.00 | 20000.00 | 500.00 | 20000.00 | 19200.00 | VOLKS ENERGIE PVT LTD
10.00 | Supply & drawing of 4 C X 2.5 sqmm ,1.1Kv grade FRLS multicore copper conductor PVC insulated unarmourd cable in the surface/recess in medium class PVC conduit for indoor and outdoor unit connection etc.complet as required. | 200.00 | Mtr. |  | 140.00 | 28000.00 | 125.00 | 25000.00 | 100.00 | 20000.00 | 20000.00 | BOSE ENGINEERING AND MARKETING COMPANY
11.00 | Supply of 4 Core X 25 sqmm, 1.1kv grade FRLS multicore copper conductor XLPE insulated and PVC sheathed armoured cable as per IS : 7098:1988 with upto date amendments. | 100.00 | Mtr. |  | 800.00 | 80000.00 | 750.00 | 75000.00 | 160.00 | 16000.00 | 16000.00 | BOSE ENGINEERING AND MARKETING COMPANY
12.00 | Supply and making end termination with Flame proof double brass compression gland and Copper thimbles for XLPE insulated and PVC sheathed copper conductor cable of 1.1kv grade of the 4 Core X 25 sqmm size as required. | 6.00 | Set |  | 900.00 | 5400.00 | 3000.00 | 18000.00 | 1400.00 | 8400.00 | 5400.00 | VOLKS ENERGIE PVT LTD
13.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of upto 35sqmm(clamped with 1mm thick saddle) on cable tray/Pipe/Raceway/Surfcace etc. complete as required. | 80.00 | Mtr. |  | 70.00 | 5600.00 | 200.00 | 16000.00 | 100.00 | 8000.00 | 5600.00 | VOLKS ENERGIE PVT LTD
14.00 | Supply, Installation, Testing & Commissioning of cubicle type panel made out of 2mm thick CRCA sheet, totally enclosed, IP 42, modular type,floor mounted with channel base frame, dust and vermin proof, indoor, compartmentalized, modular type suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with extendable busbars on both sides including control wiring with 2.5 sq mm size FRLS wires/cable, interconnection, duly powder coated painting etc. including supply & installation of following switchgears, metering instruments and accessories including panel earthing and minor civil work. Note:All MCCB's shall be provided with extended rotary handle .MCCB above 63A shall be provided with copper spreader terminal. INCOMER: 01 No. 125 Amp four pole Moulded Case Circuit Breaker (35 KA) with built in microprocessor based release unit with adjustable setting with RS 485 Port. BUSBARS: 200 Amp TPN busbars of high conductivity electrolytic quality aluminium alloy INSTRUMENTS: 01 No. digital multifunction meter ( KVA,KVAR, Kwh,THD, PF) with RS 485 Port including suitable rating CTs for 3 phase, 4 wire operation. 01 Sets of RYB phase indicating lamps controlled by 2 amp MCB OUTGOING: 2 Nos. 63 Amp 4P Moulded Case circuit breaker. | 1.00 | Set |  | 96000.00 | 96000.00 | 30000.00 | 30000.00 | 205000.00 | 205000.00 | 30000.00 | COOL TECH ENGINEERS
15.00 | Supply, Installation, Testing & Commissioning of cubicle type panel made out of 2mm thick CRCA sheet, totally enclosed, IP 42, modular type,floor mounted with channel base frame, dust and vermin proof, indoor, compartmentalized, modular type suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with extendable busbars on both sides including control wiring with 2.5 sq mm size FRLS wires/cable, interconnection, duly powder coated painting etc. including supply & installation of following switchgears, metering instruments and accessories including panel earthing and minor civil work. Note:All MCCB's shall be provided with extended rotary handle .MCCB above 63A shall be provided with copper spreader terminal. INCOMER: 250 Amp four pole Moulded Case Circuit Breaker (35 KA) with built in microprocessor based release unit with adjustable setting with RS 485 Port. (Icu=100% Ics)- 2 Sets BUSBARS: 400 Amp TPN busbars of high conductivity electrolytic quality aluminium alloy BUS COUPLER No. 250 Amp four pole Moulded Case Circuit Breaker (35 KA) with built in microprocessor based release unit with adjustable setting with RS 485 Port. (Icu=100% Ics)- 1 Set INSTRUMENTS: 01 No. digital multifunction meter ( KVA,KVAR, Kwh,THD, PF) with RS 485 Port including suitable rating CTs for 3 phase, 4 wire operation. 01 Sets of RYB phase indicating lamps controlled by 2 amp MCB OUTGOING: 125 Amp 4P Moulded Case circuit breaker (35 KA) with built in microprocessor based release. (Icu=100% Ics)- 2 Sets | 1.00 | Set |  | 196000.00 | 196000.00 | 35000.00 | 35000.00 | 380000.00 | 380000.00 | 35000.00 | COOL TECH ENGINEERS
16.00 | Supply & Installation of suitable size of electrical cable for Condenser Fan Power Input from main panel of PAC etc Complete as required. | 50.00 | Mtr. |  | 380.00 | 19000.00 | 160.00 | 8000.00 | 200.00 | 10000.00 | 8000.00 | COOL TECH ENGINEERS
17.00 | Supply of split Air conditioner with control box of indoor unit shall be flame retardant , cordless remote & of cooling capacity 6000 K Cal/hr (2 Ton) fitted with rotary /scroll /semi-hermetic compressor operating on refrigerant R -22 /Non CFC suitable for high wall mounting & suitable for operation on 230V, 50Hz, single phase AC supply capable of performing following functions; (i) Cooling (ii) Dehumidifying, (iii) Air Circulating, & (iv) Filtering. (Minimum inverter three star rating or more star rating). | 25.00 | Job |  | 36000.00 | 900000.00 | 40000.00 | 1000000.00 | 48000.00 | 1200000.00 | 900000.00 | VOLKS ENERGIE PVT LTD
18.00 | Supply of split Air conditioner with control box of indoor unit shall be flame retardant , cordless remote & of cooling capacity 4500 K Cal/hr (1.5 Ton) fitted with rotary /scroll /semi-hermetic compressor operating on refrigerant R -22 /Non CFC suitable for high wall mounting & suitable for operation on 230V, 50Hz, single phase AC supply capable of performing following functions; (i) Cooling (ii) Dehumidifying, (iii) Air Circulating, & (iv) Filtering. (Minimum inverter three star rating or more star rating). | 16.00 | Job |  | 31000.00 | 496000.00 | 32000.00 | 512000.00 | 40000.00 | 640000.00 | 496000.00 | VOLKS ENERGIE PVT LTD
19.00 | ITC of 1.5 Ton/2.0 Ton split Air conditioner with cordless remote including minor civil work at site for AC unit installation including making hole for pipe installation and making the surface good with white cement with drain pipe connection including suitable power cable ,top for power supply connection upto nearest power point i/c all minor civil work for fixing etc. complete as required. | 41.00 | Job |  | 1800.00 | 73800.00 | 1000.00 | 41000.00 | 2500.00 | 102500.00 | 41000.00 | COOL TECH ENGINEERS
20.00 | Supply & fixing of refrigerant copper pipe line with insulation along with control cabling suitable for above said split air conditioners upto 2.0TR from indoor unit to outdoor unit beyond 4.0 meters length etc. complete as required | 100.00 | Mtr. |  | 550.00 | 55000.00 | 750.00 | 75000.00 | 700.00 | 70000.00 | 55000.00 | VOLKS ENERGIE PVT LTD
21.00 | Supply and fixing of 25 mm dia PVC drain pipe along with accessories from each indoor unit as per the site conditions /requirements. | 150.00 | Mtr. |  | 90.00 | 13500.00 | 150.00 | 22500.00 | 200.00 | 30000.00 | 13500.00 | VOLKS ENERGIE PVT LTD
22.00 | Supply & Fixing of readymade wall mounted/Floor mounted MS stand suitable for installation of outdoor unit of above mentioned 1.5TR/2.0TR split Air-conditioners including painting etc. complete as required. | 41.00 | Each |  | 500.00 | 20500.00 | 750.00 | 30750.00 | 2500.00 | 102500.00 | 20500.00 | VOLKS ENERGIE PVT LTD
23.00 | Supply & Fixing of 6 feet width,high velocity stainless steel ( SS 304 grade) body air curtain suitable to work on Three / single phase 415/230 volts +/- 5% , 50 Hz AC supply including power cable, top and hanging arrangment at entry/exit gate of building with all accessories i/c all minor civil worketc. complete as required. | 15.00 | Each |  | 20000.00 | 300000.00 | 40000.00 | 600000.00 | 44000.00 | 660000.00 | 300000.00 | VOLKS ENERGIE PVT LTD
24.00 | Supply & Fixing of 4 feet width,high velocity stainless steel (SS 304 grade) body air curtain suitable to work on Three / single phase 415/230 volts +/- 5% , 50 Hz AC supply including power cable, top and hanging arrangment at entry/exit gate of building with accessories i/c all minor civil work etc. complete as required. | 20.00 | Each |  | 17000.00 | 340000.00 | 35000.00 | 700000.00 | 30000.00 | 600000.00 | 340000.00 | VOLKS ENERGIE PVT LTD
25.00 | 25 Supply & Fixing of stainless steel (SS 304 grade) heavy duty hand dryer suitable to work on Three / single phase 415/230 volts +/- 5% , 50 Hz AC supply including power cable, top and hanging arrangment with all accessories i/c all minor civil work etc. complete as required. 38.000 Each 1.00 38.00 INR Thirty Eight Only . | 38.00 | Each |  | 16500.00 | 627000.00 | 13000.00 | 494000.00 | 13000.00 | 494000.00 | 494000.00 | COOL TECH ENGINEERS, BOSE ENGINEERING AND MARKETING COMPANY
26.00 | Supply, Installation, Testing & Commissioning of Desktop intel core i7- 8th Gen or above having procesor of minimum 8 GB RAM, storage of minimum 1TB HDD, Integrated Graphics or better , monitor size of minimum 21.5" with 1920 X 1080 pixel resolution, Windows 10 pro licenced, with keyboard , mouse & availability of HDMI, VGA, USB port, other accessories as required. (OEM onsite Warranty 3Years or above). Approved makes are Dell, HP, Lenovo. | 2.00 | Set |  | 70000.00 | 140000.00 | 100000.00 | 200000.00 | 125000.00 | 250000.00 | 140000.00 | VOLKS ENERGIE PVT LTD
27.00 | Supply, Installation, Testing & Commissioning of Laptop intel core i7- 8th Gen or above having procesor of minimum 8 GB RAM, storage of minimum 512 GB SSD, Integrated Graphics or better , monitor size of minimum 14" with 1920 X 1080 pixel resolution, Windows 10 pro licenced, with keyboard , mouse & availability of HDMI, VGA, USB port, other accessories as required. (OEM onsite Warranty 3Years or above). Approved makes are Dell, HP, Lenovo. | 1.00 | set |  | 82000.00 | 82000.00 | 135000.00 | 135000.00 | 85000.00 | 85000.00 | 82000.00 | VOLKS ENERGIE PVT LTD
28.00 | Supply, Installation, Testing & Commissioning of 55" or above, 3840 X 2160 (UHD), Smart type LCD Display with Inbuilt Speaker, HDMI, USB port and wall mounting arrangement complete as required. (Minimum 3 Years or above onsite warranty). Approved makes are LG, Sony, Samsung. | 1.00 | Set |  | 58000.00 | 58000.00 | 75000.00 | 75000.00 | 170000.00 | 170000.00 | 58000.00 | VOLKS ENERGIE PVT LTD
29.00 | All Inclusive Comprehensive Maintenance Contract after completion of One years Defect Liability Period for the above 02 nos ,11 TR Precision Air Conditioning unit including periodical, preventive, break down maintenanceas per the OEM recommendations &AAI requirements and attending emergency breakdowns as and when required on 24 hrs basis (on all days including holidays) and including all necessary spares and consumables to keep the whole PAC system in perfect working condition etc. complete as required.
29.10 | a) For 2nd Year (after One year DLP) | 12.00 | Months |  | 6250.00 | 75000.00 | 5000.00 | 60000.00 | 6000.00 | 72000.00 | 60000.00 | COOL TECH ENGINEERS
29.20 | b) For 3rd Year (after One year DLP + after 2nd Year) | 12.00 | Months |  | 7917.00 | 95004.00 | 6000.00 | 72000.00 | 6500.00 | 78000.00 | 72000.00 | COOL TECH ENGINEERS
29.30 | c) For 4th Year (after One year DLP + after 2nd & 3rd Year) | 12.00 | Months |  | 9167.00 | 110004.00 | 7000.00 | 84000.00 | 7200.00 | 86400.00 | 84000.00 | COOL TECH ENGINEERS
29.40 | d) For 5th Year (after One year DLP + after 2nd & 3rd Year& 4th Year) | 12.00 | Months |  | 10000.00 | 120000.00 | 8000.00 | 96000.00 | 7800.00 | 93600.00 | 93600.00 | BOSE ENGINEERING AND MARKETING COMPANY
| Total in Figures |  |  |  |  | 5796108.00 |  | 6239750.00 |  | 7551400.00
Lowest Amount Quoted BY: VOLKS ENERGIE PVT LTD(5796108.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New Integrated Terminal Building and Associated works at Agartala Airport, Agartala, Tripura. SH Miscellaneous Electrical Works Tender ID: 2020_AAI_62548_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | VOLKS ENERGIE PVT LTD | 5796108.00 | L1
| 2 | COOL TECH ENGINEERS | 6239750.00 | L2
| 3 | BOSE ENGINEERING AND MARKETING COMPANY | 7551400.00 | L3