## BoQ1
Government eProcurement System Created By: SYED TANWEER ASHRAF Created Date/Time: 04-Jan-2021 03:47 PM Tender Title: Provision of D.G. Synchronising cum PCC Panel with AMF and Load Sharing Facility at Gaya Airport, Gaya Tender ID: 2020_AAI_62944_1
Tender Inviting Authority: AGM ( Engg. Elect), AAI, Gaya Airport, Gaya
Name of Work: <Provision of D.G Synchronising cum PCC Panel with AMF & Load Sharing Facility at Gaya Airport, Gaya >
Contract No: <0631-2210043>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | KR POWER INFRA INDIA PRIVATE LIMITED(GSTN-36AADCK6420C1ZY) |  | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION(GSTN-09AOTPS2578C1ZC) |  | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ) |  | RISHA CONTROL ENGINEERS PRIVATE LIMITED(GSTN-NA) |  | Gemtech Power Control Private Limited(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, manufacture Supply, Installation, Testing and Commissioning of D.G Synchronising cum PCC Panel with AMF, load sharing & power distribution facilities, cubicle type, made of 2 mm thick sheet steel, totally enclosed, IP 4X, free standing, floor mounting, dust and vermin proof ,indoor, compartmentalised, powder coated painting suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC supply from D.G Sets (individual or in sync. & parallel load sharing mode as per load requirements) & Mains power with Al. busbars extensible on both sides, interconnections including supply & installation of following items/components (but not limited to) and as per Technical specification & site requirement complete as required: | 1.00 | Job | 263.00 | 5025000.00 | 5025000.00 | 4200000.00 | 4200000.00 | 4506900.00 | 4506900.00 | 4170000.00 | 4170000.00 | 4230000.00 | 4230000.00 | 4170000.00 | RISHA CONTROL ENGINEERS PRIVATE LIMITED
1.00 | MAINS SUPPLY INCOMER
1.00 | 2000A FP EDO ACB (50kA) with built-in Microprocessor Based Release for (O/C, S/C, E/F Protection) and with RS485 communication port facility, closing coil ,Under Voltage Release - 2 No.
1.00 | Shunt release -2 No.
1.00 | Breaker Control Switch with (T-N-C) -2 No.
1.00 | Auto/Manual Selector Switch -2 No.
1.01 | Auxiliary Contactor 2NO+2NC - 6 No.
1.01 | Intelligent multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with communication facility (RS485 port), THD and Individual order harmonics upto 31st Order, Cl.-1.0, 96x96sq.mm., Flush Mounted - 2 No.
1.01 | CTs 2000/5A, Class-1.0, 15VA for Metering - 6 No.
1.01 | Single Phase Preventer - 2 No.
1.01 | Phase Reversal Relay (Phase Sequence Relay) - 2 No.
1.01 | 3 Phase, 4 Wire Under & Over Voltage Relay (Auto / Manual Reset, Trip Time & Power ON Delay 1-10 Sec.) OV/UV - Adjustable - 2 No.
1.01 | Indicating lamps - R/Y/B/ON/OFF/TRIP/Spring Charged - 14 No.
1.01 | 2A SP Control MCB (10kA), C-Curve -16 No.
1.01 | SPD - Class B - 2 No.
1.01 | 63A TP MPCB -2 No.
1.02 | DG INCOMER -1 & 2
1.02 | 800A TP EDO ACB (50kA) with built-in Microprocessor Based Release for (O/C, S/C, E/F Protection) with RS485 communication port facility, closing coil, Under Voltage Release - 2 No.
1.02 | 400 A Neutral isolation contactor -2 No
1.02 | Shunt release -2 No.
1.02 | Breaker Control Switch with (T-N-C) -2 No.
1.02 | Auto/Manual Selector Switch -2 No.
1.02 | Auxiliary Contactor 2NO+2NC - 4 No.
1.02 | Intelligent multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with communication facility (RS485 port), THD and Individual order harmonics upto 31st Order, Cl.-1.0, 96x96sq.mm., Flush Mounted - 2 No.
1.02 | Digital energy meter with RS-485 comm. Port CL1.0 -2 No.
1.02 | CTs 800/5A, Class-1.0, 15VA for Metering (Resin Cast) -6 No.
1.03 | CTs 800/5A, Class-PS, 15VA for Metering (Resin Cast) -8 No.
1.03 | Single Phase Preventer - 2 No.
1.03 | Phase Reversal Relay (Phase Sequence Relay) - 2 No.
1.03 | 3 Phase, 4 Wire Under & Over Voltage Relay (Auto / Manual Reset, Trip Time & Power ON Delay 1-10 Sec.) OV/UV - Adjustable - 2 No.
1.03 | Restricted Earth Fault Relay -2 No.
1.03 | Indicating lamps - R/Y/B/ON/OFF/TRIP/Spring Charged - 14 No.
1.03 | 2A SP Control MCB (10kA), C-Curve -16 No.
1.03 | SPD - Class B - 2 No.
1.03 | 63A TP MPCB -2 No.
1.03 | DG INCOMER -3
1.04 | 630A TP EDO ACB (50kA) with built-in Microprocessor Based Release for (O/C, S/C, E/F Protection) (and with RS485 communication port facility, closing coil, Under Voltage Release -1 No.
1.04 | 400 A Neutral isolation contactor -1 No
1.04 | Shunt release -1 No.
1.04 | Breaker Control Switch with (T-N-C) -1 No.
1.04 | Auto/Manual Selector Switch -1 No.
1.04 | Auxiliary Contactor 2NO+2NC -2 No.
1.04 | Intelligent multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with communication facility (RS485 port), THD and Individual order harmonics upto 31st Order, Cl.-1.0, 96x96sq.mm., Flush Mounted - 1 No.
1.04 | Digital energy meter with RS-485 comm. Port CL1.0 -1 No.
1.04 | CTs 600/5A, Class-1.0, 15VA for Metering (Resin Cast) - 3 No.
1.04 | CTs 600/5A, Class-PS, 15VA for Metering (Resin Cast) - 4 No.
1.05 | Single Phase Preventer - 1 No.
1.05 | Phase Reversal Relay (Phase Sequence Relay) - 1 No.
1.05 | 3 Phase, 4 Wire Under & Over Voltage Relay (Auto / Manual Reset, Trip Time & Power ON Delay 1-10 Sec.) OV/UV - Adjustable - 1 No.
1.05 | Restricted Earth Fault Relay -1 No.
1.05 | Indicating lamps - R/Y/B/ON/OFF/TRIP/Spring Charged - 7 No.
1.05 | 2A SP Control MCB (10kA), C-Curve -8 No.
1.05 | SPD - Class B- 1 No.
1.05 | 63A TP MPCB -1 No.
1.05 | BUS COUPLER
1.06 | 2000A FP EDO ACB (50kA) WITHOUT PROTECTION RELEASE, with Under Voltage Release - 1 No.
1.06 | Breaker Control Switch with (T-N-C) - 1 No.
1.06 | Auto/Manual Selector Switch - 1 No.
1.06 | Auxiliary Contactor 2NO+2NC - 2 No.
1.06 | Indicating lamps - ON/OFF/TRIP - 3 No.
1.06 | 2A SP Control MCB (10kA), C-Curve - 7 No.
1.06 | BUS BAR
1.06 | Common bus , main outgoing Bus bars of 2000 Amps, TPN, Aluminium Bus bars
1.06 | INTERLOCKING
1.06 | Micro PLC Interlocking among incomers from D.G.Sets (3 Nos), Mains power (2 No.) and 1no. Bus Coupler - 1 Set as required
1.07 | OUTGOINGS
1.07 | 1000A FP EDO ACB (50kA) with built-in Microprocessor Based Release for (O/C, S/C, E/F Protection) and with RS485 communication port facility - 4 No.
1.07 | Shunt release-4 No
1.07 | Breaker Control Switch with (T-N-C) - 4 No.
1.07 | Auto/Manual Selector Switch - 4 No.
1.07 | Auxiliary Contactor 2NO+2NC - 8 No.
1.07 | Digital Ammeter with in-built slector switch CL1.0 - 4 No.
1.07 | CTs 1000/5A, Class-1.0, 15VA for Metering (Resin Cast) - 12 No.
1.07 | Indicating lamps - ON/OFF/TRIP - 12 No.
1.07 | 2A SP Control MCB (10kA), C-Curve - 28 No.
1.08 | 800A FP EDO ACB (50kA) with built-in Microprocessor Based Release for (O/C, S/C, E/F Protection) with RS485 communication port facility) - 2 No.
1.08 | Shunt release - 2 No.
1.08 | Breaker Control Switch with (T-N-C) - 2 No.
1.08 | Auto/Manual Selector Switch - 2 No.
1.08 | Auxiliary Contactor 2NO+2NC - 4 No.
1.08 | Digital Ammeter with in-built slector switch CL1.0 - 2 No.
1.08 | CTs 800/5A, Class-1.0, 15VA for Metering (Resin Cast) - 6 No.
1.08 | Indicating lamps - ON/OFF/TRIP - 6 No.
1.08 | 2A SP Control MCB (10kA), C-Curve - 14 No.
1.08 | AUTO-SYNCHRONISING FOR 3 NOS. OF DG SETS:-
1.09 | Genset Controller - 3 Set (suitable for CATTER PILLAR/TIL DG sets at site.)
1.09 | MICROPLC FOR LOAD MANAGEMENT - 3 Set
1.09 | DG Set Selector Switch - 1 No.
1.09 | Communiation cabling for CAN protocol - as required
1.09 | Instrumentation cabling - as required
1.09 | Voltage monitoring devices
1.09 | Manual/PLC/ Selector Switch - 1 No.
1.09 | 12-Window Annunciator - 3 No.
1.09 | Mimic diagram-1 Set
1.09 | Engine Cranking relay - 6 No.
1.10 | Battery Charger with Ammeter & Voltmeter - 3 Set
1.10 | Power Supply 24V DC - 3 No.
1.10 | UPS 1KVA - 1 No.
1.10 | Aux. Relays - 1 Set
1.10 | Indicating lamps - 1 Set
1.10 | Push Button - 1 Set
1.10 | Hooter - 3 No.
1.10 | Control MCB - 1 Set
1.10 | Any other components, circuitary etc required for proper design,control & operation of the panel as per technical specification & site requirements. Any provisions required to be made during ITC of this panel due to dismantling of the existing AMF panels to ensure uninterrupted power supply shall be made as per site requirements
1.10 | The complete panel shall be of TTA TYPE & comply to IEC : 61439 & shall be complete in all respect for sync. operation, load sharing, load management, AMF operation & contrtol of 2 X 500 KVA + 1X 320 KVA TIL /CATERPILLAR make D.G Sets & power distribution provisions as per technical specification & site requirements etc as required.
2.00 | Supplying of following size of 1.1 KV grade XLPE insulated PVC sheathed armoured power cable of aluminium conductor confirming to IS: 7098 Part - I-1988 with latest amendments etc. as required.
2.10 | 3.5 Core X 400 Sq. mm Cable | 100.00 | Mtr. | 263.00 | 1800.00 | 180000.00 | 1500.00 | 150000.00 | 1181.00 | 118100.00 | 1460.00 | 146000.00 | 1176.00 | 117600.00 | 117600.00 | Gemtech Power Control Private Limited
2.20 | 3.5 Core X 240 Sq. mm Cable | 100.00 | Mtr. | 351.00 | 1200.00 | 120000.00 | 1200.00 | 120000.00 | 760.00 | 76000.00 | 960.00 | 96000.00 | 779.00 | 77900.00 | 76000.00 | Mona Generator Services Pvt. Ltd.
3.00 | Supplying and Making end terminations with brass compression gland and aluminium lugs for following size of PVC insulated and PVC SHEATHED/XLPE aluminium conductor cable of 1.1 KV grade as required.
3.10 | 3.5 Core X 400 Sq. mm Cable | 8.00 | Each | 263.00 | 1500.00 | 12000.00 | 4800.00 | 38400.00 | 1000.00 | 8000.00 | 2500.00 | 20000.00 | 4500.00 | 36000.00 | 8000.00 | Mona Generator Services Pvt. Ltd.
3.20 | 3.5 Core X 240 Sq. mm Cable | 10.00 | Each | 351.00 | 1200.00 | 12000.00 | 4400.00 | 44000.00 | 800.00 | 8000.00 | 2000.00 | 20000.00 | 4000.00 | 40000.00 | 8000.00 | Mona Generator Services Pvt. Ltd.
4.00 | Dismantling of existing AMF Panels of 2 No. of 550 KVA D.G Sets & 1 No. of 320 KVA D.G. Set of CATTERPILLAR / TIL make & shifting the panels at designated place/store safely & securely without any short of damage to the AMF panels. | 1.00 | Job | 352.00 | 35000.00 | 35000.00 | 50000.00 | 50000.00 | 30000.00 | 30000.00 | 75000.00 | 75000.00 | 50000.00 | 50000.00 | 30000.00 | Mona Generator Services Pvt. Ltd.
5.00 | Laying of one number XLPE insulated and PVC sheathed power cable of 1.1 KV grade in the existing open duct as required.
5.10 | Above 185 Sq. mm upto 400 Sq. mm | 200.00 | Mtr. | 352.00 | 50.00 | 10000.00 | 350.00 | 70000.00 | 150.00 | 30000.00 | 150.00 | 30000.00 | 125.00 | 25000.00 | 10000.00 | KR POWER INFRA INDIA PRIVATE LIMITED
| Total in Figures |  |  |  |  | 5394000.00 |  | 4672400.00 |  | 4777000.00 |  | 4557000.00 |  | 4576500.00
Lowest Amount Quoted BY: RISHA CONTROL ENGINEERS PRIVATE LIMITED(4557000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of D.G. Synchronising cum PCC Panel with AMF and Load Sharing Facility at Gaya Airport, Gaya Tender ID: 2020_AAI_62944_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RISHA CONTROL ENGINEERS PRIVATE LIMITED | 4557000.00 | L1
| 2 | Gemtech Power Control Private Limited | 4576500.00 | L2
| 3 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION | 4672400.00 | L3
| 4 | Mona Generator Services Pvt. Ltd. | 4777000.00 | L4
| 5 | KR POWER INFRA INDIA PRIVATE LIMITED | 5394000.00 | L5