## BoQ1
Government eProcurement System Created By: KAMBLE TANAJI Created Date/Time: 18-Dec-2020 04:51 PM Tender Title: Improvement of Illumination of Terminal Building at Pune Airport Tender ID: 2020_AAI_63352_1
Tender Inviting Authority: Asst. General Manager (Engg-Elect)
Tender Inviting Authority: Asst. General Manager (Engg-Elect)
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SHANTI ELECTRICALS(GSTN-NA)
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply Installation Testing and Commissioning of LED deep Recessed pressure die cast housing downlighter of min 4300 lumens, 40Watt (including driver), efficacy>110 lm/W, burning hour > 50,000 hrs at L70B50, CCT 4000K, SDCM <5, CRI>80, IP20 rating, suitable surge protection device as recommended by OEM, THD<10%, PF > 0.95, UGR<19, compliance with LM 80 & LM 79 with operating voltage of 140-270V, 50 Hz, AC for 12m inddor high ceiling including arranging of ladder, scafflolding, boom lift etc. and all necessary fitting accessories like mounting clamps/bracket/rods, nut, bolt, hardware etc. complete with LEDs driver of efficiency ≥85% . It also includes dismantalling of existing old fittings and handing over the same to AAI store. (Make: PHILIPS, Model: DN594B LED40/840 PSU C D200 WH WB or equivalent) | 227.00 | Each |  | 5400.00 | 1225800.00 | 1225800.00 | SHANTI ELECTRICALS
2.00 | Supply Installation Testing and Commissioning of 600x600mm size recess LED fitting made of CRCA for existing indoor ceiling including arranging of ladder, scafflolding, boom lift etc. and all necessary fitting accessories like mounting clamps, nut, bolt, hardware etc. complete with LEDs driver of efficiency ≥85%. Fixture should have efficacy ≥110lumens/watt, minimum 3600 lumens, 42W (including driver), burning hour>50000 hrs at L70B50, CCT 4000K, IP20 rating, CRI >80, PF >0.95, SDCM<5, UGR<19, compliance with LM 80 & LM 79, suitable Surge Protection device as recommended by OEM with operating Voltage 140 - 270V, 50 Hz, AC. It also includes dismantalling of existing old fittings and handing over the same to AAI store. (Make: Philips, Model:RC380B LED42S -6500 G4 L60 W60 PSD OD or equivalent) | 150.00 | Each |  | 2900.00 | 435000.00 | 435000.00 | SHANTI ELECTRICALS
3.00 | Supplying and fixing of following ways surface/ recess mounting, 415 V, horizontal pre-wired TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs including dismantlling of exisitng old DBs & handing over the sam eto AAI store etc. (but without MCBs and incomer ) as required .
3.01 | 4 way (4 + 12), Double door | 7.00 | Each |  | 3000.00 | 21000.00 | 21000.00 | SHANTI ELECTRICALS
3.02 | 6 way (4 + 18), Double door | 2.00 | Each |  | 3200.00 | 6400.00 | 6400.00 | SHANTI ELECTRICALS
3.03 | 8 way (4 + 24), Double door | 10.00 | Each |  | 3500.00 | 35000.00 | 35000.00 | SHANTI ELECTRICALS
3.04 | 12 way (4 + 36), Double door | 2.00 | Each |  | 5100.00 | 10200.00 | 10200.00 | SHANTI ELECTRICALS
4.00 | Supplying and fixing following rating four pole, 415 volts, MCB , in the existing MCB DB Complete with connections, testing and commissioning etc.as required.
4.01 | 63 Amps. 4 Pole MCB C Series | 21.00 | Each |  | 1100.00 | 23100.00 | 23100.00 | SHANTI ELECTRICALS
5.00 | Supplying and fixing following rating, 6 to 32 amp, MCB in the existing MCB DB Complete with connections, testing and commissioning etc.as required.
5.01 | Single Pole , MCB C Series | 200.00 | Each |  | 140.00 | 28000.00 | 28000.00 | SHANTI ELECTRICALS
5.02 | Single Pole & Neutral MCB C Series | 50.00 | Each |  | 350.00 | 17500.00 | 17500.00 | SHANTI ELECTRICALS
5.03 | Double Pole MCB C Series | 40.00 | Each |  | 370.00 | 14800.00 | 14800.00 | SHANTI ELECTRICALS
6.00 | Supplying and fixing following rating, 40 amp, MCB in the existing MCB DB Complete with connections, testing and commissioning etc.as required.
6.01 | Double Pole, 40 Amp C series | 40.00 | Each |  | 700.00 | 28000.00 | 28000.00 | SHANTI ELECTRICALS
7.00 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 200.00 | Each |  | 7.00 | 1400.00 | 1400.00 | SHANTI ELECTRICALS
| Total in Figures |  |  |  |  | 1846200.00
Lowest Amount Quoted BY: SHANTI ELECTRICALS(1846200.00)

## BOQ Summary
BOQ Summary Details Tender Title: Improvement of Illumination of Terminal Building at Pune Airport Tender ID: 2020_AAI_63352_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SHANTI ELECTRICALS | 1846200.00 | L1