## BoQ1
Government eProcurement System Created By: SYED TANWEER ASHRAF Created Date/Time: 15-Jan-2021 03:26 PM Tender Title: Replacement of Existing Cooling Tower at Gaya Airport, Gaya Bihar. Tender ID: 2020_AAI_63995_1
Tender Inviting Authority: AGM ( Engg. Elect), AAI, Gaya Airport, Gaya
Name of Work: Replacement of Existing Cooling Tower at Gaya Airport , Gaya (Bihar ).
Contract No: <0631-2210043>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOLKS ENERGIE PVT LTD(GSTN-07AADCV9396C1ZZ) |  | NIRVANA TECHNOLOGIES(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Dismentaling and Removing of existing Old Cooling Tower including foundation as required and Handing over the dismantled items to AAI store. | 3.00 | JOB | 263.00 | 10000.00 | 30000.00 | 45000.00 | 135000.00 | 30000.00 | VOLKS ENERGIE PVT LTD
2.00 | Supply , installation , testing & commisioning of Induced draft FRP cooling Tower of minimum 420 TR heat rejection capacity along with HDPE make up water Tank of minimum 5000 ltrs capacity ( water tank to be installed on existing foundation ) with FRP water basin to be installed on newly constrcuted /fabricated Foundation structure for Cooling tower as per cooling tower Size with Multi/Single Fan of required capacity ,PVC fillings with integral Louvers and drift Eliminators complete with hot water basin either fitted with Spray Nozzles or having self rotating sprinkerls ,statically & dynamically balanced axial flow type fan direct driven or driven through reduction gear box with TEFC induction motor with suction screen , makeup - quick fill arrengement , over flow & drain connection with fixing of necessary valves , & suitable inspection ladder , access arrangement for cooling tower interior, aniti vibration mounting complete as per specification & as required etc with following Technical Data. (a) Water Flow/Tower - 1450 USGPM (b) Entering water Temp - 97.5 degree F (c) Outlet Water Temperater - 90 degree F (d) Heat Rejection Capacity -420TR (e) Ambient wet Bulb Temp -83 degree F . ( Note - Making of new cement concrete foundation and steel /Masonary supporting structure as per manufacturer design of cooling tower are included in the item and in the scope of contractor.) | 3.00 | JOB | 263.00 | 690000.00 | 2070000.00 | 587000.00 | 1761000.00 | 1761000.00 | NIRVANA TECHNOLOGIES
3.00 | Supply, fixing, testing and commissioning of "C " Class Heavy MS Pipe of following sizes complete with nuts and Bolts , elbow , flange , painting etc complete as required for connection of Pipe line to cooling tower as per actual site requrement. ( fixing includes underground as well on Surface with supporting column as per site requirement & technical specifications).
3.10 | 250mm (Supply and return line of Cooling Tower ) | 50.00 | meter | 351.00 | 2590.00 | 129500.00 | 5000.00 | 250000.00 | 129500.00 | VOLKS ENERGIE PVT LTD
3.20 | 150 mm (Balancing Line of Cooling Tower ) | 50.00 | meter | 352.00 | 1580.00 | 79000.00 | 2600.00 | 130000.00 | 79000.00 | VOLKS ENERGIE PVT LTD
3.30 | 75 mm ( Drain Line of Cooling Tower ) | 50.00 | meter | 352.00 | 1000.00 | 50000.00 | 1200.00 | 60000.00 | 50000.00 | VOLKS ENERGIE PVT LTD
3.40 | 50 mm ( water Make up Line ) | 75.00 | meter | 352.00 | 800.00 | 60000.00 | 700.00 | 52500.00 | 52500.00 | NIRVANA TECHNOLOGIES
4.00 | Supply, fixing, testing and commissioning of following sizes butterfly Valve with CI body SS disc , nitrile rubber Seal & o -ring of PN 16 Pressure ratings for cooling tower Pipe Line including flange , nut bolts complete as required
4.10 | 250mm (Supply and return line of Cooling Tower ) | 6.00 | JOB | 352.00 | 12300.00 | 73800.00 | 32000.00 | 192000.00 | 73800.00 | VOLKS ENERGIE PVT LTD
4.20 | 150 mm (Balancing Line of Cooling Tower ) | 3.00 | JOB | 352.00 | 3800.00 | 11400.00 | 22000.00 | 66000.00 | 11400.00 | VOLKS ENERGIE PVT LTD
4.30 | 75 mm ( Drain Line of Cooling Tower ) | 6.00 | JOB | 352.00 | 2200.00 | 13200.00 | 10000.00 | 60000.00 | 13200.00 | VOLKS ENERGIE PVT LTD
4.40 | 50 mm ( water Make up Line ) | 6.00 | JOB | 352.00 | 1800.00 | 10800.00 | 5000.00 | 30000.00 | 10800.00 | VOLKS ENERGIE PVT LTD
5.00 | Supply, fixing, testing and commissioning of pressure Gauge with valve , flower , nipple , socket complete as required | 6.00 | JOB | 352.00 | 1800.00 | 10800.00 | 2000.00 | 12000.00 | 10800.00 | VOLKS ENERGIE PVT LTD
6.00 | Supply, fixing, testing and commissioning of temperature Gauge with valve , flange , thermometer with Thermowell etc | 6.00 | JOB | 352.00 | 1000.00 | 6000.00 | 3000.00 | 18000.00 | 6000.00 | VOLKS ENERGIE PVT LTD
7.00 | Supply, fixing, testing and commissioning of 3.5X 25 Sqmm , aluminium conductor armoured cable , 1.1 KV grade with 6 SWG Earthing GI wire from Electrical Panel /Starter to cooling Tower Fan complete with Thimbled Connector Connection complete as required | 210.00 | Mtr | 352.00 | 228.00 | 47880.00 | 130.00 | 27300.00 | 27300.00 | NIRVANA TECHNOLOGIES
8.00 | SITC of ON/OFF Control Starter of Cooling Tower Fan complete with Connection as required. | 3.00 | JOB | 352.00 | 7000.00 | 21000.00 | 3000.00 | 9000.00 | 9000.00 | NIRVANA TECHNOLOGIES
9.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, fixed with suitable M.S support including bolts & nut etc as required. a) 100 mm width X 50 mm depth X 1.6 mm thickness | 15.00 | Mtr | 352.00 | 300.00 | 4500.00 | 550.00 | 8250.00 | 4500.00 | VOLKS ENERGIE PVT LTD
| Total in Figures |  |  |  |  | 2617880.00 |  | 2811050.00
Lowest Amount Quoted BY: VOLKS ENERGIE PVT LTD(2617880.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Existing Cooling Tower at Gaya Airport, Gaya Bihar. Tender ID: 2020_AAI_63995_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | VOLKS ENERGIE PVT LTD | 2617880.00 | L1
| 2 | NIRVANA TECHNOLOGIES | 2811050.00 | L2