## BoQ1
Government eProcurement System Created By: rakesh kumar yadav Created Date/Time: 24-Dec-2020 04:28 PM Tender Title: Construction of ASR MSSR Building at Jaipur Airport, Jaipur. SH- SITC of Precision type Air-conditioning Tender ID: 2020_AAI_64135_1
Tender Inviting Authority: Asstt. Gen. Manager (Engg-E), Jaipur Airport, Airport - 302029
Name of Work: Construction of ASR MSSR Building at Jaipur Airport, Jaipur. SH SITC of Precision type Air-conditioning
Contract No: 2020_AAI_64135_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOLKS ENERGIE PVT LTD(GSTN-07AADCV9396C1ZZ) |  | Leo Air and Power Solution Pvt Ltd.,(GSTN-07AABCL1931F1ZW) |  | COOL TECH ENGINEERS(GSTN-08AAFFC7397B1ZD) |  | Om Vaishnav Technocrates(GSTN-07AEHPG9781R1ZJ) |  | TRAC FUJICO AIR SYSTEMS LLP(GSTN-33AAHFT3672J1ZY) |  | APEXINFRANET PVT LTD(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of Floor Mounted, Bottom discharge, Air Cooled DX type CRAC units for Equipments room application, equipped with most advanced & industry technology, guaranteeing precise control of Equipment room. Suitable for 415 Volts, 50 Hz, 3 Phase Power Supply. The units shall be selected on the basis of following parameters: i) 42.8 kW of minimum Gross Sensible Cooling Capacity @ 15800 CMH. ii) 22 Deg C/50% RH of return air. iii) Supply air in between 13-15 Deg C. iv) 45 Deg C of Design Ambient temperature. The Indoor unit shall comprise of Variable capacity Inverter Scroll Compressor, Fiberglass corrosion resistant EC fans, Evaporator DX Cooling Coil with hydrophilic coating, Microprocessor controllers, Thermostatic/Electronic Expansion valves, Driers, EU4 Filter, Suction and Discharge piping, Internal power and Control wiring, Crankcaseheaters, Steam Electrode/ Infrared Humidifier, Heaters, HP/LP Cutouts, Power and Control contactors, water leak detectors and Other Electrical accessories The Outdoor Condenser unit shall comprise of Condenser fans & motor, Condenser cooling coil (Copper coil with aluminum fins), Fan speed controller, Isolator switch. Complete as per OEMs specifications. | 3.00 | Each | 100.00 | 719000.00 | 2157000.00 | 667000.00 | 2001000.00 | 685000.00 | 2055000.00 | 640000.00 | 1920000.00 | 744694.00 | 2234082.00 | 775000.00 | 2325000.00 | 1920000.00 | Om Vaishnav Technocrates
2.00 | Installation and testing and commisiooning of Floor Mounted, Bottom discharge, Air Cooled DX type CRAC units for Equipment room application, equipped with most advanced & industry technology, guaranteeing precise control of Equipment room as supplied in item no. 1. Complete as required including minor civil work. | 3.00 | Job | 100.00 | 25000.00 | 75000.00 | 17250.00 | 51750.00 | 8000.00 | 24000.00 | 60000.00 | 180000.00 | 38720.00 | 116160.00 | 25000.00 | 75000.00 | 24000.00 | COOL TECH ENGINEERS
3.00 | Supply and fixing of Copper refrigerent piping including insulation, supports, clamps, fittings, connections, sleevs etc of required size complete with insulation as per IS specification. | 130.00 | Mtr | 100.00 | 1200.00 | 156000.00 | 1725.00 | 224250.00 | 800.00 | 104000.00 | 1200.00 | 156000.00 | 1341.00 | 174330.00 | 1100.00 | 143000.00 | 104000.00 | COOL TECH ENGINEERS
4.00 | Supply and fixing 4x 2.5 Sq.mm copper armoured cable as per relevent IS specification complete as required. | 150.00 | Mtr | 100.00 | 220.00 | 33000.00 | 225.00 | 33750.00 | 125.00 | 18750.00 | 350.00 | 52500.00 | 202.00 | 30300.00 | 125.00 | 18750.00 | 18750.00 | APEXINFRANET PVT LTD, COOL TECH ENGINEERS
5.00 | Supplying & fixing of heavy duty Wall/ Floor maunted stand for Pricision AC indoor unit including Minor Civil Work complete as required. | 3.00 | Job | 100.00 | 2000.00 | 6000.00 | 4000.00 | 12000.00 | 2500.00 | 7500.00 | 8000.00 | 24000.00 | 5124.00 | 15372.00 | 6000.00 | 18000.00 | 6000.00 | VOLKS ENERGIE PVT LTD
6.00 | Supplying & fixing of heavy duty Wall/ Floor maunted stand for Pricision AC outdoor unit Minor Civil Work complete as required. | 3.00 | Job | 100.00 | 3500.00 | 10500.00 | 4000.00 | 12000.00 | 2000.00 | 6000.00 | 9500.00 | 28500.00 | 10587.00 | 31761.00 | 6000.00 | 18000.00 | 6000.00 | COOL TECH ENGINEERS
7.00 | Supply and fixing of 32 mm dia CPVC Pipe for humidifier drain pipe, complete with fittings supports, valves , 6 mm thick nitrile rubber insulation as required. | 15.00 | Mtr | 100.00 | 125.00 | 1875.00 | 277.00 | 4155.00 | 200.00 | 3000.00 | 375.00 | 5625.00 | 560.00 | 8400.00 | 300.00 | 4500.00 | 1875.00 | VOLKS ENERGIE PVT LTD
8.00 | Supply and fixing of 40 mm dia CPVC Pipe for humidifier drain pipe, complete with fittings supports, valves , 6 mm thick nitrile rubber insulation as required. | 10.00 | Mtr | 100.00 | 185.00 | 1850.00 | 347.00 | 3470.00 | 300.00 | 3000.00 | 425.00 | 4250.00 | 758.00 | 7580.00 | 350.00 | 3500.00 | 1850.00 | VOLKS ENERGIE PVT LTD
9.00 | SITC of 22 SWG GI sheet Metal Ducting i/c necessary support, adjustable dampers, vanes etc. Complete as required. | 25.00 | Sqm | 10.00 | 716.00 | 17900.00 | 920.00 | 23000.00 | 725.00 | 18125.00 | 1250.00 | 31250.00 | 1223.00 | 30575.00 | 2000.00 | 50000.00 | 17900.00 | VOLKS ENERGIE PVT LTD
10.00 | SITC of 24 SWG GI sheet Metal Ducting i/c necessary support, adjustable dampers, vanes etc. Complete as required. | 20.00 | Sqm | 10.00 | 628.00 | 12560.00 | 978.00 | 19560.00 | 550.00 | 11000.00 | 950.00 | 19000.00 | 1065.00 | 21300.00 | 1800.00 | 36000.00 | 11000.00 | COOL TECH ENGINEERS
11.00 | Supply and fixing of nitrile insullation 13mm thick as per specifiication as required. | 20.00 | Sqm | 100.00 | 400.00 | 8000.00 | 506.00 | 10120.00 | 450.00 | 9000.00 | 750.00 | 15000.00 | 586.00 | 11720.00 | 700.00 | 14000.00 | 8000.00 | VOLKS ENERGIE PVT LTD
12.00 | Supply and fixing of accoustic lining insulation 25mm thick rigid/semirigid fibre glass 48 Kg/Cum density finished with 26 G aluminium perforated sheet. Fibre glass should be of fire retardent material as per specifiication as required. | 25.00 | Sqm | 100.00 | 560.00 | 14000.00 | 909.00 | 22725.00 | 500.00 | 12500.00 | 850.00 | 21250.00 | 867.00 | 21675.00 | 900.00 | 22500.00 | 12500.00 | COOL TECH ENGINEERS
13.00 | Supply and Fixing of alluminium powder coated grill/diffusers complete as per specifiication as required. | 10.00 | Sqm | 100.00 | 3200.00 | 32000.00 | 4287.00 | 42870.00 | 8000.00 | 80000.00 | 7500.00 | 75000.00 | 8537.00 | 85370.00 | 8800.00 | 88000.00 | 32000.00 | VOLKS ENERGIE PVT LTD
14.00 | Supply and Fixing of MS VCD for collar as per specifiication as required. | 3.00 | Sqm | 100.00 | 5700.00 | 17100.00 | 2432.00 | 7296.00 | 2000.00 | 6000.00 | 4500.00 | 13500.00 | 5608.00 | 16824.00 | 2200.00 | 6600.00 | 6000.00 | COOL TECH ENGINEERS
15.00 | Supply and Fixing of GI VCD for duct as per specifiication as required. | 5.00 | Sqm | 100.00 | 5700.00 | 28500.00 | 4888.00 | 24440.00 | 6000.00 | 30000.00 | 6500.00 | 32500.00 | 7393.00 | 36965.00 | 4200.00 | 21000.00 | 21000.00 | APEXINFRANET PVT LTD
16.00 | Supply and Fixing of canvas connection as per specifiication as required. | 3.00 | Each | 100.00 | 1500.00 | 4500.00 | 2000.00 | 6000.00 | 1800.00 | 5400.00 | 3500.00 | 10500.00 | 4723.00 | 14169.00 | 1200.00 | 3600.00 | 3600.00 | APEXINFRANET PVT LTD
17.00 | Supply and initial charge of R-410a refrigerant gas and oil required for pricision type AC | 70.00 | Kg | 100.00 | 400.00 | 28000.00 | 460.00 | 32200.00 | 650.00 | 45500.00 | 800.00 | 56000.00 | 901.00 | 63070.00 | 800.00 | 56000.00 | 28000.00 | VOLKS ENERGIE PVT LTD
18.00 | SITC of following capacity 5 Star Invertor technology Split type Air-Conditioner unit fitted with hermetically sealed compressors operating on refrigerant R-410A or equivalent green gas suitable for wall mounting and suitable for operating on 230V +_10%, 50Hz, Single Phase, AC Supply including 3 metre refrigrant piping, related civil works and providing & fixing of Iron stand for outdoor unit etc. complete as required.
18.10 | 2.0 TR | 6.00 | Each | 100.00 | 42500.00 | 255000.00 | 57788.00 | 346728.00 | 39000.00 | 234000.00 | 52200.00 | 313200.00 | 56686.00 | 340116.00 | 53000.00 | 318000.00 | 234000.00 | COOL TECH ENGINEERS
18.20 | 1.5 TR | 2.00 | Each | 100.00 | 37500.00 | 75000.00 | 44505.00 | 89010.00 | 32000.00 | 64000.00 | 42250.00 | 84500.00 | 43318.00 | 86636.00 | 45000.00 | 90000.00 | 64000.00 | COOL TECH ENGINEERS
19.00 | SITC of Tower type split air conditioners having minimum cooling capacity of 45000 BTU/hr (3.8 TR) suitable for operation on 415 volt + 10%, 3 phase 50 Hz AC supply including all the outdoor and indoor accessories etc., capable of performing cooling dehumidifying air circulation, filternation, ventilation including supply and fixing outdoor and indoor unit stand of required size complete as required. | 2.00 | Each | 100.00 | 85360.00 | 170720.00 | 103788.00 | 207576.00 | 75000.00 | 150000.00 | 165000.00 | 330000.00 | 102357.00 | 204714.00 | 120000.00 | 240000.00 | 150000.00 | COOL TECH ENGINEERS
20.00 | Supply and fixing of suitable size suction and discharge copper refrigerant extra piping including insulation suitable for above mentioned 2/1.5TR split AC units. | 50.00 | Mtr | 100.00 | 450.00 | 22500.00 | 500.00 | 25000.00 | 600.00 | 30000.00 | 850.00 | 42500.00 | 1008.00 | 50400.00 | 850.00 | 42500.00 | 22500.00 | VOLKS ENERGIE PVT LTD
21.00 | Supply and fixing of suitable size suction and discharge copper refrigerant extra piping including insulation suitable for above mentioned 3.8TR tower type AC units. | 30.00 | Mtr | 100.00 | 500.00 | 15000.00 | 500.00 | 15000.00 | 780.00 | 23400.00 | 1200.00 | 36000.00 | 1241.00 | 37230.00 | 950.00 | 28500.00 | 15000.00 | VOLKS ENERGIE PVT LTD, Leo Air and Power Solution Pvt Ltd.,
22.00 | Supply and fixing of following size PVC drain piping including insulation suitable for above mentioned split/tower type AC units. |  |  | 100.00
22.10 | 32 mm dia | 30.00 | Mtr | 100.00 | 100.00 | 3000.00 | 150.00 | 4500.00 | 150.00 | 4500.00 | 350.00 | 10500.00 | 240.00 | 7200.00 | 90.00 | 2700.00 | 2700.00 | APEXINFRANET PVT LTD
22.20 | 25 mm dia | 20.00 | Mtr | 100.00 | 90.00 | 1800.00 | 135.00 | 2700.00 | 125.00 | 2500.00 | 250.00 | 5000.00 | 178.00 | 3560.00 | 70.00 | 1400.00 | 1400.00 | APEXINFRANET PVT LTD
23.00 | Supplying and installing 200 mm width x 50mm depth x 2.0 mm thickness perforated Hot Dipped Galvanised Iron cable tray (galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, tee(s), bend(s), reducer(s), suspended from the ceiling with G.I. suspenders or fixed on wall/ structure with MS angle as per site condition including G.I. bolts & nuts, etc. as required. | 200.00 | Mtr | 100.00 | 450.00 | 90000.00 | 440.00 | 88000.00 | 100.00 | 20000.00 | 950.00 | 190000.00 | 761.00 | 152200.00 | 425.00 | 85000.00 | 20000.00 | COOL TECH ENGINEERS
24.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Each | 100.00 | 15000.00 | 30000.00 | 5000.00 | 10000.00 | 4534.00 | 9068.00 | 22000.00 | 44000.00 | 9991.00 | 19982.00 | 8500.00 | 17000.00 | 9068.00 | COOL TECH ENGINEERS
25.00 | Providing & fixing 25 mmX 5mm GI Strip in 40 mm dia GI pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 15.00 | Mtr | 100.00 | 286.00 | 4290.00 | 460.00 | 6900.00 | 425.00 | 6375.00 | 800.00 | 12000.00 | 578.00 | 8670.00 | 355.00 | 5325.00 | 4290.00 | VOLKS ENERGIE PVT LTD
26.00 | Providing and fixing 25mm x 5mm GI strip on surface/lattice tower for connections etc as required. | 30.00 | Mtr | 100.00 | 130.00 | 3900.00 | 145.00 | 4350.00 | 125.00 | 3750.00 | 125.00 | 3750.00 | 167.00 | 5010.00 | 90.00 | 2700.00 | 2700.00 | APEXINFRANET PVT LTD
| Total in Figures |  |  |  |  | 3274995.00 |  | 3330350.00 |  | 2986368.00 |  | 3716325.00 |  | 3835371.00 |  | 3736575.00
Lowest Amount Quoted BY: COOL TECH ENGINEERS(2986368.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of ASR MSSR Building at Jaipur Airport, Jaipur. SH- SITC of Precision type Air-conditioning Tender ID: 2020_AAI_64135_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | COOL TECH ENGINEERS | 2986368.00 | L1
| 2 | VOLKS ENERGIE PVT LTD | 3274995.00 | L2
| 3 | Leo Air and Power Solution Pvt Ltd., | 3330350.00 | L3
| 4 | Om Vaishnav Technocrates | 3716325.00 | L4
| 5 | APEXINFRANET PVT LTD | 3736575.00 | L5
| 6 | TRAC FUJICO AIR SYSTEMS LLP | 3835371.00 | L6