## BoQ1
Government eProcurement System Created By: ABHIJIT DATTA Created Date/Time: 22-Feb-2021 11:34 AM Tender Title: Provision of LED Apron Flood Lighting of RCS Bays, Cargo Bay C15 to C16 and new Bays C1 to C 14 at NSCBI Airport, Kolkata. Tender ID: 2020_AAI_64435_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work: Provision of LED Apron Flood Lighting of RCS Bays, Cargo Bay C15-to C16 & new Bays C1 to C 14 at NSCBI Airport, Kolkata.
Contract No: AAC/AGM(EE)-II/2020-21/NIT-04
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Kripa Electronics india pvt ltd(GSTN-27AACCK9472B1ZI) |  | PRIME ENGINEERS(GSTN-24ANMPS9053Q1Z0)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH : I SITC WORK Design & SITC of Luminaires Designing of Apron Flood Lighting for RCS Bays, Cargo Bay C15 to C16, new Bays C1 to C 14 and GSE Area beside Watch Tower no 1 of Kolkata Airport with LED flood light luminaries considering minimum glare and of less than 45 UGR at different directions for the Pilot situated at a height of 4 to 6 mtrs above ground level at Apron area and Glare Analysis reporting so as to maintain the lux level not less than the requirement of latest ICAO, Annexure - 14 / DGCA CAR at the end of 5th year and restricting the power consumption not more than (i) 1.1 KW +10% per High mast for Illumination of Cargo Bay C15 to C16. (ii) 1.2 KW + 10 % for Illumination of RCS Bays, (iii) 650Watts + 10 % for Illumination of C1 to C 14 bays where numbers and height of the high masts are fixed (as per existing plan and drawings) complete as required and vetting the same in AAI approved lab and as detailed in the Technical Specifications of this tender. | 1.00 | Job | 925000.00 | 750000.00 | 750000.00 | 800000.00 | 800000.00 | 750000.00 | Kripa Electronics india pvt ltd
2.00 | Supplying set of LED luminaires with driver set for Apron Flood Lighting for each high mast as per design requirement (ref. item-1) etc. complete as required. | 37.00 | Set | 170000.00 | 200000.00 | 7400000.00 | 140000.00 | 5180000.00 | 5180000.00 | PRIME ENGINEERS
3.00 | Supply of LED Flood lighting Luminaire with Driver set complete as required as per the Technical Specifications of the tender document. (i) 180-200 Watts 30 Degree Beam. | 40.00 | Each | 20000.00 | 24000.00 | 960000.00 | 14000.00 | 560000.00 | 560000.00 | PRIME ENGINEERS
4.00 | Supply of LED Flood lighting Luminaire with Driver set complete as required as per the Technical Specifications of the tender document. (i) 180 Watts 10 Degree Beam Angle | 5.00 | Each | 26500.00 | 24000.00 | 120000.00 | 15000.00 | 75000.00 | 75000.00 | PRIME ENGINEERS
5.00 | Supply of LED Flood lighting Luminaire with Driver set complete as required as per the Technical Specifications of the tender document. (i) 250-270 Watts 30 Degree Beam Angle. | 40.00 | Each | 22000.00 | 28500.00 | 1140000.00 | 18000.00 | 720000.00 | 720000.00 | PRIME ENGINEERS
6.00 | Supply of LED Flood lighting Luminaire with Driver set complete as required as per the Technical Specifications of the tender document. (i) 250 Watts 10 Degree Beam Angle. | 5.00 | Each | 29500.00 | 28500.00 | 142500.00 | 19000.00 | 95000.00 | 95000.00 | PRIME ENGINEERS
7.00 | Testing of randomly selected Luminaires as offered in item no. 2 in AAI approved NABL accredited laboratories for LM-79 etc. complete as required and submission of 2 sets of Report including to and from transportation, loading and unloading etc. complete as required. | 20.00 | Each | 36285.00 | 60000.00 | 1200000.00 | 60000.00 | 1200000.00 | 1200000.00 | Kripa Electronics india pvt ltd, PRIME ENGINEERS
8.00 | Installation, testing and commissioning of LED luminaires with Driver Set for Apron Flood Lighting on 7 m to 30 mtrs High Mast to maintain the illumination level as per the design (item-1) including wiring (4 sq mm for incoming and 2.5 mm Sq.mm. Cu cable for interconnection, PVC insulated PVC sheathed, ISI marked) connections, interconnection, fixing the fittings, angle setting of fixtures to achieve average lux and Glare as per the design etc. complete as required. | 37.00 | Job | 7000.00 | 3000.00 | 111000.00 | 5500.00 | 203500.00 | 111000.00 | Kripa Electronics india pvt ltd
9.00 | Design and SITC of High Masts Designing and Supplying of following height of hot dip galvanized (internal and external), polygonal, single / double sectional, slip in stress fit high mast made of Steel as per BS/DIN/ASTM, welded as per BS-5135 / AWS and designed to with stand wind speed as per IS-875 complete in all respects including manually cum electrically operated raising and lowering mechanism having double drum double gear winch, gear, motor for lifting, lowering with remote console having operated push button and with 5 mtr length of cord, Stainless steel wire ropes, lantern carriage suitable for LED luminaires as required by the design as explained in item-1 and 2 nos LED type aviation obstruction light, top pulley arrangement (triple), junction Boxes - 02 nos, Lightning finial, providing (2 nos) required length of 1.1 KV grade multicore copper conductor trailing cable (as per IS - 4289, elastomer insulated, natural or synthetic textile material braided). The Lantern Carriage should accommodate 02 nos of Junction Box with Terminal blocks to Terminate and Interconnect the trailing cables and Loop Cables of Luminaires. 20 A multiple socket and top etc. as mentioned in technical specifications, complete as required. (a) 07 mtr. High | 6.00 | Each | 96140.00 | 320000.00 | 1920000.00 | 360000.00 | 2160000.00 | 1920000.00 | Kripa Electronics india pvt ltd
10.00 | Designing and Supplying of following height of hot dip galvanized (internal and external), polygonal, single / double sectional, slip in stress fit high mast made of Steel as per BS/DIN/ASTM, welded as per BS-5135 / AWS and designed to with stand wind speed as per IS-875 complete in all respects including manually cum electrically operated raising and lowering mechanism having double drum double gear winch, gear, motor for lifting, lowering with remote console having operated push button and with 5 mtr length of cord, Stainless steel wire ropes, lantern carriage suitable for LED luminaires as required by the design as explained in item-1 and 2 nos LED type aviation obstruction light, top pulley arrangement (triple), junction Boxes - 02 nos, Lightning finial, providing (2 nos) required length of 1.1 KV grade multicore copper conductor trailing cable (as per IS - 4289, elastomer insulated, natural or synthetic textile material braided). The Lantern Carriage should accommodate 02 nos of Junction Box with Terminal blocks to Terminate and Interconnect the trailing cables and Loop Cables of Luminaires. 20 A multiple socket and top etc. as mentioned in technical specifications, complete as required. (a) 08 mtr High | 3.00 | Each | 103550.00 | 320000.00 | 960000.00 | 360000.00 | 1080000.00 | 960000.00 | Kripa Electronics india pvt ltd
11.00 | Designing and Supplying of following height of hot dip galvanized (internal and external), polygonal, single / double sectional, slip in stress fit high mast made of Steel as per BS/DIN/ASTM, welded as per BS-5135 / AWS and designed to with stand wind speed as per IS-875 complete in all respects including manually cum electrically operated raising and lowering mechanism having double drum double gear winch, gear, motor for lifting, lowering with remote console having operated push button and with 5 mtr length of cord, Stainless steel wire ropes, lantern carriage suitable for LED luminaires as required by the design as explained in item-1 and 2 nos LED type aviation obstruction light, top pulley arrangement (triple), junction Boxes - 02 nos, Lightning finial, providing (2 nos) required length of 1.1 KV grade multicore copper conductor trailing cable (as per IS - 4289, elastomer insulated, natural or synthetic textile material braided). The Lantern Carriage should accommodate 02 nos of Junction Box with Terminal blocks to Terminate and Interconnect the trailing cables and Loop Cables of Luminaires. 20 A multiple socket and top etc. as mentioned in technical specifications, complete as required. (a) 09 mtr. High | 6.00 | Each | 124450.00 | 350000.00 | 2100000.00 | 390000.00 | 2340000.00 | 2100000.00 | Kripa Electronics india pvt ltd
12.00 | Designing and Supplying of following height of hot dip galvanized (internal and external), polygonal, single / double sectional, slip in stress fit high mast made of Steel as per BS/DIN/ASTM, welded as per BS-5135 / AWS and designed to with stand wind speed as per IS-875 complete in all respects including manually cum electrically operated raising and lowering mechanism having double drum double gear winch, gear, motor for lifting, lowering with remote console having operated push button and with 5 mtr length of cord, Stainless steel wire ropes, lantern carriage suitable for LED luminaires as required by the design as explained in item-1 and 2 nos LED type aviation obstruction light, top pulley arrangement (triple), junction Boxes - 02 nos, Lightning finial, providing (2 nos) required length of 1.1 KV grade multicore copper conductor trailing cable (as per IS - 4289, elastomer insulated, natural or synthetic textile material braided). The Lantern Carriage should accommodate 02 nos of Junction Box with Terminal blocks to Terminate and Interconnect the trailing cables and Loop Cables of Luminaires. 20 A multiple socket and top etc. as mentioned in technical specifications, complete as required. (a) 12 Mtr High | 11.00 | Each | 220000.00 | 450000.00 | 4950000.00 | 420000.00 | 4620000.00 | 4620000.00 | PRIME ENGINEERS
13.00 | Designing and Supplying of following height of hot dip galvanized (internal and external), polygonal, single / double sectional, slip in stress fit high mast made of Steel as per BS/DIN/ASTM, welded as per BS-5135 / AWS and designed to with stand wind speed as per IS-875 complete in all respects including manually cum electrically operated raising and lowering mechanism having double drum double gear winch, gear, motor for lifting, lowering with remote console having operated push button and with 5 mtr length of cord, Stainless steel wire ropes, lantern carriage with latching suspension suitable for LED luminaires as required by the design as explained in item-1 and 2 nos LED type aviation obstruction light, top pulley arrangement (triple), junction Boxes - 02 nos, Lightning finial, providing (2 nos) required length of 1.1 KV grade multicore copper conductor trailing cable (as per IS - 4289, elastomer insulated, natural or synthetic textile material braided) . The Lantern Carriage should accommodate 02 nos of Junction Box with Terminal blocks to Terminate and Interconnect the trailing cables and Loop Cables of Luminaires. 20 A multiple socket and top etc. as mentioned in technical specifications, complete as required. (a) 21 Mtr High | 1.00 | Each | 700000.00 | 500000.00 | 500000.00 | 480000.00 | 480000.00 | 480000.00 | PRIME ENGINEERS
14.00 | Designing and Supplying of following height of hot dip galvanized (internal and external), polygonal, single / double sectional, slip in stress fit high mast made of Steel as per BS/DIN/ASTM, welded as per BS-5135 / AWS and designed to with stand wind speed as per IS-875 complete in all respects including manually cum electrically operated raising and lowering mechanism having double drum double gear winch, gear, motor for lifting, lowering with remote console having operated push button and with 5 mtr length of cord, Stainless steel wire ropes, lantern carriage with latching suspension suitable for LED luminaires as required by the design as explained in item-1 and 2 nos LED type aviation obstruction light, top pulley arrangement (triple), junction Boxes - 02 nos, Lightning finial, providing (2 nos) required length of 1.1 KV grade multicore copper conductor trailing cable (as per IS - 4289, elastomer insulated, natural or synthetic textile material braided) . The Lantern Carriage should accommodate 02 nos of Junction Box with Terminal blocks to Terminate and Interconnect the trailing cables and Loop Cables of Luminaires. 20 A multiple socket and top etc. as mentioned in technical specifications, complete as required. (a) 22 Mtr High | 3.00 | Each | 700000.00 | 500000.00 | 1500000.00 | 490000.00 | 1470000.00 | 1470000.00 | PRIME ENGINEERS
15.00 | Designing and Supplying of following height of hot dip galvanized (internal and external), polygonal, single / double sectional, slip in stress fit high mast made of Steel as per BS/DIN/ASTM, welded as per BS-5135 / AWS and designed to with stand wind speed as per IS-875 complete in all respects including manually cum electrically operated raising and lowering mechanism having double drum double gear winch, gear, motor for lifting, lowering with remote console having operated push button and with 5 mtr length of cord, Stainless steel wire ropes, lantern carriage with latching suspension suitable for LED luminaires as required by the design as explained in item-1 and 2 nos LED type aviation obstruction light, top pulley arrangement (triple), junction Boxes - 02 nos, Lightning finial, providing (2 nos) required length of 1.1 KV grade multicore copper conductor trailing cable (as per IS - 4289, elastomer insulated, natural or synthetic textile material braided) . The Lantern Carriage should accommodate 02 nos of Junction Box with Terminal blocks to Terminate and Interconnect the trailing cables and Loop Cables of Luminaires. 20 A multiple socket and top etc. as mentioned in technical specifications, complete as required. (a) 28 Mtr High | 1.00 | Each | 760000.00 | 650000.00 | 650000.00 | 690000.00 | 690000.00 | 650000.00 | Kripa Electronics india pvt ltd
16.00 | Designing and Supplying of following height of hot dip galvanized (internal and external), polygonal, single / double sectional, slip in stress fit high mast made of Steel as per BS/DIN/ASTM, welded as per BS-5135 / AWS and designed to with stand wind speed as per IS-875 complete in all respects including manually cum electrically operated raising and lowering mechanism having double drum double gear winch, gear, motor for lifting, lowering with remote console having operated push button and with 5 mtr length of cord, Stainless steel wire ropes, lantern carriage with latching suspension suitable for LED luminaires as required by the design as explained in item-1 and 2 nos LED type aviation obstruction light, top pulley arrangement (triple), junction Boxes - 02 nos, Lightning finial, providing (2 nos) required length of 1.1 KV grade multicore copper conductor trailing cable (as per IS - 4289, elastomer insulated, natural or synthetic textile material braided) . The Lantern Carriage should accommodate 02 nos of Junction Box with Terminal blocks to Terminate and Interconnect the trailing cables and Loop Cables of Luminaires. 20 A multiple socket and top etc. as mentioned in technical specifications, complete as required. (a) 30 Mtr High | 3.00 | Each | 800000.00 | 650000.00 | 1950000.00 | 690000.00 | 2070000.00 | 1950000.00 | Kripa Electronics india pvt ltd
17.00 | Carrying out soil test at various locations of NSCBIA by NABL Accredited laboratories which shall include taking the samples, parameters, compilation of field tests and laboratory test results analysing the safe bearing capacity of the particular heights High Masts foundation locations as mentioned in the drawings D1 to D4. (a) For F-Taxi = 02 nos. (b) near Demolished Cargo = 01 no, (c) RCS Bay = 01 no, (d) near WT no1 = 01 no. and submission of 2 sets of each detailed soil testing reports to AAI. | 5.00 | Job | 300000.00 | 200000.00 | 1000000.00 | 280000.00 | 1400000.00 | 1000000.00 | Kripa Electronics india pvt ltd
18.00 | Providing detailed design and drawings of Foundations with minimum M 20 grade concrete for High Masts upto height of 12 mtrs and minimum M 30 Grade for High Masts above 12 mtrs height at various locations of NSCBI Airport Kolkata by taking into consideration inputs of Soil Testing as mentioned in 6 (i) above including vetting the foundation designs from IIT/NIT/Jadavpur University/IISER, or any Govt. Engineering College (2 sets of each detailed and approved drawings for the each type of foundations to be submitted to AAI). | 8.00 | Job | 200000.00 | 19000.00 | 152000.00 | 17000.00 | 136000.00 | 136000.00 | PRIME ENGINEERS
19.00 | Construction of RCC foundation as per the approved vetted design i/c foundation bolts, nut, washers, template, HDPE pipes for cable entry etc for the high masts as offered in Schedule of Quantity including excavation of the Apron area and filling with grade not less M 20 grade for High Masts upto height of 12 mtrs and M 30 Grade for High Masts above 12 mtrs height at various locations of NSCBI Airport Kolkata, refilling the same as per the design requirement etc., Installation, testing and commissioning of High masts of required height, making connection, numbering, necessary electrical connections and making all around steel barricading with MS square tube of size 100mm x 100mm as per the design approved by EIC and grouting on concrete with anchor fastener, red white painting for protection of high masts, Electrical panel and control panels etc. so as to complete the work as required. (a) 07 mtr. High Mast | 6.00 | Each | 150000.00 | 70000.00 | 420000.00 | 110000.00 | 660000.00 | 420000.00 | Kripa Electronics india pvt ltd
20.00 | Construction of RCC foundation as per the approved vetted design i/c foundation bolts, nut, washers, template, HDPE pipes for cable entry etc for the high masts as offered in Schedule of Quantity including excavation of the Apron area and filling with grade not less M 20 grade for High Masts upto height of 12 mtrs and M 30 Grade for High Masts above 12 mtrs height at various locations of NSCBI Airport Kolkata, refilling the same as per the design requirement etc., Installation, testing and commissioning of High masts of required height, making connection, numbering, necessary electrical connections and making all around steel barricading with MS square tube of size 100mm x 100mm as per the design approved by EIC and grouting on concrete with anchor fastener, red white painting for protection of high masts, Electrical panel and control panels etc. so as to complete the work as required. (a) 08 mtr High Mast | 3.00 | Each | 150000.00 | 70000.00 | 210000.00 | 110000.00 | 330000.00 | 210000.00 | Kripa Electronics india pvt ltd
21.00 | Construction of RCC foundation as per the approved vetted design i/c foundation bolts, nut, washers, template, HDPE pipes for cable entry etc for the high masts as offered in Schedule of Quantity including excavation of the Apron area and filling with grade not less M 20 grade for High Masts upto height of 12 mtrs and M 30 Grade for High Masts above 12 mtrs height at various locations of NSCBI Airport Kolkata, refilling the same as per the design requirement etc., Installation, testing and commissioning of High masts of required height, making connection, numbering, necessary electrical connections and making all around steel barricading with MS square tube of size 100mm x 100mm as per the design approved by EIC and grouting on concrete with anchor fastener, red white painting for protection of high masts, Electrical panel and control panels etc. so as to complete the work as required. (a) 09 mtr. High Mast | 6.00 | Each | 170000.00 | 70000.00 | 420000.00 | 110000.00 | 660000.00 | 420000.00 | Kripa Electronics india pvt ltd
22.00 | Construction of RCC foundation as per the approved vetted design i/c foundation bolts, nut, washers, template, HDPE pipes for cable entry etc for the high masts as offered in Schedule of Quantity including excavation of the Apron area and filling with grade not less M 20 grade for High Masts upto height of 12 mtrs and M 30 Grade for High Masts above 12 mtrs height at various locations of NSCBI Airport Kolkata, refilling the same as per the design requirement etc., Installation, testing and commissioning of High masts of required height, making connection, numbering, necessary electrical connections and making all around steel barricading with MS square tube of size 100mm x 100mm as per the design approved by EIC and grouting on concrete with anchor fastener, red white painting for protection of high masts, Electrical panel and control panels etc. so as to complete the work as required. (a) 12 Mtr High Mast | 11.00 | Each | 210000.00 | 100000.00 | 1100000.00 | 150000.00 | 1650000.00 | 1100000.00 | Kripa Electronics india pvt ltd
23.00 | Construction of RCC foundation as per the approved vetted design i/c foundation bolts, nut, washers, template, HDPE pipes for cable entry etc for the high masts as offered in Schedule of Quantity including excavation of the Apron area and filling with grade not less M 20 grade for High Masts upto height of 12 mtrs and M 30 Grade for High Masts above 12 mtrs height at various locations of NSCBI Airport Kolkata, refilling the same as per the design requirement etc., Installation, testing and commissioning of High masts of required height, making connection, numbering, necessary electrical connections and making all around steel barricading with MS square tube of size 100mm x 100mm as per the design approved by EIC and grouting on concrete with anchor fastener, red white painting for protection of high masts, Electrical panel and control panels etc. so as to complete the work as required. (a) 21 Mtr High Mast | 1.00 | Each | 235000.00 | 200000.00 | 200000.00 | 150000.00 | 150000.00 | 150000.00 | PRIME ENGINEERS
24.00 | Construction of RCC foundation as per the approved vetted design i/c foundation bolts, nut, washers, template, HDPE pipes for cable entry etc for the high masts as offered in Schedule of Quantity including excavation of the Apron area and filling with grade not less M 20 grade for High Masts upto height of 12 mtrs and M 30 Grade for High Masts above 12 mtrs height at various locations of NSCBI Airport Kolkata, refilling the same as per the design requirement etc., Installation, testing and commissioning of High masts of required height, making connection, numbering, necessary electrical connections and making all around steel barricading with MS square tube of size 100mm x 100mm as per the design approved by EIC and grouting on concrete with anchor fastener, red white painting for protection of high masts, Electrical panel and control panels etc. so as to complete the work as required. (a) 22 Mtr High Mast | 3.00 | Each | 236000.00 | 200000.00 | 600000.00 | 240000.00 | 720000.00 | 600000.00 | Kripa Electronics india pvt ltd
25.00 | Construction of RCC foundation as per the approved vetted design i/c foundation bolts, nut, washers, template, HDPE pipes for cable entry etc for the high masts as offered in Schedule of Quantity including excavation of the Apron area and filling with grade not less M 20 grade for High Masts upto height of 12 mtrs and M 30 Grade for High Masts above 12 mtrs height at various locations of NSCBI Airport Kolkata, refilling the same as per the design requirement etc., Installation, testing and commissioning of High masts of required height, making connection, numbering, necessary electrical connections and making all around steel barricading with MS square tube of size 100mm x 100mm as per the design approved by EIC and grouting on concrete with anchor fastener, red white painting for protection of high masts, Electrical panel and control panels etc. so as to complete the work as required. (a) 28 Mtr High Mast | 1.00 | Each | 285000.00 | 200000.00 | 200000.00 | 240000.00 | 240000.00 | 200000.00 | Kripa Electronics india pvt ltd
26.00 | Construction of RCC foundation as per the approved vetted design i/c foundation bolts, nut, washers, template, HDPE pipes for cable entry etc for the high masts as offered in Schedule of Quantity including excavation of the Apron area and filling with grade not less M 20 grade for High Masts upto height of 12 mtrs and M 30 Grade for High Masts above 12 mtrs height at various locations of NSCBI Airport Kolkata, refilling the same as per the design requirement etc., Installation, testing and commissioning of High masts of required height, making connection, numbering, necessary electrical connections and making all around steel barricading with MS square tube of size 100mm x 100mm as per the design approved by EIC and grouting on concrete with anchor fastener, red white painting for protection of high masts, Electrical panel and control panels etc. so as to complete the work as required. (a) 30 Mtr High Mast (AAI shall provide 03 nos HM from stores for erection). | 6.00 | Each | 315000.00 | 200000.00 | 1200000.00 | 250000.00 | 1500000.00 | 1200000.00 | Kripa Electronics india pvt ltd
27.00 | Dismantling of existing high mast i/c disconnection of the existing circuits, removal of Control panel to High Masts, disconnection of earthling connection, removal of luminaires and carrying the High mast alongwith accessories to the departmental store of AAI from the operational area and Dismantling of existing high mast concrete foundation including foundation bolts, levelling of excavated surface with cement concrete of Grade M 20 etc. and making good the area same as existing apron, complete as required. (a) upto 20 mtr. High Mast | 2.00 | Job | 100000.00 | 75000.00 | 150000.00 | 50000.00 | 100000.00 | 100000.00 | PRIME ENGINEERS
28.00 | Dismantling of existing high mast i/c disconnection of the existing circuits, removal of Control panel to High Masts, disconnection of earthling connection, removal of luminaires and carrying the High mast alongwith accessories to the departmental store of AAI from the operational area and Dismantling of existing high mast concrete foundation including foundation bolts, levelling of excavated surface with cement concrete of Grade M 20 etc. and making good the area same as existing apron, complete as required. (a) 21 mtr to 30 mtrs High mast | 2.00 | Job | 100000.00 | 10000.00 | 20000.00 | 50000.00 | 100000.00 | 20000.00 | Kripa Electronics india pvt ltd
29.00 | Dismantling of existing Pole i/c disconnection of the exiting circuits to pole, disconnection of earthing connection, removal of luminaires and carrying the pole alongwith accessories to the departmental store of AAI from the operational area and Dismantling of existing concrete foundation, levelling etc. and making this area good same as existing apron, complete as required. (a) upto 12 Mtr Hight | 7.00 | Job | 58000.00 | 100000.00 | 700000.00 | 110000.00 | 770000.00 | 700000.00 | Kripa Electronics india pvt ltd
30.00 | Electrical and associated works Supply of weather proof, vermin proof, powder coated, free floor-standing type, fully compartmentalised, double door, outdoor type High Mast Main Panel generally conforming to IP-55 and having SC capacity of 25 KA, fabricated from 2 mm. thick CRCA sheet, treated through seven tank process suitable to accommodate the following along with detachable gland plate (2 mm thick CRCA sheet), the enclosure shall be provided with ventilation louver covered with wire mesh. i) (Incomer): 125A, 415V, Four pole MCCB - 1 no. ii) (Outgoing): a) 63 A, 4P MCCB (C-series) - 01 no.; b) 100 A,4P MCCB (C-Series) - 01 no. iii) 150 A rating Al - Bus bar, Four pole with Fiber glass insulated support & PVC sleeve etc. iv) R Y B indication lamp (LED) with 3 nos 2 A SP MCB (B-series) = 01 set v) Separate Cable Alley for cable terminations. 02 nos of 100 A 4 Pole terminals. vi) Voltmeter Digital Type -1 no, Ammeter Digital Type - 1 no. | 1.00 | Each | 63500.00 | 67100.00 | 67100.00 | 90000.00 | 90000.00 | 67100.00 | Kripa Electronics india pvt ltd
31.00 | Supplying of weather proof, vermin proof, powder coated, free floor-standing type, fully compartmentalised, double door, outdoor type High Mast Sub Panel generally conforming to IP-55 and having SC capacity of 25 KA, fabricated from 2 mm. thick CRCA sheet, treated through seven tank process suitable to accommodate the following along with detachable gland plate (2 mm thick CRCA sheet) the enclosure shall be provided with ventilation louver covered with wiremesh. i) (Incomer):100A, 415V, Four pole MCCB - 2 nos. (ii) (Outgoing): a) 25 A, 4P MCB (C-series) - 06 nos.; (iii) 150 A rating Al - Bus bar, four pole with Fiber glass insulated support & PVC sleeve etc. (iv) R Y B indication lamp (LED) with 3 nos. 2 A SP MCB (B-series) = 01 set (v)Separate Cable Alley for cable terminations.08 nos of 100 A 4 Pole terminals (vi) 130 A,4 Pole contactor = 02 nos (for auto changing power supply and vice versa including 09 A Auxiliary contactor-01no and (ADD-ON BLOCK- N0-NC = 02 nos.); Indication Lamp for showing the selective power supply - 02 nos. (vii) Voltmeter Digital Type -1 no, Ammeter Digital Type - 1 no. | 5.00 | Each | 78000.00 | 110000.00 | 550000.00 | 140000.00 | 700000.00 | 550000.00 | Kripa Electronics india pvt ltd
32.00 | Supplying of weather proof, vermin proof, powder coated, free floor-standing type, fully compartmentalised, outdoor type High Mast Control Panel generally conforming to IP-55 and having SC capacity of 25 KA, fabricated from 2 mm. thick CRCA sheet, treated through seven tank process suitable to accommodate the following along with detachable gland plate (2 mm thick CRCA sheet), the enclosure shall be provided with ventilation louver covered with wiremesh. i) a) 25A, 415V, Four pole MCB - 1 nos. (Incomer Power supply) b) 16A, 415V, Four pole MCB - 2 nos. (Lifting lowering, lighting/timer) ii) (a) 32A 4 Pole contactor=01 no. 09 A TP contactor = 02 nos. (each for lifting, lowering, lighting/timer); (ADD-ON BLOCK- NO-NC=02 nos.) (b) On delay timer = 01 no; (c) 20 A socket outlet with top= 01 no (for Remote). iii) Auto / Manual toggle switch = 1 No, 100 A 4 Pole terminal: 3 nos. (Incomer Power Supply, Lighting, Lifting Lowering); Circuit Control Fuse: Mini MCB 2 A: 02 nos. (Incomer Power Supply, Lighting). Suitable quantity of Din Rail for mounting iv) Separate cable manager casing capping suitable quantity 1.5 sq mm copper wires for interconnection and 4 sq. mm. copper wires for power lines connection. Indication lamp: ON, OFF, TRIP: - 3 nos. | 25.00 | Each | 28029.00 | 25000.00 | 625000.00 | 45000.00 | 1125000.00 | 625000.00 | Kripa Electronics india pvt ltd
33.00 | Supplying of weather proof, vermin proof, powder coated, free floor-standing type, fully compartmentalised, double door, outdoor type High Mast Sub Panel generally conforming to IP-55 and having SC capacity of 25 KA, fabricated from 2 mm. thick CRCA sheet, treated through seven tank process suitable to accommodate the following along with detachable gland plate (2 mm thick CRCA sheet) the enclosure shall be provided with ventilation louver covered with wire mesh, lifting hooks. i) (Incomer) 63A, 415V, Four pole MCCB - 1 no. ii) (Outgoing): a) 32 A, 4P MCB (C-series) - 02 nos; iii) R Y B indication lamp (LED) with 3 nos. 2 A SP MCB (B-series) = 01 set iv)Voltmeter Digital Type -1 no, Ammeter Digital Type - 1 no. | 2.00 | Each | 27300.00 | 25000.00 | 50000.00 | 15000.00 | 30000.00 | 30000.00 | PRIME ENGINEERS
34.00 | Supplying of weather proof, vermin proof, powder coated, free floor-standing type, fully compartmentalised, outdoor type High Mast Control Panel generally conforming to IP-55 and having SC capacity of 25 KA, fabricated from 2 mm. thick CRCA sheet, treated through seven tank process suitable to accommodate the following along with detachable gland plate (2 mm thick CRCA sheet), the enclosure shall be provided with ventilation louver covered with wire mesh, lifting hooks. i) (Incomer) 25A, 415V, Four pole MCB - 2 no. (Incomer Power supply) ii) (Outgoing): a) 16A, 4P MCB (C-series) - 02 nos.; Lighting / Timmer and Lifting lowering) iii) (a) 32 A 4Pole contactor=03 nos, 9 A TP contactor = 02 nos. (each for lifting-lowering, lighting/timer); 9 A Auxiliary contactor = 01 no. (for auto changing power supply and vice versa including an ADD-ON BLOCK- NO-NC = 02 nos.) Indication Lamp for showing the selective power supply-02 nos (b) On delay timer = 01 no; (c) 20 A socket outlet with top = 01 no (for Remote). iv) R Y B indication lamp (LED) with 3 nos. 2 A SP MCB (B-series) = 01 set v) Auto / Manual toggle switch = 1 No, 100 A 4 Pole terminal : 4 nos. (02 no Incomer Power Supply, Lighting, Lifting Lowering); Circuit Control Fuse : Mini MCB 2 A: 03 nos. (Incomer supply, Lighting). Suitable quantity of Din Rail for mounting vi) Separate cable manager casing capping suitable quantity 1.5 sq. mm. copper wires for interconnection and 4 sq. mm. copper wires for power lines connection. Indication lamp: ON, OFF, TRIP: - 3 nos. | 12.00 | Each | 42510.00 | 40000.00 | 480000.00 | 60000.00 | 720000.00 | 480000.00 | Kripa Electronics india pvt ltd
35.00 | Installation, testing and commissioning of High Mast Electrical Panel / Control Panel as offered in item no. 10, 11, 12, 13, 14 including concrete foundation (1:3:6) and brick work of suitable size on three sides. It also includes swapping, recoiling, handling, refilling with sand and brick protection of all incoming and outgoing loop cables etc. complete as required. | 45.00 | Job | 17142.00 | 15000.00 | 675000.00 | 12000.00 | 540000.00 | 540000.00 | PRIME ENGINEERS
36.00 | Supply of XLPE insulated, PVC sheathed, Aluminium conductor, armoured power cable of following sizes of 1.1 kV grade and conforming to IS 7098 (part1) as required. (a) 3.5C x 120 Sq.mm. | 1120.00 | Metre | 425.00 | 400.00 | 448000.00 | 460.00 | 515200.00 | 448000.00 | Kripa Electronics india pvt ltd
37.00 | Supply of XLPE insulated, PVC sheathed, Aluminium conductor, armoured power cable of following sizes of 1.1 kV grade and conforming to IS 7098 (part1) as required. (a) 3.5C x 70 Sq. mm. | 1800.00 | Metre | 322.00 | 200.00 | 360000.00 | 240.00 | 432000.00 | 360000.00 | Kripa Electronics india pvt ltd
38.00 | Supply of XLPE insulated, PVC sheathed, Aluminium conductor, armoured power cable of following sizes of 1.1 kV grade and conforming to IS 7098 (part1) as required. (a) 3.5C x 35 Sq. mm. | 350.00 | Metre | 182.00 | 200.00 | 70000.00 | 240.00 | 84000.00 | 70000.00 | Kripa Electronics india pvt ltd
39.00 | Supply of XLPE insulated, PVC sheathed, Aluminium conductor, armoured power cable of following sizes of 1.1 kV grade and conforming to IS 7098 (part1) as required. (a) 4C x 16 Sq. mm. | 3100.00 | Metre | 115.00 | 110.00 | 341000.00 | 160.00 | 496000.00 | 341000.00 | Kripa Electronics india pvt ltd
40.00 | Supply of permanently lubricated HDPE (High density polyethylene) pipe of 75 mm outer dia along with necessary connectors/couplers/adaptors etc. complete as required and as per the technical specifications. | 6740.00 | Metre | 257.00 | 200.00 | 1348000.00 | 240.00 | 1617600.00 | 1348000.00 | Kripa Electronics india pvt ltd
41.00 | Laying of 75 mm dia permanently lubricated HDPE pipe along with its accessories like coupler, end plugs etc. in following way - (a) below the ground (i/c Road crossing, Cement concrete Apron Area) at a depth of 2 m to 6 m through horizontal directional drilling etc. complete as required. | 4315.00 | Metre | 271.00 | 220.00 | 949300.00 | 260.00 | 1121900.00 | 949300.00 | Kripa Electronics india pvt ltd
42.00 | Laying of 75 mm dia permanently lubricated HDPE pipe along with its accessories like coupler, end plugs etc. in following way - (a) On taxiway shoulder/Apron / for electrical work i/c machine cutting of runway / taxiway/Apron/ shoulder surface of suitable width and up to 150 mm depth, refilling and making good the same by concreting finish as per the site requirement. | 955.00 | Metre | 580.00 | 420.00 | 401100.00 | 480.00 | 458400.00 | 401100.00 | Kripa Electronics india pvt ltd
43.00 | Laying of 75 mm dia permanently lubricated HDPE pipe along with its accessories like coupler, end plugs etc. in following way - (a) Laying of 75 mm dia OD HDPE pipe , complete with accessories like couplers, bends, tee etc. in the soil for GLF work up to 750 mm deep with excavation, back filling & making good the same as per site requirement. | 470.00 | Metre | 650.00 | 270.00 | 126900.00 | 320.00 | 150400.00 | 126900.00 | Kripa Electronics india pvt ltd
44.00 | Laying of 75 mm dia permanently lubricated HDPE pipe along with its accessories like coupler, end plugs etc. in following way - (a) Laying of 75 mm dia OD HDPE pipe , complete with accessories like couplers, bends, tee etc. in the existing cable duct / masonry trench by saddling on the adjoining walls etc. the same as per site requirement. | 1000.00 | Metre | 80.00 | 130.00 | 130000.00 | 170.00 | 170000.00 | 130000.00 | Kripa Electronics india pvt ltd
45.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC / HUME / METAL / HDPE pipe as required. (a) Upto 35 sq. mm | 3433.00 | Metre | 33.00 | 100.00 | 343300.00 | 80.00 | 274640.00 | 274640.00 | PRIME ENGINEERS
46.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC / HUME / METAL / HDPE pipe as required. (a) Above 95 sq. mm and upto 185 sq. mm. | 1792.00 | Metre | 51.00 | 150.00 | 268800.00 | 130.00 | 232960.00 | 232960.00 | PRIME ENGINEERS
47.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC / HUME / METAL / HDPE pipe as required. (a) Above 95 sq. mm and upto 185 sq. mm. | 1120.00 | Metre | 69.00 | 200.00 | 224000.00 | 180.00 | 201600.00 | 201600.00 | PRIME ENGINEERS
48.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. (a) 3.5C x 120 Sq.mm. (45 mm) | 6.00 | Each | 492.00 | 350.00 | 2100.00 | 440.00 | 2640.00 | 2100.00 | Kripa Electronics india pvt ltd
49.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. (a) 3.5C x 70 Sq. mm. (38 mm) | 16.00 | Each | 370.00 | 245.00 | 3920.00 | 220.00 | 3520.00 | 3520.00 | PRIME ENGINEERS
50.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. (a) 3.5C x 35 Sq. mm. (32 mm) | 4.00 | Each | 307.00 | 245.00 | 980.00 | 210.00 | 840.00 | 840.00 | PRIME ENGINEERS
51.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. (a) 4C x 16 Sq. mm. (28 mm) | 98.00 | Each | 255.00 | 245.00 | 24010.00 | 210.00 | 20580.00 | 20580.00 | PRIME ENGINEERS
52.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 74.00 | Job | 6595.00 | 12000.00 | 888000.00 | 18000.00 | 1332000.00 | 888000.00 | Kripa Electronics india pvt ltd
53.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling, connection, fitting, numbering, painting etc. as required. | 750.00 | Metre | 459.00 | 440.00 | 330000.00 | 490.00 | 367500.00 | 330000.00 | Kripa Electronics india pvt ltd
54.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 590.00 | Metre | 208.00 | 115.00 | 67850.00 | 100.00 | 59000.00 | 59000.00 | PRIME ENGINEERS
55.00 | SH-II : COMPREHENSIVE MAINTENANCE WORK Job Contract for Comprehensive Maintenance of Apron Flood light system (AFL) as installed with its control, Sub feeder, main feeder panel, by deploying adequate manpower in three shifts on all days throughout the year including Sundays and holidays, preventive maintenance as per PMI schedule, attending complaints/faults/breakdown including taking rectification action and ensuring serviceability/satisfactory working condition, supply and replacement of all defective spares like MCCBs, MCB, contactors, LED fitting with driver, time switch, control cable, connectors, obstruction lights etc. and ensuring serviceability/satisfactory working condition of AFL masts, taking lux level measurement, maintaining all records and documentation etc., as per special conditions of contract and the instruction of Engineer in-charge or his authorised representative, as per requirement of the works. Note : Defect Liability period (DLP) for LED fitting and Driver is 5 Years and for other items it is 2 years. Cost of spare parts shall not be considered during Defect Liability Period. Only expenditure for manpower to be considered. The contractor needs to deploy the following minimum manpower with reliever. 1. Skilled Manpower - 3 Nos. (1 No. in each shift) and 2. Unskilled manpower - 3 Nos. (1 No. in each shift). a) 1st Year (of defect liability period). | 1.00 | Year | 1900000.00 | 2150000.00 | 2150000.00 | 2000000.00 | 2000000.00 | 2000000.00 | PRIME ENGINEERS
56.00 | Job Contract for Comprehensive Maintenance of Apron Flood light system (AFL) as installed with its control, Sub feeder, main feeder panel, by deploying adequate manpower in three shifts on all days throughout the year including Sundays and holidays, preventive maintenance as per PMI schedule, attending complaints/faults/breakdown including taking rectification action and ensuring serviceability/satisfactory working condition, supply and replacement of all defective spares like MCCBs, MCB, contactors, LED fitting with driver, time switch, control cable, connectors, obstruction lights etc. and ensuring serviceability/satisfactory working condition of AFL masts, taking lux level measurement, maintaining all records and documentation etc., as per special conditions of contract and the instruction of Engineer in-charge or his authorised representative, as per requirement of the works. Note : Defect Liability period (DLP) for LED fitting and Driver is 5 Years and for other items it is 2 years. Cost of spare parts shall not be considered during Defect Liability Period. Only expenditure for manpower to be considered. The contractor needs to deploy the following minimum manpower with reliever. 1. Skilled Manpower - 3 Nos. (1 No. in each shift) and 2. Unskilled manpower - 3 Nos. (1 No. in each shift). a) 2nd Year (of defect liability period). | 1.00 | Year | 1900000.00 | 2150000.00 | 2150000.00 | 2400000.00 | 2400000.00 | 2150000.00 | Kripa Electronics india pvt ltd
| Total in Figures |  |  |  |  | 45799860.00 |  | 47305280.00
Lowest Amount Quoted BY: Kripa Electronics india pvt ltd(45799860.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of LED Apron Flood Lighting of RCS Bays, Cargo Bay C15 to C16 and new Bays C1 to C 14 at NSCBI Airport, Kolkata. Tender ID: 2020_AAI_64435_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Kripa Electronics india pvt ltd | 45799860.00 | L1
| 2 | PRIME ENGINEERS | 47305280.00 | L2